## Civil
S.No | Desription | UOM | Rate (Rs.) | [5 empty] | Remarks
|  |  | IVFG (5) | IVFP (3) | IVFW (2) | SOTC (8) | DCA (0) | DCA (1)
1 | Dismantling, clearing away and carefully stacking useful materials for re- use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges, etc., complete. Brick Masonry at Gandhi Hospital | Cum | 398 | 398 | 398 | 900 | 1527 | 1527 | IVFG
2 | Dismantling doors, windows and clear storey windows, Ventilators etc., wood or steel shutters including Chowkhats, architraves, hold fasts and other attachments etc., and stacking them within 100m lead including labour charge etc., and complete for finished item of work. Not exceeding 3 sqm in area: Doors 1.00x2.60M at Gandhi Hospital | No | 350 | 350 | 350 | 1800 | 1018 | 1018 | IVFG
3 | Dismantling doors, windows and clear storey windows, Ventilators etc., wood or steel shutters including Chowkhats, architraves, hold fasts and other attachments etc., and stacking them within 100m lead including labour charge etc., and complete for finished item of work. Exceeding 3 sqm in area: Doors 1.50x2.60M at Gandhi Hospital | No | 468 | 468 | 468 |  | 313 |  | IVFG
4 | Conveyance of un-useful excavated earth to a distance of 21 KM for disposal including hire charges of T and P, labour charges etc., complete for finished item of work. Dismantled Brick masonry at Gandhi Hospital | Cum | 454 | 455 | 455 | 900 | 954 | 954 | IVFG
5 | Brick masonry for panel walls in superstructure with CM 1:8 prop: Aerated Cellular Autoclaved Concrete Blocks conforming to IS:2185 Part-3 - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600 x 200 x 200 mm including cost and conveyance of all materials like cement, screened sand, bricks, water etc., to site, including sales and other taxes on all materials and such as labour charges, like mixing cement mortar, scaffolding charges, constructing masonry, lift charges, curing, etc.,complete for finished item of work. TSSS No.501 and 504. 5th Floor at Gandhi Hospital | Cum | 16055 | 14558 | 16055 | 15300 | 7636 | 8017 | IVFG
6 | Reinforced Masonry for partition walls 100 mm thick in CM 1:4 prop. Aerated Cellular Autoclaved Concrete Blocks conforming to IS:2185 Part-3- 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600 x 200 x 100 mm and placing 2Nos. of 6mm M.S plain rods in every third layer with free ends of the reinforcement pegged into mortar joints of main brick walls where applicable including cost and conveyance of all materials like cement, steel, sans, brick, water etc., to site, including sales and other taxes excluding GST on all materials, all operational, incidents charges, constructing masonry, lift charges, curing, complete for finished item of work. TSSS No. of 509.5th Floor at Gandhi Hospital | Sqm | 1952 | 1716 | 1952 | 2700 | 1090 | 1144 | IVFG
7 | Providing Mild steel MS steel bars Fe 250 grade as per IS 432 of different diameters including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying including sales and other taxes on all materials etc. , complete for finished item of work. TSSS No.126 For RBM walls 6mm dia: 5th Floor at Gandhi Hospital | MT | 116500 | 116500 | 116500 | 126000 |  |  | IVFG
8 | Plastering 20mm thick in two coats using screened sand with base coat of 16mm thick in CM1:6 and top coat of 4mm thick in CM1:4 with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales and other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., complete for finished item of work .SS 901,903and 904 5th Floor at Gandhi Hospital | Sqm | 1077 | 945 | 1077 |  | 802 | 842 | IVFG
9 | Plastering 12mm thick in two coats using screened sand with base coat of 8mm thick in CM 1:6 and top coat of 4mm thick in CM 1:4 with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales and other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and complete for finished item of work. SS 901,903 and 904. 5th Floor at Gandhi Hospital | Sqm | 1041 | 906 | 1041 | 1224 | 436 | 458 | IVFG
10 | Supply and Installing change room Cubicles, at Gandhi Hospital. GENERALSPECIFICATIONS: Thickness of Compact Laminate: 12 mm Thick Colour of HPL Boards: In Single Colour, Size of Cubicle : As per DWG, Door Size for Normal Cubicle : As per DWG, Overall Height Of Cubicle : 2105 mm Including bottom gap of 100mm, Accessories: Manufacturers standard makes of Aluminium, SS Accessories. a Aluminium H Top Rail b SS Hinges c SS Privacy Thumb turn c/w Occupancy Indicator d SS Coat Hook e SS Door Knob f Aluminium U channel g Aluminium Door Stopper channel h Rubber Lining i SS Screws and PVC Wall Plugs | Sqm | 9055 | 9055 | 9055 |  | 7000 |  | IVFG
11 | Providing and laying screed plain cement concrete as per site condition for floor bedding using high quality aggregates including base preparation, compaction, levelling, all lead and lifts, rough finishing at the top surface, curing, shuttering if necessary etc., complete as directed . at Gandhi Hospital | Cum | 4700 | 4670 | 4700 | 9000 |  |  | IVFG
12 | Supply and fixing powder coated aluminium fully glazed swing door as per the approved drawing with fixed fan light of 500mm height at top door using aluminium sections of 101.60 mm x44.45mm , 3.18 mm thick for frame and door shutter made of styles , top and middle rail of 47.62mm x 44.45mm, 3.18 mm thick and bottom rail of 96.00mm x 44.45 mm,3.18mm thick, powder coating of aluminium sections 25mm microns thick, 5 mm thick plain glass fitted with suitable aluminium glazing clips and rubber beading in fan light portion, double shutters fitted with 5mm thick frosted glass in the top half and 12mm thick Prelaminated particle board One side choice colour and other side balancing white lamination in the bottom half fitted with suitable aluminium glazing clips and rubber beading, as approved by Engineer-in-Charge including supply and fixing ISI marked powder coated aluminium fixtures of 2 Nos. tower bolts 10mm bolt IS:204 300mm long, 4 Nos. aluminium handles IS:208 150mm dia and 1 Nos. aldrops IS:2681 250mm, 1 No. door closure, Al. Butt hinges 125mm long 6Nos including labour charges for manufacturing door , fixing the door with required No. of screws etc., complete for finished item of work. The Aluminium section used shall be standard make confirming to IS 1948-1961 and as approved by the Engineer 1200mmx2100mm at Gandhi Hospital | Sqm | 13713 | 13713 | 13713 |  |  |  | IVFG
13 | Supplying and fixing of Unplasticised Poly Vinyl Chloride UPVC 3 track sliding windows with mesh shutter – 2-glass shutters and 1-mesh shutter duly manufactured using UPVC reinforced profiles Composition of profile shall consists a minimum of 5.5 PHR of TiO2 and not more than 12 PHR of CaCo3 for every 100 parts of PVC resin of 94mm x 45 mm/80 mm x 52 mm x 2.20 mm for outer frames, 58 mm x 39 mm/54 mm x 38 mm x 2.20mm for sliding shutter frames capable of mounting single glazing system structurally reinforced with hot dip galvanized up to 50 microns of minimum thickness of 1.0/1.2 mm prefabricated and welded through fusion welding. The window sash shall be fitted with 5 mm thick clear float glass of reputed make and mesh shutter frame shall be 42 mm x 25mm/52 mm x 21.5 mm x 2.0 mm fitted with Vinyl Coated Fiber mesh- on rollers/ pulley duly fixed with Grey colour TPV Gasket for sash and Glazing bead shall be co- extruded with Grey colour soft PVC. System shall have single point locking with Touch Lock and the system is to be installed at the site using anchor fasteners, silicon rubber sealant, easy glazing/deglazing at site etc., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site includingetc., complete for finished item of work. at Gandhi Hospital | Sqm | 9517 | 9517 | 9517 | 9000 | 8188 |  | IVFG
14 | Providing, supplying and fixing of Fixed Louvered Ventilator made out of multi chambered uPVC sections with Glazing bead shall be co-extruded with Grey colour soft PVC. having isolated drainage and reinforced with Galvanized Iron profiles throughout the window. The outer frame having an overall size of 60 mm x 55 mm x 2.40 with reinforcement of 1 mm thickness and Mullion with overall size of 74 mm x 60 mm x 2.40 mm with reinforcement of 1 mm thickness. Composition of profile shall consists a minimum of 5.5 PHR of TiO2 and not more than 12 PHR of CaCo3 for every 100 parts of PVC resin. Ventilator shall be provided with 4.5 mm Pin Head glass, standard hardware. Wall thickness of frame and Mullion shall be 2.4 mm., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site etc., complete for finished item of work hinges IS:205 150mm long, 1 No. aldrop IS:2681 300mm long, 1 No. tower bolt IS:204 of 200 mm x 10 mm dia at top, 2 Nos. 150 mm at Gandhi Hospital | Sqm | 8564 | 8564 | 8564 | 12000 |  |  | IVFG
15 | Supply and fixing doors as per drawings with medium teak wood frame of section 100mm x 65 mm and ISI marked flush door shutters of 30 mm thick single shutter with bond wood solid block board type Core having cross bands and face veneers, hot pressed bonded with water proof phenol formaldehyde synthetic resin factory made conforming to IS 2202-1991 Part- I both sides commercial ply with internal lipping on all sides including cost and conveyance to site of teak wood frame, flush shutter including supply and fixing 6 Nos. MS Z hold fasts of size 300 mm x 40 mm x 5mm including cost of ISI marked Aluminium fixtures of 3 Nos. butt long handles IS:208, 1 No. door stopper and 1 No. rubber bush including fixing the fixtures to door with required number of screws, bolt and nuts including labour charges for fixing the frame in position, fixing the shutter to the frame etc., complete for finished item of work as per APSS 1001 and 1002 The vertical frame of door shall be embedded in flooring for a depth of not less than 10 mm 1000mm x 2100mm at Gandhi Hospital | Sqm | 5593 | 5593 | 5593 | 7400 |  |  | IVFG
16 | Supply and fixing doors as per drawings with medium teak wood frame of section 100mm x 65mm and ISI marked flush door shutter of 30mm thick single shutter with bond wood solid block board type Core having cross bands and face veneers, hot pressed bonded with water proof phenol formaldehyde synthetic resin factory made conforming to IS 2202-1991 Part- I both sides commercial ply with internal lipping on all sides including cost and conveyance to site of medium teak wood door frame, flush shutter, including suply and fixing 6 Nos. MS Z hold fasts of size 300mm x 40mm x 5mm including ISI marked Aluminium fixtures 3 Nos. butt hinges IS:205 of 150mm long, 1 No. aldrop IS:2681 250 mm long, 1 No. tower bolt IS:204 of 150 mm x 10mm dia, 2 Nos. 125mm long handles IS:208,1 No. rubber bush including supplying and fixing 1.20mm thick PVC sheet to full height of the shutter inside including labour charges for fixing the frame in position, fixing the shutter to the frame etc., complete for finished item of work as per APSS 1001 and 1002. The vertical frame of door shall be embedded in flooring for depth of not less than 10mm 750mm x 2100mm. at Gandhi Hospital | Sqm | 6510 | 6510 | 6510 |  | 7900 |  | IVFG
17 | Flooring with soluble salt porcelain vitrified tiles screen printed and polished of size 600 x 600 mm and thickness between 8 to 10mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630Parts 1 to 15 of any colour and finish in all shades and designs with borders and design as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM 1:8 prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread at the rate 3.3 kgs per Sqm. and jointed neatly with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site excluding cost of C.C. bed including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in- charge etc., and complete for finished item of work. TSSS No.701 and 707. 5th Floor at Gandhi Hospital | Sqm | 1725 | 1593 | 1725 | 2550 | 1000 | 1050 | IVFG
18 | Flooring with non-skid full body ceramic floor tiles of size 300mm x 300mm and thickness between 7 - 8mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630 Part 1 to 15 of any colour and finish in all shades and designs as approved by Engineer-in-charge, set over base coat of cement mortar 1:8, 12mm thick using screened sand over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread at the rate 3.3 Kgs per Sqm and jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, screened sand , water and tiles etc., complete for finished item of work. TSSS No.701 and 707 at Gandhi Hospital | Sqm | 1525 | 1395 | 1525 | 1710 | 1080 | 1134 | IVFG
19 | Providing and fixing in true horizontal level 14 mm - Mineral Fiber sheet 595 x 595 Square / Tegular Fissura fine model edge tiles with a Humidity Resistance of 90percentage RH, Average NRC 0.50, Light Reflectance greater than80percentage, Thermal Conductivity equal to 0.052 to 0.057 w/mk, Fire Performance Class 0/Class 1 using hot dipped Galvanized Steel section exposed surface with pre-coated capping, main Tee of size 24 x 32 mm at every 1200 mm c/c maximum and rotary stitched cross tee of size 24 x 27 mm at every 600 mm c/c and sub-cross tee of size 24 mm x 25 mm at 1200 mm c/c and wall angle of size 19 x 19 mm fixed to periphery of the wall and the above grid is suspended at every 1200 mm c/c in both directions using 2.0 mm thick pre-straightened GI Wire including cost and conveyance of all materials and labour charges such as cutting , fixing of standing of frame work exposing roof making etc., complete for finished item of work in 5th floor. at Gandhi Hospital | Sqm | 1636 | 1636 | 1636 | 1800 | 1675 |  | IVFG
20 | Providing dadooing to walls with glazed full body porcelain wall tiles of size 300 x 600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. 5th Floor at Gandhi Hospital | Sqm | 1423 | 1391 | 1423 | 1440 | 1080 | 1134 | IVFG
21 | Providing and applying Wall putty of White Cement or Polymer or Cement based of average 1 to 2 mm thickness over plastered surface to prepare the surface even and smooth after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, applying emery paper, Sand the surface, clean and wipe off loose dust, applying knifing paste filler by putty knife / muslin pad, air dry for 2 - 3 hrs, sand with 180 and 320 No., emery paper for the surface preparation including cost and conveyance of all materials to work site and all operational, incidental, labour charges, over heads and etc., complete for finished item of work in 5th floor Internal walls. at Gandhi Hospital | Sqm | 315 | 315 | 315 | 270 |  |  | IVFG
22 | Painting to new wood work and flush shutters with lappam finish, over a primary coat and painting two coats of synthetic enamel paint Grade-II VOC Volatile Organic Compound content less than 50 grams/litre of approved shade including cost and conveyance of all materials to site cost of primer coat and all labour charges etc. complete including applying sand paper on lappam coats for neat finish including sales and other taxes on cost of all materials etc., complete in all floors APSS No.1200, 1207 and 1211. at Gandhi Hospital | Sqm | 281 | 281 | 281 | 360 | 515 |  | IVFG
23 | Supply and application of one coat water based cement primer of interior grade I and two coats of water based PU paint having anti-bacterial applications content less than 50 grams/litre for internal walls including cost and conveyance of all materials to site, sales and other taxes, incidental, operational and all labour charges etc., and complete for finished item of work in 5th floor. at Gandhi Hospital | Sqm | 260 | 259 | 259 | 360 | 410 |  | IVFG
24 | Painting to old walls with 2 coats of water proof cement paint of shade as approved by the Engineer-In-Charge to give an even shade after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, scaffolding charges, incidental, labour charges etc., and overheads and contractors profit complete for finished item of work as per SS 912 in 5th floor. at Gandhi Hospital | Sqm | 229 | 229 | 229 |  |  |  | IVFG
25 | Supply and installation of 80mm thick double skin modular wall Panels made of 0.8 mm thick powder coated GI on both the sides, with 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, flush on both sides with maximum allowable gap of 3- 4mm filled with food grade silicon sealant and placed on cold rolled galvanised bottom tracks with a recess to provide floor to wall coving flush with the wall panel. This includes all required harware for completion Panels to be covered with a protective film to avoid any damages during transportation and installation at Gandhi Hospital | sqm | 5620 | 5620 | 5620 |  |  |  | IVFG
26 | Supply and installation of 50mm thick double skin ceiling system made of 0.8 mm thick Powder Coated GI sheets on both sides, 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, panels flush towards room side with maximum allowable gap of 3-4mm at panel to panel joints filled with silicon sealant. Ceiling panels are suspended from the RCC slab by using concealed AL ceiling grid with tie rod and adjustable turn buckle arrangement etc. This includes all required hardware for completion. Panels to be covered with a protective film to avoid any damages during transportation and installation at Gandhi Hospital | sqm | 5135 | 5135 | 5135 |  |  |  | IVFG
27 | Double leaf clean room Doors : 46mm thick flush doors made of 0.8mm thick Powder coated GI sheets on both sides, 90 plus or minus 2 kg/m3 density Honeycomb with stand upto 220 Deg.C Temperature, and compressible strength upto 400 Kg/Sqm, 1.2 mm thick GPSP . door frames, double glazed vision panel with necessary adhesive tapes and silicon sealant, necessary hardware like SS304 ball bearing butt hinges, D- handles, push plates, Dorma make door closure, concealed tower bolt, drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms, Both side lock and keys etc. complete. Size 1500 X 2100 mm with 300mm X 300mm double glazed view panels at Gandhi Hospital | No | 46000 | 46000 | 46000 |  |  |  | IVFG
28 | Single leaf clean room Doors : 46mm thick flush doors made of 0.8mm thick Powder coated GI sheets on both sides, 90 plus or minus 2 kg/m3 density Honeycomb with stand upto 220 Deg.C Temperature, and compressible strength upto 400 Kg/Sqm, 1.2 mm thick GPSP . door frames, double glazed vision panel with necessary adhesive tapes and silicon sealant, necessary hardware like SS304 ball bearing butt hinges, D- handles, push plates, Dorma make door closure, concealed tower bolt, drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms, Both side lock and keys etc. complete. Size 900 X 2100 mm with 300 mm x 300 mm View panel at Gandhi Hospital | No | 28700 | 28700 | 28700 |  |  |  | IVFG
29 | Emergency Fire Doors : 46mm thick flush doors made of 0.8mm thick Powder coated GI sheets on both sides, 90 plus or minus 2 kg/m3 density Honeycomb with stand upto 220 Deg.C Temperature, and compressible strength upto 400 Kg/Sqm, 1.2 mm thick GPSP . door frames, double glazed vision panel with necessary adhesive tapes and silicon sealant, necessary hardware like SS304 ball bearing butt hinges, D- handles, push plates, Dorma make door closure, concealed tower bolt, drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms, Both side lock and keys etc. complete. Size 1500 X 2100 mm with 2 hours fire rated and panic push bar and accessories etc. at Gandhi Hospital | No | 55000 | 55000 | 55000 |  | 90000 |  | IVFG
30 | Supply and installation of Extruded Aluminium Coving at Gandhi Hospital | Rmt | 585 | 585 | 585 |  |  |  | IVFG
31 | Providing, laying of scratch proof PVC/Vinyl flooring of 2mm thickness with proper welded joints air tight, along with leveling compound to match the existing flooring levels as per engineer in charge instructions. Sub floor preparation with self leveling compound. After the sub floor preparation, it should be suitable for ESD flooring. Rate inclusive of sifting of material and labour charges. at Gandhi Hospital | Sqm | 4070 | 4070 | 4070 | 3000 |  |  | IVFG
32 | Supply, installation, testing and commissioning of 16 G GI powder coated suitable single person entry air shower as per Technical Specifications at Gandhi Hospital | No | 355000 | 355000 | 355000 |  |  |  | IVFG
33 | Supply, installation, Testing and Commissioning of Static Pass Boxes of Size 450X450mm with 1.2mm thick SS 304 Mat finish , with interlock doors, UV light On when doors closed condition. As per clean room standard and requirement. at Gandhi Hospital | No | 61000 | 61000 | 61000 |  |  |  | IVFG
34 | Supply and application of one coat water based cement primer of interior grade I for internal walls including cost and conveyance of all materials to site, sales and other taxes, incidental, operational and all labour charges etc., and complete for finished item of work in 5th floor (for Ceiling) at Gandhi Hospital | Sqm | 85 | [5 empty] | IVFG
35 | Dismantling of unreinforced cement concrete, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete | Cum | 4036 |  |  | 4500 |  |  | IVFG
36 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete - Old Cement Mortor (Plaster) | Sqm | 13 | 13 |  |  |  |  | IVFG
37 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete. Reinforced Cement Concrete | Cum | 4424 | 4424 |  | 5400 | 2618 | 2618 | IVFG
38 | Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707) | Rmt | 162 | 151 |  | 120 | 280 | 294 | IVFG
39 | Providing of Factory made prelaminated FPVC (Foamed Polyvinyl Chloride) Door frame of the size 105x40mm with a wall thickness of 10mm made out of extruded rigid FPVC profile mitre joined with 6 Nos. of 50mm long screw. The door frame shall be fixed to the wall by using 80mm long screws through the frame with the help of PVC fasteners of 3 no's to be provided for each vertical member, GI stiffeners of ("U" channel of size 29x9x1mm, 150mm long) -3 no's at hinge point, Frame reinforcement of("U" GI channel of size 46x22x.06mm),Bottom tie rod of ("U" GI channel size of 15x15x1mm) etc. complete as per manufacturers specification for finished item of work. Maximum door frame size : 980 x 2070 including providing of 35mm thick Factory made Prelaminated ABS (Acrylonitrile Butadiene Styrene) Door shutter moulded in different designs, consisting of all round Frame made out of water proof solid foam PVC bar of size 20x32mm, reinforced by 32x 32mm - 2 nos. for vertical made out of LVL (Laminated Veneer Lumber), core material of 32 mm thick high density craft paper honey comb board, sandwiched on both sides with prelaminated ABS sheet thickness of 1.5mm . PVC edge banding of size 0.45mm on the vertical sides. Hardware made out of steel coated butterfly hinges - 3 Nos. for each shutter and ISI make S.S round lock completes for finished item of work. Maximum shutter size of : 910 x 2030 mm | Sqm | 9241 | 9241 |  |  |  |  | IVFG
40 | Flooring with 16 to 18 mm thick high polished granite stone slabs black colour as approved by the Engineer-in-Charge of length not less than 2.43 mts set over base coat of cement mortar (1:8) , 20mm thick using screened sand over CC bed already laid or RCC roof slab including neat grey cement slurry of honey like consistency spread @ 3.3 Kg per sqm and jointed neatly with white cement paste mixed with pigment of matching shade to full depth including cost and conveyance of all materials like cement , sand , water , granite slabs etc., to work site and all operational, incidental labour & lift charges, half rounding the edge , polishing charges and all other taxes on all materials, cost of base coat and overheads & contractors profit complete for finished item of work for platforms (S.S.701 & special) (for Reception Table). | Sqm | 5839 |  |  |  | 4136 |  | IVFG
41 | 50 LPH storage type RO of dimensions 525 x 425 x 1450 mm (WxDxH) of approx. weight 75Kg consists of 4 nos of 80 GPD 3-layer Thin Film Composite (TFC) membrane with 0.0001-micron pore size which can prevent TDS, heavy metals and equipped with 6 stage purification process which reduces pesticides in the water for reducing scale formation when water is heated. The RO should take min input pressure of 0.6 kg/cm2, 2000 ppm of TDS in Water, 500 ppm of Hardness, 6.5 to 8.5 PH of water which can give output of 20 to 25 % recovery in purified water and can run on 230V AC, 50 Hz supply with operating temp of 5oC-45oC. | Nos | 75000 | 75000 |  |  |  |  | IVFG
42 | Supply and placing of the Design Mix Concrete M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Weight Batcher / Concrete mixer with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials, centering using Casurina Ballies, Bamboos, Wooden Reapers, Runners, Wood Posts, Steel Plates etc., including all operational, incidental and labour charges such as weigh batching, machine mixing, lifting of concrete manually, laying concrete, curing , overheads & contractors profit etc., complete but excluding cost of steel and its fabrication charges for finished item of work (APSS No. 402) (for Lintels) | Cum | 15969 | 14683 |  | 11740 |  |  | IVFG
43 | Supply and fixing of Dress Hangers of size 450mm length with 8 Nos hooks, each capped with plastic protective cap (in change rooms). | Nos | 510 | 510 |  |  |  |  | IVFG
44 | Supplying and fixing Rectangular Mirror Frameless of size 457 .2 mm x 609.6 mm (For Change room) | Nos | 1775 | 1775 |  |  |  |  | IVFG
45 | Supply of Venetian blinds Vertical blinds 100 mm wide with all accessories. (For semen collection room & Counselling room Windows) | Sqm | 2187 | 2187 |  |  |  |  | IVFG
46 | Name Plates (Room Names) as approved by the Engineer In-charge. | Nos | 600 | 600 |  |  |  |  | IVFG
47 | Supply and fixing of High Quality IVF Procedural photos placed between two transparent acrylic boards fixed with studs at four corners to the PVC frame placed on DBs. (2' x 2' and above) | Nos | 9000 | 9000 |  |  |  |  | IVFG
48 | Providing, Fabricating and fixing full height V-board partitions of overall thickness of 75mm Partition frame work to be formed out of 50 X 25mm aluminium frame work placed vertically and horizontally at required centre to centre and cross braced with floor and ceiling channels. The cross bracing channels shall be provided also at above and below the partition framework and to be secured to floor at bottom and to any nearest structural member using galvanized metal screws and wooden / PVC rawl plugs. Partition framework to be cladded with 12.5mm thick tapered edge board on both sides of the partition in line and level fixed with drywall screws @ 300mm c/c with staggered joints to avoid through joints and finished with proprietary supplied jointing tape and compound. | Sqm | 1625 | 1625 |  | 3640 |  |  | IVFG
49 | Supply and fixing of doors as per approved drawings with (WPC) single extruded Door Frame section of 100*65 MM and30mm thick Wood Plastic Composite (WPC) Door shutter, comprising of 70% virgin polymer, 15% wood powder (fiber), and the remaining 15% additives, the door shutter shall be water resistant, fire resistant and termite resistant,with Tensile Strength not less than 170Kgf/cm2 and the door shutters surface finished deco paint including cost and conveyance to site of teak wood frame, WPC shutter including supply and fixing 6 nos MS Z hold fasts of size 300 mm x 40 mm x 5mm including cost of ISI marked brass fixtures of 6 Nos butt hinges (IS:205) 150mm long , 1 No. aldrop (IS:2681) 300mm long, 2 Nos tower bolts- 10mm (IS:204) of 200 mm long at top, 1 No. tower bolt- 10mm bolt (IS:204) 150mm long at bottom, 2 Nos. 150mm long fancy handles (IS:208), 2 Nos door stopper and 2 Nos rubber bushes including fixing the fixtures to door with required number of screws, bolt and nuts including labour charges for fixing the frame in position, fixing the shutter to the frame, fixing glass in fan light portion etc., including overheads & contractors profit complete for finished item of work as per APSS 1001 & 1002 The vertical frame of door shall be embedded in flooring for a depth of not less than 10 mm) (800mm x 2100mm) (For Wash Rooms). | Sqm | 6734 | 6734 |  | 5400 |  |  | IVFG
50 | Wall Paneling 14mm thick Indoor WPC louvers providing & Fixing full height said 12mm SHERA Board panneling till slab with wooden framing in line and level including fling joints and joint calls and neccesary hardware | Sqm | 15500 | [5 empty] | IVFG
51 | 2 WPC Louvers Ceiling Praviding and fixing WPC Louvers to the Celling of which includes G Perimeter Channels of size 0.55mm thick (having One Flange of 20mm and another flange of 30mm and a web of 27mm) along with perimeter of ceiling screw fixed to brick wall/partition with the help of Nylon sleeves and screws at 610mm centres. Then suspending G1 intermediate channels of size 45mm 10. 9mm thick with 2 flanges of 15mm each) from the soffis at 1220mm centres with ceiling angle of width 25mm x 10mm X0.55mm thick fixed to saffit with GI. cleat and steel expansion fasteners. Ceiling section of 0.55mm thick having knurled web of 51.5mm and 2 flanges of 26mm each with lips of 10.5mm are Soft then fixed to the intermediate channel with the help of connecting clips and in direction perpendicular to the intermediate channel at 450 mm centres IN ULTRA GI CHANNELS Rute to be included all kinds of profiles and cut outs required for light fixtures Speakers. Smoke detector, trao doors and AC grill in the ceiling | Sqm | 17450 | [5 empty] | IVFG
52 | Providing and fixing of wooden box celling at the top of Reception table with Imm thick laminate with wooden framing of BWP 710 Gurjan Ply support from the top slab end to end with neccesary cutouts for lighting and hardware | Sqm | 11335 | [5 empty] | IVFG
53 | Back Pannelling with laminate Finish of 1 mm thick Providing & Fixing full height solid 12mm BWF 710 GURIAN PLY Board panneling till slab with wooden framing in line and level including the neccesary hardware and cutouts | Sqm | 10500 | [5 empty] | IVFG
54 | Providing and fixing ISI marked Magnetic 25mm Block Board door shutters, core of block board construction with frame of 1st class hard wood and fixing 1 MM laminate on both faces of shutters, including ISI marked Stainless Steel butt hinges with necessary screws and tower bait complete | Nos | 13800 | [5 empty] | IVFG
55 | Providing and fixing PVC frames on the walls for covering the area over DB Boxes with 12 mm PVC sheets in a box section of 60mm thick including neccesary accessories. | Sqm | 6473 | [5 empty] | IVFG
56 | Providing and Fixing of (25X25) mm WPC corner L-Patties at the topper edge of the wall tile cladding | Rmt | 230 | [5 empty] | IVFG
57 | Providing and Fixing of SS-ROSE GOLD corner & L-Patties at the SIDE edge of the wall tile cladding | Nos | 1500 | [5 empty] | IVFG
58 | Providing and fixing of Door Frame panneling with 18mm BWP 710 Gurjan Ply and 8mm thick beeding half rounded on the both sides with 1mm thick laminate Finish with necessary handware and Polishing. | Rmt | 2166 | [5 empty] | IVFG
59 | Providing and fixing the 60mm Thick Box framing as the back support for the name plate installed of 18mm BWP 710 Gurjan and 1mm thick high glossy laminate finish | Sqm | 11012 | [5 empty] | IVFG
60 | Providing and Fixing of 32mm Double Flush Door with frame 8mm beeding on its edges on four sides with polishing finish and 1 mm thick laminate on the both sides of which including ISI marked Stainless Steel centre lock and butt hinges with necessary screws and tower bolt complete for (1500 x 200 mm door) | Nos | 50400 | [5 empty] | IVFG
61 | Providing and fixing of Side wall decor Frame for photo hangings panneling with 18mm BWP 710 Gurjan Ply and 8mm thick beeding half rounded on the both sides with 1mm thick laminate finish with necessary hardware and Polishing. | Rmt | 2170 | [5 empty] | IVFG
62 | Supply and fixing of Wall paper as approved by the Engineer In-charge. (1. 1 x 2 x 4350 x 85 mm & 2. 1 x 2 x 820 x 85 mm) | Nos | 5175 | [5 empty] | IVFG
63 | Supply and fixing of Main IVF logo with LED arcylic board fixed with LEDs inside and electrical connections as approved by the Engineer In-charge ( 520 mm dia & 50 mm thick) | Nos | 11475 | [5 empty] | IVFG
64 | Supply and fixing of Main Entrance LED 3D Arcylic letter board fixed with LEDs inside and electrical connections as approved by the Engineer In-charge (2890 mm x 465 mm) | Nos | 44250 | [5 empty] | IVFG
65 | Providing and fixing Aluminium Extruded Section Body Tubular Type Hydraulic Door Closer (IS: 3564) with double speed adjustment with necessary accessories and screws etc. complete. Make: Haffele | Nos | 2819 | [5 empty] | IVFG
66 | Supplying and fixing of windows / in open court yards using 25mm x 6mm MS flat alround and 10mm MS square bars horizontally at 125mm centre to centre and vertically at 300mm centre to centre including fixing with 4 Nos of MS Z holdfasts (2 on each side) duly making cutting brick masonry, fixing and making to original surface neatly and painting grill with one coat of red oxide primer including cost all taxes and conveyance of all materials including cutting, bending, welding including all operational charges and all labour charges etc., complete for finished item of work. (for Window Grills) | Sqm | 1569 | 1569 |  |  |  |  | IVFG
67 | AHU shed with provision for fencing, door with lock- key arrangement shall be provided with Framework vertically made of MS Square Pipe frame: 2 Inches X 2 Inches, 16Gauge M S Fencing with wire mesh: ½ inch X ½inch. Supporting Structure M S Angle: 50 X 5mm GI pre-coated corrugated profile roof sheet: 0.5 mm thick duly supported with JHook 10 SWG with provision of door with lock and key AHU Shed with fencing should be duly enamel painted and with anti-rust coating from both sides. | Iob | 300000 | 300000 |  |  |  |  | IVFG
68 | Supply of Sun Control film to the glazed windows (For Windows & Door view Windows) | Sqm | 381 | 381 |  |  |  |  | IVFG
69 | Dismantling clearing away and carefully stacking useful materials for re use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges etc complete for Flooring at MGMH Petlaburj | Sqm |  | 20 | 20 |  | 600 | 600 | IVF Petlaburj
70 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Kadapa slabs or shahabad stone slabs on sand bed) | Sqm |  |  |  | 630 |  |  | SOTC
71 | RCC M 20 grade design mix (50mm thick platforms) | Sqm |  |  |  | 1170 |  |  | SOTC
72 | RCC M 20 grade design mix (25 mm thick Shelves) | Sqm |  |  |  | 900 |  |  | SOTC
73 | PCC (1:3:6) nominal mix using 20mm size graded m/c (For bed blocks and hold fasts) (OTs screed) | Cum |  |  |  | 9000 |  |  | SOTC
74 | Filling with light weight concrete in Cement Concrete (1:5:10) proportion using brick jelly for low roofs | Cum |  |  |  | 7200 | 3883 | 3981 | SOTC
75 | Impervious coat to exposed RCC roof slab surfaces (APSS No. 901 and 903) For Toilets | sqm |  |  |  | 360 | 541 | 568 | SOTC
76 | Dadooing to walls with glazed full body Ceramic tiles | Sqm |  |  |  | 1440 |  |  | SOTC
77 | Painting to new iron work | Sqm |  |  |  | 270 | 485 |  | SOTC
78 | Two shutter cupboards | Sqm |  |  |  | 9000 |  |  | SOTC
79 | Fixed Glass Window – 1200 x 1200 | Sqm |  |  |  | 5400 |  |  | SOTC
80 | Grouting the holes with neat cement slurry of 20mm dia with all required accessories of all materials etc., including cost & Conveyance of all labour Charges etc., complete finished item of work (*As per SSR2021-22 of S.NO:-8) | Nos |  |  |  | 90000 |  |  | SOTC
81 | Pressure grouting the drilled holes with neat cement slurry or with approved grout admixture using pump - excluding cost of drilling holes after fixing nozzles as technical specification approved by the department etc., including cost & Conveyance of all labour charges etc., complete finished item of work | Nos |  |  |  | 315000 |  |  | SOTC
82 | Supply and fabricating,erecting and fixing inposition trusses of approved design with structural steel other than MS. | Kgs |  |  |  | 1170000 |  |  | SOTC
83 | Supply and fixing of pre painted Galvalume Trapezoidal Profile Roofing with 0.50mm Thickness. | Sqm |  |  |  | 70200 |  |  | SOTC
84 | Supply and installation of Under-deck Thermocol insulation sheets of 40 mm thick having more than 30 Kg/m3 density to ceiling by brush application of bituminous adhesive to the sheets and secured with screw along with washer at the centre of the sheet supported with GI wire running diagonally to the sheet of 2mm dia. (in ICUs & MOTs Integration Room) | Sqm |  |  |  | 1014 |  |  | SOTC
85 | Supply and placing of the Design Mix Plain Cement Concrete of M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Concrete Batching Plant with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials. (in 6 OTs) | Cum |  |  |  | 11740 |  |  | SOTC
86 | Supply and Laying of Floor leveller compund (self smoothing mortar) to level the surface, having bulk density not less than 2 Kg/l for a fresh mortor, compressive strength not less than 20 N/mm2, initial setting time not more than 40 minutes and offer a 25 minutes working time, The surface should be walkabe after 30 min of laying. (all rooms & corridors except OTs, TIRs and Sterile corridor) | Sqm |  |  |  | 1460 |  |  | SOTC
87 | Providing dadooing to walls with glazed full body ceramic wall tiles of size 800 x 1600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. (at Entrance) | Sqm |  |  |  | 4665 |  |  | SOTC
88 | Providing (1500 X 2100) single sliding door operated by elbow switches / foot switch as well as touchless sensor of 10mm thick toughened glass (Saint Gobin / Modi Guard) fixed in SS 304 grade 2 Track top channel of 45 mm (one track to hold fixed glass partition in position and second track with top rollers suitably angled to reduce resistance to movement to facilitate smooth sliding movement of the door). Single track bottom channel to be provided for fixed glass partition. Floor guide to be provided for smooth sliding of the door. Concealed door handle of (150 mm) to be provided in cutout on the sliding door for manual operation when required. All fittings provided should be of Titon /Ozone / Enox make in SS 304 - In TIRs | Nos |  |  |  | 270276 |  |  | SOTC
89 | V-Board Partitions on top of false ceiling for partitioning of sterile corridor and non-sterile corridor (for dividing corridors into zones above ceiling) | Sqm |  |  |  | 3640 |  |  | SOTC
90 | GI Powder Coated Sliding Doors (0.8mm shutter sheet thk & 1.2mm frame sheet thk with Single Rebate and Honeycomb Infill) Double Leaf Door 1200 x 2100mm with Accessories (Sliding Track for Double Door, Sliding Dead Lock Enox, Concealed Handles 100mm Ahlada, Flush Bolt 300mm Ahlada, SS304 Kick Plate upto 350mm ht, DG Clear Float Glass 350x750x6mm with Adhesive Tape & Silicon Sealant) (for change rooms to corridor entrance) | Nos |  |  |  | 84133 |  |  | SOTC
91 | Supply and installation of 50mm thick double skin modular wall Panels made of 0.8 mm thick powder coated GI on both the sides, with 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, flush on both sides with maximum allowable gap of 3- 4mm filled with food grade silicon sealant and placed on cold rolled galvanised bottom tracks with a recess to provide floor to wall coving flush with the wall panel. This includes all required harware for completion Panels to be covered with a protective film to avoid any damages during transportation and installation | Sqm |  |  |  | 7450 |  |  | SOTC
92 | Supply and installation of 50mm thick double skin ceiling system made of 0.8 mm thick Powder Coated GI sheets on both sides, 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, panels flush towards room side with maximum allowable gap of 3-4mm at panel to panel joints filled with silicon sealant. Ceiling panels are suspended from the RCC slab by using concealed AL ceiling grid with tie rod and adjustable turn buckle arrangement etc. This includes all required hardware for completion. Panels to be covered with a protective film to avoid any damages during transportation and installation | Sqm |  |  |  | 7450 |  |  | SOTC
93 | Acoustic Wall Panelling with framework consisting of 25mm high GI wall channels with fully knurled surface of 0.55mm thick bottom wedge of 80mm width, having two equal flanges of 26mm is anchored to GI studs of 50mm high. GI studs of 50mm High to be fixed to wall at 600mm centres, 25mm thick channels are then fixed perpendicular to the GI studs and suitable fixing channel is fixed to the cross channel to fix the panel to achieve overall air gap of 75mm from the wall and GI Clips for inside panel and Clips for border panel of 18mm to be fixed to the GI wall channel to achieve required shape. Secured arranging of polyester wool of – thickness/density, Prelam Board to be installed. 15mm thick Prelam perforated Wooden slat of required dia perforation & pitch is to be customised and then fixed to GI frame rigidly by using fixing channel fastened perpendicular to the cross channel with GI brackets. The boards shall be fixed to the GI frame with special cleats. (MOTs Integration Room) | Sqm |  |  |  | 6350 |  |  | SOTC
94 | Accooustic Ceiling Paneling with Perforated board Fine line Grid false ceiling using 11mm thick Perforated Board sheet tiles of size 595mm x 595mm fixing to steel precoated GI wall angle of size 25mm x 25mm x 0.70mm thick along the perimeter of ceiling screw fixed to brick work / partition at 610mm center to center and suspending the frame work using precoated GI Tee section (24mm x 38mm x 0.7mm) from soffit at 1220mm center to center fixed with GI Soffit Cleat, rawl plugs and steel expansion fasteners & connecting clip to the GI Tee section with 4mm dia GI rod with galvanised spring steel level clip of PVC unversal holding clips system at 1200mm center to center and Secured arranging of polyester wool of 50mm thick 1000 GSM, Prelam Board to be installed. 15mm thick Prelam perforated Wooden slat of required dia perforation & pitch is to be customised and then fixed to GI frame rigidly by using fixing channel fastened perpendicular to the cross channel with GI brackets. The boards shall be fixed to the GI frame with special cleats. (MOTs Integration Room) | Sqm |  |  |  | 5700 |  |  | SOTC
95 | Wooden Flooring with Engineered wood planks of 14mm thick (MOTs Integration Room) | Sqm |  |  |  | 7300 |  |  | SOTC
96 | Skirting for Wooden Flooring with Engineered wood planks of 14mm thick (MOTs Integration Room) | Rmt |  |  |  | 900 |  |  | SOTC
97 | 80% blockout Ruler Blinds for MOTs Integration Room Windows | Nos |  |  |  | 12000 |  |  | SOTC
98 | Supply and installation of double pass RO system having 2 nos feed pumps of 1.5 HP with max flow of 4000 ltr/hr including construction of sand filter of dimensions (H=1650 mm, D=325 mm) with filter media as Quartz sand of SS vessel construction and Activated Carbon filter of dimensions (H= 1650mm) with filter media as Activated carbon (IV-600) of SS vessel construction, with 4 nos of spiral wound RO membrane of size 4 inch dia x 1 m length of make ION EXCHANGE (HYDROMEN) (or) equal, 2 nos UV system with service flow of 1000 ltr/hr (Before 2nd filter and after SS tank out-let) with PEX pipeline recirculation loop to avoid contamination in pipe to supply for 10 beds in Post ICU, 4 beds in Transplant ICU and 1 for each TIR.) Drinage outlet to be provided near each RO outlet. | Job |  |  |  | 6240000 |  |  | SOTC
99 | Terrace Water Proofing: Dismantling and shifting of debris to Ground Floor: Dismantling the existed Concrete Screed flooring completely by using mechanical chipping machine, and shifting debris from terrace to ground floor. | sqm |  |  |  | 306.8 |  |  | SOTC
100 | Terrace Water Proofing: Surface Preparation & Cracks Treatment: Prepare the surface thoroughly by cleaning and wash, removing dust, dirt, oil, grease and loose particle with high 160 bar pressure water Jet pumps. Find the cracks on rcc slab, Shrinkage and non-moving cracks should be pre-treated by cutting the crack @10mmx10mm, prepare the cracks dust free by using of wire brush& air blower, mix the two components of low viscosity epoxy epoxy resin Fosroc Conbextra EP10/Dr. Fixit Pidiprime A/ SIKA Davco FLORPRIMW WB- Water based epoxy primer, two components epoxy injection grout and treat the cracks. Seal the cracks with Fosroc Nitoseal PU 50/ Dr. Fixit Crack X Paste/ Sikalastic(R) -562 IN (DAVCO K10 Polyurethane Plus) single-component moisture-cure, polyurethane hybrid joint sealant. | Sqm |  |  |  | 206.5 |  |  | SOTC
101 | Terrace Water Proofing: Angle fillet / taper: Providing angle fillet of 75mmx75mm with polymer modified mortar in the ratio of cement: sand: aggregate in the ratio of (1:1.5:1.5) admixed with Fosroc Nitobond SBR/M-Crete PC Bond SBR/ Dr. Fixit Pidicrete URP @10% by the weight of cement to avoid cracking at 90º angle of RCC slab & Masonry wall joints. | Sqm |  |  |  | 507.4 |  |  | SOTC
102 | Terrace Water Proofing: Primer Coat: Applying 1 coat of Fosroc Nitoproof WB Primer/ Dr. Fixit Primeseal Primer/ SikaFloor(R)-133 W Primer (Floorprime WB) is a two component product and must be mixed & applied in order to perform as specified. Transfer base and the hardener to a suitable fresh container and mix thoroughly with a slow speed mixer for 2 -3 minutes which makes the mix as a milky white paste . Add double the quantity of clean water by volume to the mix gradually under mixing which makes the mix as low viscous milky white liquid. The diluted primer should be applied at a coverage of 8-10 m2/litre, preferably using roller. The applied primer should be allowed to reach tack free condition before applying liquid applied coatings and membranes. The tack free condition of Nitoproof WB primer happens after 4-5 hours of application @ 27 deg. | Sqm |  |  |  | 159.3 |  |  | SOTC
103 | Terrace Water Proofing: Application of 2 Coats of Pitch Free PU based Liquid applied single component elastomeric waterproofing membrane (Fosroc Nitoproof 600PF/ BASF HLM5000/ Dr. Fixit Roofseal Ultra). Application of Fosroc Nitoproof 600PF/ BASF HLM5000/ Dr. Fixit Roofseal Ultra can be applied by brush, squeegee, roller/ suitable spray applied machine. It is applied at a minimum wet film thickness of 1.5mm in 2 coats. The second coat should be applied in perpendicular direction to the first coat. | Sqm |  |  |  | 1569.4 |  |  | SOTC
104 | Terrace Water Proofing: Laying 200 GSM Geotextile Fabric: Laying of 200GSM geotextile cloth over the waterproof coating with overlap of 30mm at cloth joints. | Sqm |  |  |  | 177 |  |  | SOTC
105 | Terrace Water Proofing: Laying of 125mm Fiber Reinforced M20 Grade Protective Concrete Screed on Terrace. Marking the levels over the waterproofing system as per the slab level towards rain outlet. Laying of M20 grade fiber reinforced concrete screed, leveling the surface as per the marked levels, providing the proper slope to rain water outlets providing the neat kalai finish polymer modified slurry. Cut the 5mmx5mm groove for every 4mtx4mt between 24hrs - 48hrs of concrete laying. Provide water stoppers for curing with water. | Sqm |  |  |  | 1770 |  |  | SOTC
106 | Terrace Water Proofing: Control Joints Treatment: Provide the masking tape of both edges of joint, prepare the joints dust free by wire brush and air blower, seal the joints of 5mmx5mm with Fosroc Nitoseal PU50/ Dr. Fixit Crack X Paste/ Sikalastic(R)- 562 IN (DAVCO K10 Polyurethane Plus) single component polyurethane sealant by using PU Gun. Remove the masking tapes. | Sqm |  |  |  | 265.5 |  |  | SOTC
107 | External Walls Repair & Waterproofing Treatment: RCC Sunshades Repairs : a. Check the damaged Rcc sunshades/ projections/ any plastered area damages by visual inspection & fiber hammer test. b. Mark those damaged area, cut the marked area with electronic cutting machine and remove the loose concrete/ plaster and expose the reinforcement. c. Apply Fosroc Reebaklens RR Rust remover/ Dr. Fixit Repairpro rust remover/ SikaRustoff-100 IN with brush for complete wetting of rusted reinforcement and allowed to react it for 16-24 hours. After 24 hours, clean the rust with wire brush & air blower. | Sqm |  |  |  | 5192 |  |  | SOTC
108 | External Walls Repair & Waterproofing Treatment: d. Wash the reinforcement thoroughly with clean water. Wire brush again to remove remaining loose material and finish by thoroughly washing down with clean water and allow to complete dry. e. Applying of FOSROC Nitozinc primer/ Dr. Fixit Epoxy zincrich primer/ Sika Ferrogard-950 IN to exposed existed reinforcement after cleaning the Rust, an unbroken 40 microns coating capable of provided 'active' galvanic protection for exposed reinforcement. f. Enhancing the bonding between Old RCC Ceiling to New Polymer Mortar with applying of SBR Based Polymer Modified Cementitious Bond coat admixed FOSROC Nitobond SBR/ M- Crete PC bond SBR/ Dr. Fixit Pidicrete URP. | [7 empty] | SOTC
109 | External Walls Repair & Waterproofing Treatment: g. Providing 20mm of structural grade polymer modified mortar by Fosroc Renderoc S2/M- Crete PC Mortar Ultra with then 2nd layer of finishing will be done by polymer modified mortar with cement mortar 1:3 (cement:sand) admixed Fosroc Nitobond SBR/M-Crete PC bond SBR/ Dr. Fixit Pidicrete URP @10% by the weight of cement weight and water, make the proper finish to existed wall level. h. Any holes will be packed with polymer modified mortar (M-Crete PC mortar Ultra) prior that holes should be prepared dust free by wire-brush and Air Blower, wash the holes with clean water and maintain SSD condition. | [7 empty] | SOTC
110 | External Walls Waterproofing: a. Surface Preparation: Surface must be thoroughly cleaned by using 160 bar Jet pump to clean dust, fungus, algae, grease etc. Treat any areas affected by Algae, moss or fungal growth. b. Crack Filling: The surface to be checked for cracks, cut the cracks 5mmx5mm by electronic cutting machine, clean the cracks with wire brush and air blower, seal the cracks with Fosroc Nitoseal PU50/ Dr. Fixit Crack X paste/ Sikalastic(R) -562 IN (DAVCO K10 polyurethane Plus) Polyurethane Sealant . c. External Wall Waterproof Coating & Priming: After the proper surface preparation and curing of repaired areas wash the surface well and maintaining it in saturated surface dry condition proceed for priming using Dr. Fixit Primeseal diluted in 2:1 ratio with water (2 parts Primeseal diluted with 1 part water). Maintain the spreading rate of 8-10 sq mtr per litre for a single coat application to achieve about 20 – 25 microns DFT. Allow it to dry for 6-8 hrs. | Sqm |  |  |  | 826 |  |  | SOTC
111 | External Walls Waterproofing: d. COATING(2-Coats): Brush apply 1st coat of Dr. Fixit Raincoat waterproof coating without any dilution. Maintain the spreading rate of 3.5 - 4.0 sqm per litre / coat application to achieve about 120-130 microns DFT. The 2nd coat of Dr. Fixit Raincoat Classic Topcoat to be apply ith the interval of 6-8 hrs without any dilution. Maintain the spreading rate of 7-8 sqm per litre/ coat application to achieve about 50-60 microns DFT. | [7 empty] | SOTC
112 | Window Frame-Wall Joints/Gaps Treatment: Cut the joint and make a groove of 5mmx5mm by electronic cutting machine, clean the cracks with wire brush and air blower, seal the cracks with Fosroc Nitoseal PU50/ Dr. Fixit Crack X Paste/ Sikalastic(R) -562 IN (DAVCO K10 Polyurethane Plus) olyurethane Sealant. | Sqm |  |  |  | 421.26 |  |  | SOTC
113 | Supply of Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs with borders and design as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM (1:8) prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab , including neat cement slurry of honey like consistancy spread @ 3.3 kgs per Sqm. and jointed neately with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site (excluding cost of C.C. bed) including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in-charge etc.,and overheads & contractors profit complete for finished item of work. (APSS No.701 & 707). | Sqm |  |  |  | 2550 |  |  | SOTC
114 | Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707) | Rmt |  |  |  | 250 |  |  | SOTC
115 | Doors as per approved drawings with medium teak wood frame (1500mm x 2600mm) | Sqm |  |  |  | 6300 |  |  | SOTC
116 | Supply & Fixing of Powder Coated Fire Rated doors. | Sqm |  |  |  | 29000 |  |  | SOTC
117 | Scientific Doors with metal door frames and door shutters made of galvanize steel | Sqm |  |  |  | 18000 | 12500 |  | SOTC
118 | Flooring with 16 to 18 mm thick high polished granite stone slabs black colour for platforms (S.S.701 and special) | Sqm |  |  |  | 6300 |  |  | SOTC
119 | Stainless Steel Pre-fabricated Wall panels. (MOTs & MOT Corridor) - Wall panels | Sqm |  |  |  | 15010 |  |  | SOTC
120 | Stainless Steel Pre-fabricated Ceiling panels In MOTs & MOTs Corridor | Sqm |  |  |  | 15010 |  |  | SOTC
121 | Electro conductive Flooring inside MOTs | Sqm |  |  |  | 4035 |  |  | SOTC
122 | Flooring with Vinyl Sheets In MOT Corridor | Sqm |  |  |  | 3750 |  |  | SOTC
123 | Dismantling clearing away and carefully stacking useful materials for re use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges etc complete for. False Ceiling. | Sqm |  |  |  |  | 90 | 90 | DCA
124 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials including excavated earth/debris to a distance of 21 KM as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges etc complete Brick masonry 168.50 Cum Flooring 56.40 Cum CC up to 15cm thick 14.10 Cum RCC 14.27 Cum False Ceiling 352.00 Sqmt Doors and Windows 106 No complete for finished item of work. (Total Qty = Brick work - 168.50 Cum + Flooring - 56.40 Cum + CC - 14.10 Cum + RCC - 14.27 Cum + False ceiling - 4.22 Cum = 258 Cum = 1 Job = Rs. 1.75 Lakhs) (Rs 678 / Cum) | Job |  |  |  |  | 175000 |  | DCA
125 | Supply and placing of the Reinforced Cement Concrete M 20 grade Nominal Mix as per Technical specifications For Lintels in Ground Floor. | Cum |  |  |  |  | 8727 | 9163 | DCA
126 | Supplying, providing and installing Self Leveling Epoxy flooring system EPU 3mm thick, as per Technical Specifications. Including R 75 Aluminium coving wall to flooring including c/c of all materials and labour charges etc complete finished item of work | Sqm |  |  |  |  | 1769 | 1769 | DCA
127 | Providing specialized high performance acrylic polymer modified elastomeric cementitious waterproof coating to the terrace walls internal portion of the bathroom and toilets internal portion of the water tanks Pg.no 729 SOR No TBSCQ.VII 04 as per Technical Specifications. | Sqm |  |  |  |  | 412 |  | DCA
128 | Providing specialized polysulphide sealant treatment to the expansion joints as per Technical Specifications. Sl.no 732 SOR. No TBSCQ.VII 07, including fixing of 24 gauge alluminium sheet over expansion joint | Rmt |  |  |  |  | 759 |  | DCA
129 | Painting One coat Water Based Cement Primer of Exterior Grade II and two coats of Acrylic Emulsion paint over Exterior grade Texture ready mixed paint with sand texture as per Technical Specifications. | Sqm |  |  |  |  | 502 |  | DCA
130 | Effluent Collection Tank: Earthwork excavation, PCC 1:4:8 150mm thick , RCC M25 300mm thick base Base Slab, RCC M 25 230mm side walls, Supply, fabricating, erecting and fixing in position trusses of approved design with structural steel other than MS circular tubes including roof frame work, Supply and Installation of two 5000 Litres HDPE Tanks with Pumping System 1 Running and 1 Stand by inside the constructed RCC structure complete as per Technical specifications for finished item of work as approved by the Engineer-in-Charge. | Job |  |  |  |  | 459000 |  | DCA
131 | Dismantling clearing away and carefully stacking useful materials for re use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges complete Unreinforced cement concrete up to 15cm thickness. (Shabadh stone flooring bottom) | Cum |  |  |  |  | 1700 |  | DCA
132 | Supply, Fabrication and Erection on site MS Emergency Exit Staircase with MS railing confirming to IS 1161 to 1st Floor including Earthwork excavation, PCC 1:4:8 prop., Thermo Mechanically treated steel, RCC M 25 grade Concrete in foundation, Heavy-duty anchor HSL-3-G M16/25 Anchor Bolts, complete as per Technical specifications for finished item of work as directed by the Engineer-in-Charge. | Job |  |  |  |  | 600000 |  | DCA
133 | Supply and fixing of Photoluminiscent Safety Signages and Lab Name Boards etc as per the Technical Specifications. | Job |  |  |  |  | 40000 |  | DCA
134 | Supply erection testing and commissioning of RO Water Purification System of 500 LPH capacity to connect to the existing supplying system as per the directions of the Engineer-in-Charge and as per the Technical Specifications. | Job |  |  |  |  | 350000 |  | DCA
135 | Dismantling,Clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual pre-measurements before diamantling including all labour charges etc., complete. Not Exceeding 3 sqm in area (Wooden partitions / cupboards) | Nos |  |  |  |  | 233 |  | DCA
136 | Earth work excavation for foundations (Manual Means) of buildings, septic tank, sump, compound wall in ordinary soils and depositing on bank with an initial lead of 10m and depth up to 3m including all operational,incidental, labour charges such as shoring, sheeting, planking, strutting etc., and overheads & contractors profit complete for finished item of work excluding dewatering charges etc., as per SS 20 B(APSS 308) (Open Drain) | Cum |  |  |  |  | 237 |  | DCA
137 | Plain Cement Concrete (1:4:8) (cement: fine aggregate: Coarse aggregate) for foundations and under flooring bed using coarse aggregate 40mm size hard , machine crushed granite from approved quarry including cost and conveyance of all materials like cement, sand, coarse aggregate, water etc. to site, including sales & other taxes on all materials and including all charges for machine mixing, laying concrete in foundations and under flooring bed, ramming in 15 cm layers finishing top surface to the required level curing etc., and overheads & contractors profit complete for finished item of work. (APSS No. 402) (Open Drain & Open to sky area) | Cum |  |  |  |  | 3859 |  | DCA
138 | Plain Cement Concrete (1:5:10) (cement: fine aggregate: Coarse aggregate) for foundations and under flooring bed using coarse aggregate 40mm size hard , machine crushed granite from approved quarry including cost and conveyance of all materials like cement, sand, coarse aggregate, water etc. to site, sales & other taxes on all materials and including all charges for machine mixing, laying concrete in foundations and under flooring bed, ramming in 15 cm layers finishing top surface to the required level curing etc.,and overheads & contractors profit complete for finished item of work. (APSS No. 402) Ground Floor ( Connecting corridor ) | Cum |  |  |  |  | 3681 |  | DCA
139 | Plain Cement Concrete (1:3:6) nominal mix using 40mm size machine crushed hard granite metal (coarse aggregate) in (2:1) ratio from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand), coarse aggregate, water etc. to site, sales & other taxes on all materials, all charges for mixing, laying concrete in position, curing charges, overheads & contractors profit etc., for finished item of work for C.C Bed in masonry walls. | Cum |  |  |  |  | 4178 |  | DCA
140 | Providing Thermo Mechanically Treated (TMT) (Fe-500/500D/550D from Primary producer TATA, SAIL, VSP.JSW&Shyam Steel etc as per IS 1786-2008) of different diameters for RCC works, including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting. bending, placing in position, tying including sales and other taxes on all materials etc. ,and overheads & contractors profit complete for finished item of work. APSS No. 126) For Chajjas & Lintels | MT |  |  |  |  | 64900 |  | DCA
141 | Painting to old wood work and flush shutters with two coats of synthetic enamel paint Grade-II Voc (Volatile Organic Compound) content less than 50grams/litre of approved brand and shade including cost and conveyance of all materials to site and all labour charges etc., complete sales & other taxes on cost of all materials etc and overheads & contractors profit complete in all floors (APSS No 1200, 1207 & 1211) (Ceased material store room) | Sqm |  |  |  |  | 109 |  | DCA
142 | Painting two coats with synthetic enamel paint Grade-II VOC (Volatile Organic Compound) content less than 50 grams/litre over primer coat of red oxide to Old iron work including cost and conveyance of all materials to site, sales & other taxes, incidental, operational and all labour charges etc., and overheads & contractors profit complete for finished item of work in all floors. (SS No. 1201, 1212 & 1207). (Ceased material store room) | Sqm |  |  |  |  | 103 |  | DCA
143 | Pre construction Anti termite treatment is a process in which chemical toxic to sub terrain termites is apply/ inject into soil during early stage of building Construction Treatment of soil Beneath the building and around the foundations conduct and chemical use as per BIS - IS 6313 (Part -2) 2013 code specification & CIB RC registered termiticide which creates a continuous chemical barrier beneath the building which kills or repels terminates & impervious to tremite entry Imidacloprid 30.5% SC (IS 63131) dissolve 2.1 Ml/1 liter of water and apply emulsion/solution @ 7.5 Litres/Square meter (Sqm) of internal, external vertical surface of the columns , plinth beams (Back filling) walls and floor junction, external perimeters, along retaining wall @ 5.0 Liters/Sqm of the horizontal surface of basement top surface of the basement filling below flooring bed (Plinth) & @ 2.0 Litres/ Line meter at expansion joints. The substructure of a depth of 500mm around columns & 300mm deep around plinth beams, basements & floor filling area including excavation channel along the wall & rodding etc. cost & Conveyance of all materials to the site, cost of labour for spraying, rodding etc. complete for furnished item of work as per the approval of the Engineer-in-charge (Plinth area measurements will be taken for payment). (DC Lab) | Sqm |  |  |  |  | 152 |  | DCA
144 | Plain Cement Concrete M 20 Nominal mix using Concrete Batching Plant, 20mm size hard granite machine crushed graded metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) from approved quarry, using a minimum quantity of 330 kgs. of cement per 1 cum of concrete including cost and conveyance of all materials like cement, fine aggregate (Sand), coarse aggregate, water etc., to site including steel centering, shuttering, machine mixing, lift charges, laying concrete,vibrating, curing, overheads & contrctors profit etc., complete for finished item of work (APSS No. 402 & 403). Microbiology Room Flooring 2nd Floor. | Cum |  |  |  |  | 6722 |  | DCA
145 | Supplying and fixing of 7.5mm thick Aluminium Grill (as approved by the department) 3.58 Kg/Sqm including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site, overheads and contractor profit etc., complete for finished item of work. (For Electrical Panel Room) | Sqm |  |  |  |  | 1009 |  | DCA
146 | Providing cladding to walls with High Polished Granite 16 to 18 mm thick up to 8'-00 (2.43 M) other than black and regular colours, length equal to flooring slabs set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., and overheads & contractors profit complete for finished item of work. (For entrance) | Sqm |  |  |  |  | 3460 |  | DCA
147 | Supplying and fixing of 30mm thick Wood Plastic Composite (WPC) Door shutter, comprising of 70% virgin polymer, 15% wood powder (fiber), and the remaining 15% additives, the door shutter shall be water resistant, fire resistant and termite resistant, with Tensile Strength not less than 170 Kgf/cm2 and the door shutters surface finished deco paint etc., complete excluding cost of hinges, latches, aldrops etc., and including ISI marked Stainless Steel fixtures 3 Nos. butt hinges (IS:205) of 75mm long, 1 No. aldrop (IS:15834) 200 mm long, 1 No. tower bolt (IS:15833) of 100 mm x 10mm dia, 1 No. 105mm long handles (IS:208), including labour charges for fixing the frame in position, fixing the shutter to the frame etc., including overheads & contractors profit complete for finished item of work as per APSS 1001 & 1002. (The vertical frame of door shall be embedded in flooring for deth of not less than 10mm) (1000mm x 2100mm) (Toilets) | Sqm |  |  |  |  | 2935 |  | DCA
148 | Providing and fixing factory made solid Wood Polymer Composite (WPC) single extruded Door Frame section of 100*65 MM with encapsulation of 6 MM rigid layer on all external surfaces. The door frame will have a rebate of 32MM/ 37 MM. The two Vertical members are to be joined together with the horizontal member using 8x75MM long MS Star full thread screws to be used with reverse forward speed control hand rilling machine. The ready/assembled door frame is fixed to wall using Z Hand fast 300 MM long hold fast. (For Toilets) | Rmt |  |  |  |  | 669 |  | DCA
149 | Supply and placing of Pre-cast RCC slabs of size 600mm x 400mm x 50mm on open drain area including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site including overheads and contractor profit etc., complete for finished item of work. (Open drain) | Nos |  |  |  |  | 575 |  | DCA
150 | Emergency Crash Panel toughend glass of 10mm thickness in Microbiology lab area of size 1000x2100x10mm, accessories, labour charges for transportation, erection at site, complete for finished item of work. (MB Lab) | Nos |  |  |  |  | 39000 |  | DCA
151 | Providing and placing on terrace (at all floor levels) polyetheylene water storage tank with double layer approved brand and manufacture with cover and suitable locking arrangement and making necessary holes for inlet and outlets and over flow pipes but without fittings and base support for tanks including cost and conveyance of all materials and labour charges , overheads & contractors profit complete for finished item of work. (Storage Tanks) | Ltr |  |  |  |  | 7 |  | DCA
152 | Providing 110 mm Dia ISI marked PVC down water take pipes with socket, 2.5mm thick 4.0 kg/sq.cm pressure of ISI marked including cost of necessary PVC Bends, shoes, iron / PVC clamps and all other accessories and fixing in position including cost and conveyance of all materials, sales & other taxes on materials to site, operational & incidental charges including all labour charges for fixing at site etc., and overheads & contractors profit complete for finished item of work. (APSS No. 1328) (Rain water down take pipe from terrace) | Rmt |  |  |  |  | 255 |  | DCA
153 | Supply and Fixing of name Boards with approved names on Acrylic sheet including cost of materials, cutting printing names and fixing particulars location labour charges etc., complete for finished item of work Acrylic 3mm signage boards for Size 6"x24" (Item already approved in Genetic Lab, NIMS work) | Each |  |  |  |  | 850 |  | DCA
154 | 100 mm thick double skin Walls panels of Modular clean room walls panel system | Sqm |  |  |  |  | 4256 |  | DCA
155 | 100 mm thick double skin Walls panels of Modular clean room walls panel system with return Air Raisers and Grill | Sqm |  |  |  |  | 5376 |  | DCA
156 | 50 mm thick double skin Walls panels of Modular clean room walls panel system | Sqm |  |  |  |  | 3136 |  | DCA
157 | 50 mm thick double skin Ceiling panels of Modular clean room ceiling panel system | Sqm |  |  |  |  | 3696 |  | DCA
158 | Providing and Fixing of Scientific Doors as per Technical Specifications. | Sqm |  |  |  |  | 12500 |  | DCA
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212
213
214
215
216
217
218
219
220
221
222
223
224
225
226
227
228
229
230
231
232
233
234
235
236
237
238
239
240
241
242
243
244
245
246
247
248
249
250
251
252
253
254
255
256
257
258
259
260
261
262
263
264
265
266
267
268
269
270
271
272
273
274
275
276
277
278
279
280
281
282
283
284
285
286
287
288
289
290
291
292
293
294
295
296
297
298
299
300
301
302
303
304
305
306
307
308
309
310
311
312
313
314
315
316
317
318
319
320
321
322
323
324
325
326
327
328
329
330
331
332
333
334
335
336
337
338
339
340
341
342
343
344
345
346
347
348
349
350
351
352
353
354
355
356
357
358
359
360
361
362
363
364
365
366
367
368
369
370
371
372
373
374
375
376
377
378
379
380
381
382
383
384
385
386
387
388
389
390
391
392
393
394
395
396
397
398
399
400
401
402
403
404
405
406
407
408
409
410
411
412
413
414
415
416
417
418
419
420
421
422
423
424
425
426
427
428
429
430
431
432
433
434
435
436
437
438
439
440
441
442
443
444
445
446
447
448
449
450
451
452
453
454
455
456
457
458
459
460
461
462
463
464
465
466
467
468
469
470
471
472
473
474
475
476
477
478
479
480
481
482
483
484
485
486
487
488
489
490
491
492
493
494
495
496
497
498
499
500
501
502
503
504
505
506
507
508
509
510
511
512
513
514
515
516
517
518
519
520
521
522
523
524
525
526
527
528
529
530
531
532
533
534
535
536
537
538
539
540
541
542
543
544
545
546
547
548
549
550
551
552
553
554
555
556
557
558
559
560
561
562
563
564
565
566
567
568
569
570
571
572
573
574
575
576
577
578
579
580
581
582
583
584
585
586
587
588
589
590
591
592
593
594
595
596
597
598
599
600
601
602
603
604
605
606
607
608
609
610
611
612
613
614
615
616
617
618
619
620
621
622
623
624
625
626
627
628
629
630
631
632
633
634
635
636
637
638
639
640
641
642
643
644
645
646
647
648
649
650
651
652
653
654
655
656
657
658
659
660
661
662
663
664
665
666
667
668
669
670
671
672
673
674
675
676
677
678
679
680
681
682
683
684
685
686
687
688
689
690
691
692
693
694
695
696
697
698
699
700
701
702
703
704
705
706
707
708
709
710
711
712
713
714
715
716
717
718
719
720
721
722
723
724
725
726
727
728
729
730
731
732
733
734
735
736
737
738
739
740
741
742
743
744
745
746
747
748
749
750
751
752
753
754
755
756
757
758
759
760
761
762
763
764
765
766
767
768
769
770
771
772
773
774
775
776
777
778
779
780
781
782
783
784
785
786
787
788
789
790
791
792
793
794
795
796
797
798
799
800
801
802
803
804
805
806
807
808
809
810
811
812
813
814
815
816
817
818
819
820
821
822
823
824
825
826
827
828
829
830
831
832
833
834
835
836
837
838
839
840
841
842
843
844
845
846
847
848
849
850
851
852
853
854
855
856
857
858
859
860
861
862
863
864
865
866
867
868
869
870
871
872
873
874
875
876
877
878
879
880
881
882
883
884
885
886
887
888
889
890
891
892
893
894
895
896
897
898
899
900
901
902
903
904
905
906
907
908
909
910
911
912
913
914
915
916
917
918
919
920
921
922
923
924
925
926
927
928
929
930
931

## EQP & FUR
S.No | Description | UOM | Rate
SOTC
1 | Dynamic Hatch Box | Nos | 295000
2 | Electro conductive Flooring inside MOTs | Sqm | 4035
3 | Pressure Relief Dampers | Nos | 22500
4 | Single arm Anesthesia Pendants (Imported) | Nos | 1195000
5 | Triple Dome Ceiling OT LED Lights (Imported) | Nos | 4750000
6 | Double Dome Ceiling OT LED Lights (Imported) | Nos | 3550000
7 | Detachable Hi Definition Cameras in Triple Dome Ceiling OT Lights | Nos | 995000
8 | Ceiling/Wall mounted CCTV Room Camera | Nos | 22500
9 | LED Peripheral Lights cum clean room (OT) luminaries | Nos | 18750
10 | View Window with Motorised Blinds of 1 Mt Length & 1 Mt Height | Nos | 115000
11 | Hermetically Sealed Doors (1.80mt x 2.10 mt) | Nos | 115000
12 | (1.50mt x 2.10 mt) Sliding Automatic Sliding Doors with View Windoy of 1 Mt x 1 Mt | Nos | 525000
13 | Storage Units | Nos | 75000
14 | Writing Board (List Board) | Nos | 18750
15 | X-Ray CT Scan LED viewing Screen | Nos | 37500
16 | Touch Screen Surgeon Control Panels | Nos | 385000
17 | 3-Bay Scrub Stations/Sinks | Nos | 368750
18 | Video and Image Management system | Nos | 8000000
19 | Medical Grade Monitors 32 inch 4 K Resolution | Nos | 1295000
20 | Wall mounted large screen display 55 inch (Commercial Grade) | Nos | 495000
21 | Cable connections for integration within MOTs and with Workshop Projector Hall, Networks with OFC Cable | Job | 997500
22 | Wireless Microphone | Nos | 255000
23 | Digital mixer Amplifier | Nos | 245000
24 | Ceiling Mounted Speakers | Nos | 15000
25 | Video Conferencing System | Nos | 1195000
26 | Home Theatre Power Conditioner, 230 V | Nos | 145000
27 | Amplifier (8 Channel) | Nos | 245000
28 | HiFi Active Sub Woofer | Nos | 50000
29 | 4K Laser Projection TV | Nos | 1495000
30 | Equalization & Loud Speaker Control System | Nos | 40000
31 | Sound Analog Mixer | Nos | 245000
32 | Pressure Relief Dampers | Nos | 22500
33 | Hermetically Sealed Doors (1.80mt x 2.10 mt) | Nos | 525000
34 | 12mm thick glazed Glass partition walls in TIRs | Sqm | 650
35 | Wall mounted LED TV43 inchesFull HD | Nos | 165000
36 | Ceiling/Wall mounted CCTV Room Camera | Nos | 12000
37 | BED HEAD PANEL FOR TIR WITH DOUBLE OUTLETS AND ELECTRICAL OUTLETS | Nos | 49500
38 | X-RAY VIEWERS FOR ALL ICUS AND PRE OPP AREAS AND DOCTORS ROOMS | Nos | 37500
39 | WRITING BOARDS FOR ICUS, PRE OPP | Nos | 18750
40 | Double Arm Surgical Pendant | Nos | 1195000
IVFs
41 | Ovum Aspiration Pumps at Gandhi Hospital | No | 240000
42 | IVF Test tube Warmers at Gandhi Hospital | No | 49500
43 | DICOM compatible fully digital, compact, portable, Ultrasound Scan Machine Colour Doppler at Gandhi Hospital | No | 1365000
44 | Multipurpose Electro hydraulic with manual override mobile OT Table, with divided leg section suitable for all Gynaecological surgical procedures, complete with 5cm Mattress and corded handset at Gandhi Hospital | No | 563750
45 | LED procedure Lights Double dome at Gandhi Hospital | No | 312500
46 | LED procedure Lights Single dome at Gandhi Hospital | No | 187500
47 | IVF Workstation with LAF at Gandhi Hospital | No | 687500
48 | IVF Ant vibration Table for procedure at Gandhi Hospital | No | 96250
49 | CO2 Incubators at Gandhi Hospital | No | 825000
50 | Trigas bench Top Incubators for Human Embryo culture at Gandhi Hospital | No | 825000
51 | Trinocular Stereozoom Microscope at Gandhi Hospital | No | 309000
52 | ICSI Micro manipulator with Inverted Microscope at Gandhi Hospital | No | 2625000
53 | IVF Laser System at Gandhi Hospital | No | 2560000
54 | IVF Thermometer at Gandhi Hospital | No | 61875
55 | CO2 Cylinder and Manifold at Gandhi Hospital | No | 50000
56 | CO2 and O2 Analyzer at Gandhi Hospital | No | 378000
57 | PH Meter at Gandhi Hospital | No | 93750
58 | VOC Meter for ART Lab at Gandhi Hospital | No | 731250
59 | Sperm Counting Makler Chamber at Gandhi Hospital | No | 75625
60 | Binocular Microscope for Semen Analysis at Gandhi Hospital | No | 41250
61 | Laminar flow cabinet with Andrology Work station at Gandhi Hospital | No | 250000
62 | Clinical Centrifuge machine for Andrology at Gandhi Hospital | No | 34500
63 | Dry Incubators at Gandhi Hospital | No | 563750
64 | Pipetter and Denudation system at Gandhi Hospital | No | 103125
65 | Pharmaceutical Refrigerator at Gandhi Hospital | No | 225000
66 | Cryocans with wheels at Gandhi Hospital | No | 61875
67 | Defibrillator at Gandhi Hospital | No | 312500
68 | 7 Para Patient Monitor at Gandhi Hospital | No | 280000
69 | Suction machine at Gandhi Hospital | No | 49500
70 | Anaesthesia Work station at Gandhi Hospital | No | 937500
71 | Autoclave at Gandhi Hospital | No | 562500
72 | Operative Hysteroscopy and Resectoscope Set Machine at Gandhi Hospital | No | 2125000
73 | Operative Laparoscopy Set at Gandhi Hospital | No | 4200000
74 | Multifunctional Printer at Gandhi Hospital | No | 43750
75 | Ultrasound Examination Couch at Gandhi Hospital | No | 81250
76 | UPS 20KVA with battery backup at Gandhi Hospital | No | 0
77 | Laptop for Office usage at Gandhi Hospital | No | 115000
78 | Reception Table at Gandhi Hospital | No | 110000
79 | Reception chair at Gandhi Hospital | No | 34500
80 | Filing Cabinet at Gandhi Hospital | No | 34500
81 | Patient Seating 3 in 1 model at Gandhi Hospital | No | 38500
82 | Consultant Chair at Gandhi Hospital | No | 19250
83 | Patient Chair at Gandhi Hospital | No | 13750
84 | Small Trolley at Gandhi Hospital | No | 39200
85 | Big Trolley at Gandhi Hospital | No | 62500
86 | Wall Storage Cabinets at Gandhi Hospital | No | 17500
87 | Office Table at Gandhi Hospital | No | 20000
88 | Fowler Two Function Bed with ABS Panel, ABS Side Railings, Wheels, Mattress Pillow, & Bed Fixing IV Road Features (Knee rest & Backrest) Size-L,84, W-42, H-24. The finished bed must be rust proof, pre-treated and treated with epoxy polyester antimicrobial powder coated to increase the bacteriostatic property. The bed must be quoted with washable cover of lasting quality. The mattress should be made of high-density PU foam of 100 mm thickness. | Nos | 39000
89 | Bed side Table with ABS Plastic body construction having 1 drawer and an adequated space with openable door with handle of size | Nos | 9000
90 | Corporate Deluxe Locker with SS 304 grade Top of size 508 x 406 x 762 mm having 1 drawer and an adequate storage space with openable door with SS handle. Equipped with wheels for easy movement. | Nos | 8400
91 | Bed side stand with full SS 304 grade constructionof size 406 x 203 x 762 mm equipped with SS Handles on top for carrying. | Nos | 9300
92 | Bed side stand with full GI Powder coated constructionof size 406 x 203 x 762 mm equipped with powder coated handles on top for carrying. | Nos | 4200
93 | Cryo Can 11 Ltr without wheels | Nos | 32000
94 | 3-Bay Surgical Scrub Station/Sink to be provided for use in the OT complex providing for pre-procedural scrub up with minimum three bay sink combination as suitable. The Scrub Station shall be made of Stainless Steel of 304 grade sheet with minimum thickness of 1.5mm and designed as per the high aesthetics of the theatre complex. Shall have smoothened surfaces & corners. The scrub sink shall be provided with a front access panel which shall be easily removed for access to the water-controlled valve, waste connections, stoppers & strainers. The Scrub station should be equipped with two foot operated and one elbow operated mechanisms. Shall have provision for fresh water and waste water piping ready for connections. | Nos | 97000
95 | Supply of Sample collection bed of size 1850x620x700 mm, featuring plain design equipped with 1 drawer and storage space with openable door type with SS-304 grade handles positioned at head side of the bed. The material of construction of the bed to be of Powder coated GI for entire body. All the legs of the bed to be capped with nylon bushes. The finished bed must be rust proof, pre-treated and treated with epoxy polyester antimicrobial powder coated to increase the bacteriostatic property. The bed must be quoted with washable cover of lasting quality. The mattress should be made of high-density PU foam of 100 mm thickness. | Nos | 29000
96 | Supply of a Sample collection chair of size 800x580x700 mm, meeting medical standards, featuring adjustable height and tilt padded armrests, and durable upholstery, suitable for comfortable patient positioning during blood donation or phlebotomy procedures. The chair is made from mild steel with good finish. The chair to be of easy to manoeuvre and transport and of light weight. | Nos | 16200
97 | Supply and installation of Stainless Steel 304 grade CSSD Rectangular Working table of size 1200x480x1050 mm with inbuilt sink of size 450x380x300 mm equipped with jali at bottom to stop any large particles entering into the drain to avoid drain clog. The table to be designed with raised front section and provision of SS sheet at foot level of the table forming a flat surface for storing/placing of items. The table to be of ready to use with all necessary fittings. | Nos | 46000
98 | Writing board made of Pressed wood coated with melamine surface. It has 900mm writing surface height, 1200mm writing surface wide, and 11mm deep, suitable for working on dry wipe board markers. It has an aluminium frame with dark grey plastic corner caps and maker tray. It is enabled with an easy wall mounting with a concealed slot system. It can be mounted either horizontally or vertically. IT consists of a complete mounting set, marker tray, and a board marker | Nos | 2100
99 | Providing MDF 18 mm thick wooden table of size 900x450 mm with 1 drawer at right side of the table. The table includes keyboard tray. Bottom equipped with nylone bushes for floor protection and easy movement. | Nos | 14500
100 | Supply of a 3-seater sofa upholstered with PU leather, with a high-quality finish. The sofa shall feature a kiln-dried hardwood frame for durability, reinforced with corner blocks for stability. The seat cushions to be constructed with high-density foam padding for comfort and resilience, while the backrests shall feature a combination of foam and fiberfill for optimal support. The sofa arms shall be padded for additional comfort, with sleek wooden or metal legs providing sturdy support. The leather upholstery shall be treated for resistance to stains and spills, ensuring longevity and ease of care. The dimensions of the sofa shall be suitable to accommodate three individuals comfortably, with ample seating space and ergonomic design considerations. | Nos | 24000
101 | SS-304 working table of size 685x685x762 mm with I type support inner frame SS-304 pipe of size 40x40x1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. | Nos | 16300
102 | SS-304 working table of size 457x457x762 mm with I type support inner frame SS-304 pipe of size 40x40x1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. | Nos | 14500
103 | SS-304 working table of size 610x610x762 mm with I type support inner frame SS-304 pipe of size 40x40x1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. | Nos | 15100
104 | SS-304 working table of size 660x610x762 mm with I type support inner frame SS-304 pipe of size 40x40x1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. | Nos | 15800
105 | Supply and fixing of Powder coated GI stand with 4 nos height adjustable racks of size 670x410x1570 mm connected to two big rods of rectangular hollow section type supported with 4 legs with wheels with brakes to restrict movement/easy movement. Equipped with frame for holding a cylinder. A lockable box type space to be provided at bottom rack. | Nos | 80000
106 | The Multipurpose Electro Hydraulic Mobile OT Table is designed for gynecological surgical procedures, featuring a wide range of adjustments for optimal patient positioning. It offers precise control with movement controls at the side of the table and a wired remote control handset and features like S. S. Arm Rest, Anaesthetic Screen, Lithotomy Leg Holders with Stirr-Ups, Leather Wristlets, Padded Leg Rest, Anti-static mattress, and an additional Poly-urethane mattress. Built with a Stainless Steel 304 frame and bottom, it ensures durability. The table top, reinforced with three-section stainless steel and radiolucent capabilities, allows for comprehensive patient support. Its flexibility includes 360° rotation, adjustable Trendelenburg, Reversed Trendelenburg, Head Section, Back Section, and Leg Section. Physical specifications include a 1900 mm x 525 mm top with an elevation range of 640mm to 1040mm, supporting patients up to 140 kg. Environmental considerations ensure operational efficiency in various conditions. | Nos | 210000
DCA
107 | Lab furniture with accessories :
108 | C Shaped Sitting Height Work Bench | No | 215000
110 | J Shaped Sitting Height work Bench with Sink | No | 260000
112 | Standing Height Works Bench | No | 80000
114 | Standing Height Work Bench with Sink | No | 170000
116 | L Shaped Standing Height Work Bench with Sink | Nos | 130000
118 | Standing Height Island Work Bench | Nos | 210000
120 | Standing Height Anti Vibration Tables | Nos | 25000
122 | Apron Cabinet | Nos | 63000
124 | Open Storage Racks | Nos | 7000
126 | Vertical Storage Cabinet | Nos | 31500
128 | Sitting Height Work Bench | Nos | 90000
130 | Sitting Height Work Bench with H-frame table | Nos | 130000
132 | Overhead Wall Storage Cabinets | Nos | 9000
134 | Vertical Acid Corrosives Storage cabinets | Nos | 74000
136 | Vertical Solvent Flammables Storage Cabinets | Nos | 140000
138 | SS Garment Disposable Bin Tilting Type | Nos | 9000
140 | Lab Chairs Type I | Nos | 15340
142 | Lab Chairs Type II | Nos | 6435
144 | Linear work Stations | Nos | 40000
146 | Crossover bench | Nos | 41000
148 | SS Double Rack Trolleys | Nos | 18000
150 | Equipment
151 | De-Dusting Chamber | Nos | 680000
152 | Spot Extractors | Nos | 19500
154 | 5 Feet Bench Top Fume Hood | Nos | 174000
156 | Dynamic Pass Box | Nos | 390000
158 | Laminar Air Flow Cabinet | Nos | 770000
160 | Bio Safety Cabinet | Nos | 890000
164 | Office Furniture :
165 | Task Chairs | Nos | 8700
167 | Manager Chair | Nos | 15000
169 | Manager Work Station | Nos | 30500
170 | Placement of vertical autoclave in wash and decontamination area duly following the below steps: 1)Removing of 2 Sceintific door for entry and placing of the vertical Autoclave 2) Removing of Existing 50mm wall panels, 3)Removing electrical cables and sockets, 4)Removing of electrical switches, 5)Dismantling of electrical service drop, 6)Dismantling of work station, 7)cutting and bull nose of granite,8) Laying of New RO line for vertical autoclave, 9) drain line for vertical autoclave, 10)removing and re applying of Epoxy Coving works in Wash and Decontamination room in Microbiology lab area 11) Retermination of Electrical switches, sockets and electrical cables. 12) Re-fixing of 50mm wall panels and doors (Wash & Decontamination area MB Lab) | Job | 325000

## Electrical
S.No | Description | UOM | Rate
SOTC
1 | Electrical Installations in MOTs & TIRs | Job | 195000
2 | Supply and Fixing of 25mm dia Conduit Pipes surface on wall. | Rmt | 110
3 | Supply and Fixing of 25mm dia Conduit Pipes Concealed on wall. | Rmt | 115
4 | Wiring with run of 2 of 1.5 Sqmm Copper cable for points wiring. | Pts | 1525
5 | Wiring with run of 2 of 1.5 Sqmm Copper cable for stairecase points wiring. | Pts | 1100
6 | Supply and fixing of 6A/10A ISI Mark 3/2 pin Modular socket Common switch board | Pts | 900
7 | Wiring with 3 of 1.5 sq.mm with 6A switch and 6A, 3/2 pin socket Modular type with 6A switch control fixing on separate board. | Pts | 2800
8 | Supply and fixing of 6A switchs - 2 Nos and 6A 3/2 pin socket - 3 Nos Modular type with cover plate | Pts | 1400
9 | Supply & fixing of 16A/6A, 2 in one socket with 16A switch control modular type | Nos | 900
10 | Supply & fixing of 32A, socket with switch control modular | Nos | 1600
11 | Supply & fixing of 64A, socket with 64A switch control modular type | Nos | 18000
12 | Supply and Run of 1 of 1.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 36
13 | Supply and Run of 3 of 1.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable . | Rmt | 100
14 | Supply and Run of 3 of 2.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 145
15 | Supply and Run of 3 runs of 4.0 sq mm (phase neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 230
16 | Supply and Run of 3 of 6.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 325
17 | Supply and Run of 5 of 6.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 545
18 | Supply and Run of 5 of 10.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 850
19 | Supply and fixing of DP Metal Enclosure with IP 20 Protection DB Make with 1 No 20A, 10 KA DP MCB | Nos | 1800
20 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 (For Lighting DBs) | Nos | 13000
21 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 (For Power DB's) | Nos | 13000
22 | Supply and fixing of 8 Way VTPN DB with IP 43 Protection as per IS:13032 | Nos | 50000
23 | Supply and fixing of cable adopteres box with cover for DBs including, massanory work etc., complete., | Nos | 6000
24 | Providing independent earthing for Important equipment with 40mm dia 'B' class 2.5m long G.I pipe (GI Earthing) | Nos | 22500
25 | Providing independent earthing by exacavating a pit to a depth of 2.25Mtr in all soils as per size specified in the data for Sophisticated Electronic equipment (Copper Earthing) | Nos | 54000
26 | Providing independent earthing for Important equipment with 100mm dia Heavy gauge C.I Earthing | Nos | 25000
27 | Supply and Run of 50mm x 6mm G.I Strip | Rmt | 450
28 | Supply and Run of 25mm x 3mm copper strip | Rmt | 300
29 | Supply, transportation and fixing of 22W +/ 10% , >/ 2300 lumens, 1200mm length LED light | Nos | 4800
30 | Supply, transportation and fixing 32-36W (>=3600 Lumens), 2' x2' (600mm x 600mm) slim panel LED luminaire | Nos | 4000
31 | Supply, transportation and fixing 12 W +/-10% (>= 1200 Lumens) Down lighter back lit LED Down Light Recessed / Surface | Nos | 1400
32 | Supply, transportation and fixing 18 W +/-10% (>= 1800 Lumens) Down lighter back lit LED Down Light | Nos | 1800
33 | Supply, transportation and fixing ISI mark batten holder / slanting holder | Nos | 160
34 | Supply, Transportation of energy efficient fan, 1200 mm sweep, aluminium body, consuming 28 W, BEE 5 star rated, ceiling fan | Nos | 3700
35 | Supply and fixing of Modular type Stepped electronic regulator. | Nos | 1000
36 | Labour charges for fixing of ceiling fan and regulator | Nos | 210
37 | Supply and erecting 19/20mm steel tube down rod of one meter length | Nos | 600
38 | Supply of 12" (300mm) Light duty exhaust fan | Nos | 3000
39 | Supply,Transportation of 12" (300mm) ISI, 900 RPM Heavy duty exhaust fan | Nos | 4900
40 | Labour charges for fixing the exhaust fan in wall with necessary connections | Nos | 900
41 | Supply and fixing of GI louver shutter including GI mesh | Nos | 3200
42 | Main Power Panel with 1000A 4 Pole ACB as incomer - 1 No and out goings 800 A 4P MCCB - 1 No., 630 A 4P MCCB - 1 No., 400A 4P MCCB - 4 Nos & 250A 4P MCCB - 3 No's with required Digital Ammeter and Voltmer, LED Indicators | Nos | 1315000
43 | Floor Power Panel : Incomer: 630A 4 Pole MCCB,- 1 No Outgoings 250 A 4P MCCB - 4 No's 125 A 4P MCCB - 10 No's, 63 A 4P MCCB - 4 No's with required Digital Ammeter and Voltmer, LED Indicators | Nos | 875000
44 | Electrical Lighting Panels : Incomer: 250 A 4 Pole MCCB - 1 No, Out Goings 125 A 4P MCCB - 4 No's 63 A 4P MCCB - 3 No's with required Digital Ammeter and Voltmer, LED Indicators | Nos | 370000
45 | 130KVAR Out Door Capacitor panel : Incomer: 250A FP MCCB - 1 No, 63A 10KA TP MCB - 9 Nos. 20 KVAR Capacitor Duty contactors - 5 Nos., 10 KVAR Capacitor Duty contactors - 2 Nos, .5 KVAR Capacitor Duty contactors - 2 Nos. 12 stage APFC Relay - 1 No | Nos | 450000
46 | 630 KVA Transformer OLTC for transformers with RTCC: Supply, Transportation, Installation, Testing and Commissioning of 630 KVA TRANSFORMER with all test reports. The Transformer shall be designed and manufactured as per IS:1180 OLTC with level-II with initial filling of oil as per IS 335-1993. 1000 A LT Breaker Kiosk - 01 No.The basic details of the Transformer are as under. Makes: Kirloskar / PETE / Esennar / Voltamp / Crompton / ABB / Schneider. | Nos | 4000000
47 | Supply of 25 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 300
48 | Supply of 50 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 560
49 | Supply of 70 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 750
50 | Supply of 120 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 1050
51 | Supply of 185 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 1500
52 | Supply of 240 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 1900
53 | Supply of 300 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 2400
54 | Termination of UG cables of 3.5 core 25 Sq.mm | Nos | 850
55 | Termination of UG cables of 3.5 core 50 Sq.mm | Nos | 1200
56 | Termination of UG cables of 3.5 core 70 Sq.mm | Nos | 1500
57 | Termination of UG cables of 3.5 core 120 Sq.mm | Nos | 1900
58 | Termination of UG cables of 3.5 core 185 Sq.mm | Nos | 2500
59 | Termination of UG cables of 3.5 core 240 Sq.mm | Nos | 3500
60 | Termination of UG cables of 3.5 core 300 Sq.mm | Nos | 4000
61 | Earth work excavation of Trench laying of U.G cables up to 70 sqmm | Rmt | 1100
62 | Earth work excavation of Trench laying of U.G cables from 95 Sqmm | Rmt | 1150
63 | Laying of PVC armoured under ground cable up to 95 Sqmm on wall | Rmt | 125
64 | Laying of PVC armoured under ground cable from 120 Sq.mm to 400 Sqmm saddles on wall | Rmt | 270
65 | Supply, Transportation and Installation of 150mm x 50mm x 2mm thick hot dip GI perforated cable tray | Rmt | 1295
66 | Supply, Transportation and Installation of 300mm x 50mm x 2mm thick thick hot dip GI perforated cable tray | Rmt | 4500
67 | Supply, Transportation and installation of 10KVA / 312V DC on line UPS system | Nos | 400000
68 | Supply and fixing of 12V, 150 AH MF battery | Nos | 25000
70 | Supply and providing of UPS cum battery rack 20 batteries | Nos | 30000
72 | Supply, Transportation, Installation, Testing and commissioning of storage / Pressure type 5 Star rated water heater with ABS plastic body of 15 Ltrs | Nos | 16000
73 | Supply, Transportation and installation of 20KVA / 312V DC on line UPS system (for emergency lighting in all rooms & Corridor except OTs & TIRs) | Nos | 629358
74 | 800 KVA Transformer OLTC for transformers with RTCC: Supply, Transportation, Installation, Testing and Commissioning of 800 KVA TRANSFORMER with all test reports. The Transformer shall be designed and manufactured as per IS:1180 OLTC with level-II with initial filling of oil as per IS 335-1993. 1000 A LT Breaker Kiosk - 01 No.The basic details of the Transformer are as under. Makes: Kirloskar / PETE / Esennar / Voltamp / Crompton / ABB / Schneider. | Nos | 4814994
75 | 750 KVA Generator Set with AMF Control Panel Supply, Transportation, erection and commissioning (Excluding Foundation) of 3 Phase, 415, 50Hz, water cooled multi cylinder diesel generator set with alternator of 750 KVA output continuous rating directly coupled Engine and Alternator 750 KVA, 415 Volts with guard and mounted on a common base plate of Robust construction and complete with AMF panel having IP-52 protection, Acoustic Enclosure as per CPCB norms , sound absorbing material, t to restrict sound level up to 75 dB up to 1 Mtr distance and as per CPCB norms etc. | Nos | 9540000
IVFs
76 | Supply and laying of ISI 25mm outer dia medium grade with IS:9537-part 3 rigid PVC pipe concealed in wall with all required PVC / Metallic Junction Boxes including masonry work and labour charges etc., Makes: Sudhakar / Precision /Universal/ Modi / Million Plast. at Gandhi Hospital | Rmt | 116
77 | Supply and laying of ISI 25mm outer dia medium grade with IS:9537-part 3 rigid PVC pipe surface on wall with all required PVC / Metallic Junction Boxes including masonry work and labour charges etc., Makes: Sudhakar / Precision /Universal/ Modi / Million Plast. at Gandhi Hospital | Rmt | 107
78 | Wiring with 2 runs of 22/0.3mm 1.5 Sq.mm FRLS / HFFR P.V.C. insulated flexible copper cable ISI MARK in existing pipe with 6A Modular switch, Ceiling rose/BH/SBH Modular switches with cover plate and GI switch box including all labour charges etc., complete. for Non- Residential Building Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. Makes of switches: - GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/Gold Medal curve. at Gandhi Hospital | Pts | 945
79 | Supply and fixing of 6A ISI Mark 3/2 pin Modular socket with 6A 1way Modular switch, 3 Module box with cover frame and GI switch box on common switch board with connections etc., complete. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. Makes of switches: - GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/Gold Medal curve. at Gandhi Hospital | No | 675
80 | Supply and fixing of 16A switches - 1Nos and 6/16A 2 in one socket - 1Nos Modular type with cover plate and GI switch box fixing on separate board including all labour charges etc., complete. Makes of switches: - GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/Gold Medal curve. at Gandhi Hospital | No | 1040
81 | Supply and fixing of 16A/6A, 2 in one socket - 2 Nos with 16A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: - GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/Gold Medal curve. at Gandhi Hospital | No | 1755
82 | Supply and fixing of 16A/6A, 2 in one socket - 4 Nos with 16A switch control - 4 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: - GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/Gold Medal curve. at Gandhi Hospital | No | 3092
83 | Supply and run of 1 of 22 /0.3mm 1.5 Sq.mm FRLS / HFFR P.V.C. insulated flexible copper cable in existing conduit pipe for earth continuity including all labour charges etc., complete. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at Gandhi Hospital | Rmt | 40
84 | Supply and run of 3 of 2.5 sq.mm 36/0.3mm phase neutral and earth FRLS / HFFR PVC insulated flexible copper cable in existing conduit pipe for individual lighting circuits including labour charges etc., complete as required for switch boards. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at Gandhi Hospital | Rmt | 177
85 | Supply and 3 runs of 4.0 sq mm 56/0.3 mm phase neutral and earth FRLS / HFFR PVC insulated flexible copper cable in existing conduit pipe including labour charges etc., complete for 16A sockets. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at Gandhi Hospital | Rmt | 255
86 | Supply and run of 5 of 6.0 Sqmm 90/0.3 mm 3 phases, neutral and earth FRLS / HFFR PVC insulated flexible copper cable in the existing conduit pipe for run of mains from Power panel board to TPN DBs with pin type lugs and connections etc., complete. for LDBs Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at Gandhi Hospital | Rmt | 606
87 | Supply and run of 5 of 10.0 Sqmm 140/0.3 mm 3 phases, neutral and earth FRLS / HFFR PVC insulated flexible copper cable in the existing conduit pipe for run of mains from Power panel board to TPN DBs with pin type lugs and connections etc., complete. for PDBs Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at Gandhi Hospital | Rmt | 967
88 | Supply and fixing of DP Metal Enclosure with IP 20 Protection DB Make with 1 No 20A, 10 KA DP MCB Make: Legrand / Schneider including internal connection and labour charges for Flush Mounting etc., complete. Makes: Legrand / Schneider. at Gandhi Hospital | No | 2562
89 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand / Schneider and Supply and Fixing of 1 No., of 40A FP 30mA RCCB as incomer and 12 Nos 6-32 A 10kA SP MCBs Makes: Legrand-DX3 / Schneider-Acti9 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. For Lighting DBs at Gandhi Hospital | No | 18325
90 | Supply and fixing of 8 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand / Schneider and Supply and Fixing of 1 No., of 63A FP 100mA RCCB as incomer and 24 Nos 6-32 A 10kA SP MCBs Makes: Legrand-DX3 / Schneider-Acti9 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. For Lighting DBs At Gandhi Hospital | No | 28460
91 | Supply and fixing of 8 Way VTPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand / Schneider and Supply and Fixing of 1 No., of 100A FP 10KA MCB as incomer and 4 Nos 63 A 10kA TP MCBs, 4 Nos 40 A 10kA TP MCBs Makes: Legrand-DX3 / Schneider-Acti9 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. For UPS MDB DBs At Gandhi Hospital | No | 64067
92 | Providing and fixing of 125A 25KA TPN Thermal Magnetic Release Based MCCB and Terminal Spreaders in Existing panel board with 1 No. and 1 Set of Indication Lamps, LED type, R,Y,B and breaker ON , OFF, TRIP and spring charged lamps. and replace with above Mentioned with required Drilling Holes, removing and Making Busbar connections etc, as required. Makes: Legrand / Schneider/ABB/LandT/CandS At Gandhi Hospital | No | 28883
93 | Providing and fixing of 100A 10KA FP MCB and Terminal Spreaders in IP 43 isolator Box Making connections etc, as required. Makes: Legrand / Schneider/ABB/LandT/CandS At Gandhi Hospital | No | 3260
94 | Supply, transportation and fixing of 24W edge lit LED Down light Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser Square with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor greater than 0.9, Surge protection: greater than 2KV, System efficacy of greater than100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI greater than80, and THD is less than 15percentage etc., with BIS Certification. Makes: Phillips / OSRAM / Wipro / Crompton / Bajaj / Havells At Gandhi Hospital | No | 2652
95 | Supply and Transportation 36W Edge lit, 2 feet x2 feet 600mm x600mm slim panel LED luminaire Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor greater than 0.9, Surge protection greater than 2KV, System efficacy of greater than100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI greater than80, and THD is less than 15percentage etc., complete. Makes: Phillips / OSRAM / Wipro / Crompton / Bajaj / Havells At Gandhi Hospital | No | 4350
96 | Supply and Transportation 42W Clean room Light fixture, 2 feet x2 feet 600mm x600mm LED luminaire CRCA powder coated white after phosphocreatine treatment provided as standard. with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor greater than 0.9, Surge protection greater than 2KV, System efficacy of greater than100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI greater than80, and THD is less than 15percentage etc., complete. MAKE: OSRAM / Wipro / Crompton / Bajaj / Havells At Gandhi Hospital | No | 4762
97 | Supply and fixing of ISI mark batten holder / slanting holder Makes : Anchor/ Gold Medal Olive / Million Zoom in lieu of ceiling rose of light point complete with all connections and all labour charges with 5.0W LED Lamp MAKE: OSRAM / Wipro / Crompton / Bajaj / Havells At Gandhi Hospital | No | 184
98 | Supply, Transportation of energy efficient fan, 1200 mm sweep, aluminium body, consuming 28 W, BEE 5 star rated, ceiling fan with Brush Less Direct Current BLDCmotor, class of insulation: B, 3 nos blades, 30 cm long down rod, 2 nos canopies, shackle ‘kit, safety rope, copper winding, Power Factor greater than 0.90, Service Value CMMAV greater than 8.5, Air delivery minimum 235 CMM,350 RPM tolerance as per IS:374-2019, THD less than 10percentage. with remote or compatible to electronic step type regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise equal to75 degree Cmax, insulation resistance more than 2 mega ohm, suitable for 230V, 50 HZ, single phase AC supply, earthing etc., including all standard accessories etc., complete. Makes : Atomberg Efficio / Havells /Orient At Gandhi Hospital | No | 4090
99 | Supply and fixing of Modular type Stepped electronic regulator Makes : GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/ Cabtree Verna/ Million logus / Gold Medal Curve for sweep AC ceiling fans of 1200mm / 1400mm complete with connections. At Gandhi Hospital | No | 827
100 | Supply and installation of 225mm Light duty exhaust fan with metal blades etc complete Makes: Crompton / Havells Ventilair-DB/ Orient hill air. At Gandhi Hospital | No | 2203
101 | SITC of Hot dip galvanized perforated cable tray of 100 mm Wide sizes for to run the cable from DBs to SBs and sockets and AC panel to Units units. All necessary supports and accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. At Gandhi Hospital | Rmt | 429
102 | SITC of Hot dip galvanized perforated cable tray of 300 mm Wide sizes for to run the cable from Floor Panel to Lab Panel and electrical room to AC panel and AC panel to Units. All necessary supports and accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. At Gandhi Hospital | Rmt | 1310
103 | Supply and installation of 20KVA 3ph in and 3ph out on line UPS system IGBT based rectifier with input power factor correction 32 bit microprocessor based with isolation transformers double conversion, SNMP controls, LCD display, Pure sine wave output, with auto static switch three phase input / Three phase output and modular structure for better thermal technology / cooling facility, with warranty up to three years.Makes: APC / Numeric / Emerson / Fuji Electric At Gandhi Hospital | No | 305000
104 | Supply and fixing of 12V 65 AH SMF battery including wire leads. Makes: Quanta / Racket / Exide. At Gandhi Hospital | No | 20584
105 | Supply and providing of UPS cum battery rack for 20 batteries At Gandhi Hospital | No | 6764
106 | Providing and Fixing maintenance free earthing which consists of G.I. Earth station, with 600X600X3.15mm GI Plate at 2500mm Depth including construction of brick pedestal, providing meshed funnel, GI cover and other civil Engineering works, spreading a homogenous mixture of salt, charcoal around the pipe etc., completely as per IS 3043, 1987 or latest revision. Earthing testing should be done as per IE Rules like Earth valve test Etc. At Gandhi Hospital | No | 8500
107 | Providing and Fixing maintenance free earthing which consists of copper. Earth station, with 600X600X3.15mm Copper Plate at 2500mm Depth including construction of brick pedestal, providing meshed funnel, GI cover and other civil Engineering works, spreading a homogenous mixture of salt, charcoal around the pipe etc., completely as per IS 3043, 1987 or latest revision. Earthing testing should be done as per IE Rules like Earth valve test Etc. At Gandhi Hospital | No | 22283
108 | Supply and installation of 50x6 GI flat for body earthing of electrical panel and AC Panel which is laid in 300mm cable tray At Gandhi Hospital | Rmt | 329
109 | Supply and installation of 25x3 GI flat for body earthing of DBs and Cable tray which is laid in 100mm cable tray At Gandhi Hospital | Rmt | 163
110 | Supply and installation of 25x3 Copper flat for Neutral earthing of UPS and Equipment which is laid in 100mm cable tray At Gandhi Hospital | Rmt | 902
111 | Supply and installation of 4 sqmm Copper wire for Earthing of DBs Equipment At Gandhi Hospital | Rmt | 83
112 | Supply, Laying and testing of 3.5Cx95 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc. Make of cable:Polycab/KEI/Universal/Glostar/Finolex Make of gland and Lungs: HMI/Commet/Dowell’s At Gandhi Hospital | Rmt | 1207
113 | Supply, Laying and testing of 3.5CX50 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc.. Make of Cable: Polycab/KEI/Universal/Glostar/ Finolex Make of gland and Lungs: HMI/Commet/Dowell’s At Gandhi Hospital | Rmt | 722
114 | Supply, Laying and testing of 4Cx16 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc..Make of Cable: Polycab/KEI/Universal/Glostar/Finolex Make of gland and Lungs: HMI/Commet/Dowell’s At Gandhi Hospital | Rmt | 1483
115 | Supply, Laying and testing of 4Cx6 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc. Make of Cable: Polycab/KEI/Universal/Glostar/Finolex Make of gland and Lungs: HMI/Commet/Dowell’s At Gandhi Hospital | Rmt | 484
116 | Supply, Lying and testing of 4Cx4 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc. Make of Cable: Polycab/ KEI/Universal/ Glostar/Finolex. Make of gland and Lungs: HMI/Commet/Dowell’s at Gandhi Hospital | Rmt | 356
117 | SITC of IVF Center Main Panel Indoor IP-42 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with /without detachable extension type structure with all type of suitable switching accessories and bus-bar as per load requirement of respective IVF equipment’s. Which is including Lighting, power DBs and UPS at Gandhi Hospital | No | 355000
118 | SITC of IVF center AC Panel outdoor IP-54 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with / without detachable extension type structure with all type of suitable switching accessories and bus-bar as per load requirement of respective AC equipment’s. Which is including 1nos AHU’s stater with VFD by pass, Heater, ODU and VRF system At Gandhi Hospital | No | 270000
119 | Supply and installation of AHUs stater on/off push button station for Remote control for inside IVF center with control wiring from AC panel to on /off push button station with necessary items. at Gandhi Hospital | No | 1540
120 | Supply and Transportation 56W Clean room Light fixture, 2' x2' (600mm x600mm) LED luminaire CRCA powder coated white after phosphocreatine treatment provided as standard. with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% including all accessories and labour charges etc., complete. | Nos | 17241
121 | Supply and Transportation of 48" ( 1200 mm) High Speed Fan Sweep Celing Fan with all accessories etc., complete. Make Havells S S 390 | Nos | 4317
122 | Labour charges for fixing of ceiling fan and regulator including transportation and giving connections with twin core wire etc., complete. Makes : Finolex / RR Kabel / Havells / Polycab / GM / Million / V-Guard / Gold Medal / HPL / RPG. | Nos | 185
123 | Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete | Nos | 162
124 | Supply & fixing of 2nos6A, 2 in one socket - 2 Nos with 6A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benz Plus | Nos | 1178
125 | Supply,Transportation of 15" (375mm) ISI, 900 RPM Heavy duty exhaust fan with metallic blades wiremesh with all accessories etc complete Makes : Crompton / Almonard / Havells Turbo Force SP. | Nos | 4310
126 | Labour charges for fixing the exhaust fan in wall with necessary connections and masonary work of making hole, finishing etc., complete. Makes : Finolex / Havells / Polycab / Finecab | Nos | 788
127 | Supply and fixing of 12 Way SPN DB with IP 43 Protection as per IS:13032 with 1 No 63A FP MCB as Incommer, and 8 Nos of 6-32A SP MCB 10KA, C/D Curve ISI Mark as out goings, concealing in wall etc complete. DB Makes :Legrand MCB Makes : Legrand-DX3 | No | 9444
128 | Supply and fixing of cable adapteres box with cover for DBs including, massanory work etc., complete., | Nos | 5085
129 | Supply and Installation of control cum transmission wiring of size 4C x 2.5 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing and accessories as At Gandhi Hospital | Rmt | 289
130 | Supply and Installation of control cum transmission wiring of size 2C x 1.5 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing and accessories as At Gandhi Hospital Makes : Polycab | Rmt | 173
131 | 4C x 1.5 Sqmm Copper Flexible Cable For Condensing Unit to Electrical Panel Makes : Polycab | Rmt | 130
132 | Supply and fixing of FP Metal Enclosure with IP 20 Protection DB Make with 1 No 63A, 10 KA FP MCB including internal connection and labour charges for Flush Mounting etc.,complete. Makes of Enclousure : Legrand MCB Makes : Legrand-DX3 | Nos | 4203
133 | POINT WIRING and LIGHT FIXTURES & FITTINGS Providing Point wiring for Light Concealed Type with 2 x 1.0 Sq.mm. Copper. PVC Insulated wire 1.1 KV grade ISI marked in rigid ISI mark PVC conduit minimum 20mm (1.6 mm thick) dia. with necessary accessories and Pannel and Spot LED lights of Havells/Wipro company. | Nos | 1200
134 | Proving and fixing Profile lights at wpc Louvers | Rmt | 1182
135 | Proving and fixing Track lights at side wall décor frame with 4 fixtures and 2 tracks | Job | 9600
136 | External Profile light at Name Plate | Rmt | 1182
137 | Supply and fixing of suitable out door feeder piller box of size made with 14 SWG CRCA sheet with double door arrangement, making powder coating after processing of 7 Tank process, lock and key, hinges, rubber gasket, danger board,suitable angle iron stand for mounting the feeder pillar with cement concrete, including Supply and fixing of Legrand / Schnieder make as out goings, indication lamps, din channel, 6 Sqmm 3 core copper cable for invidual light control, connectors, bus bars, shroudings, gland plates and provision for 3 phase energy meter etc., complete for finished item of work and suitable wiring provision for connecting the nature switch with following.63A, 4 Pole MCB as incomer, 9 Nos 6-32A SP MCBs | Nos | 30768
DCA
138 | Supply, fixing of internal/external electrification including required Switches, Sockets, Conduits, Wiring, Run of mains, Distribution Boards, Earthing, Fixtures, Main Power Panel, Main Lighting Panel, UG cables, LT Cables terminations, APFCR panel for 100KVAR in Substation etc., complete as per list of requirements and as per Technical Specification. | Job | 5000000
139 | Supply erection testing and commissioning 30KVA UPS System including cost of Supply, transportation and fixing of 12V 100 AH SMF batteries 26 No including wire leads.complete as per the Technical Specifications. (As per BOQ) | JOB | 1378000
140 | Supply and Laying of ISI 25mm outer dia heavy grade with IS:9537 part 3 regid PVC pipe concealed in Roof Slabs with all required PVC / Metallic Deep Boxes including masonary work and labour charges etc., complete. Makes: Sudhakar / Finolex / Modi / VIP Precision / Universal / Million Plast / Polycab / DEC.(Ceased Material store) | Rm | 74
141 | Wiring with 2 runs of 22/0.3mm ( 1.5 Sq.mm) FRLS / [HFFR P.V.C. insulated flexible copper cable (ISI MARK) in existing pipe with 6A Modular switch, Ceiling rose/BH/SBH Modular switches with cover plate and GI switch box including all labour charges etc., complete. (for NonResidential Building) ¦Makes of wires : Finolex / RR kabel / Havells / APAR EBXL / KEI (HFFR) / Polycab ((HR_ FR-LF) /L&T / HPL RPG / Anchor / GM / Million / Gold Medal / Power Flex. Sudhakar. Makes of switches: Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / GM-Zenova / L&T- Englaze / Million mway / Goldmedal Curve / Anchor Roma viola / Havells Fabio / Panasonic Vision / Hager Insista /C&S Primo / Polycab Levana.(Ceased Material store) | Pts | 568
142 | Supply and fixing of 6A ISI Mark 3/2 pin Modular socket with 6A 1way Modular switch, 3 Module box with cover frame and GI switch box on common switch board with connections etc., complete. Makes of switches: Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / GM-Zenova / L&T - Englaze / Million mway / Goldmedal Curve / Anchor Roma viola / Havells Fabio / Panasonic Vision / Hager Insista /C&S Primo / Polycab Levana.(Ceased Material store) | Nos | 383
143 | Supply, transportation and fixing of 22W, 2300 lumens, 1200mm length LED light housing made with alluminium anodised body, wide operating voltage with PF20.9, Surge protection: > 2KV, THD<10%, with inbuilt driver and frosted cover CCT: 3000K - 6500K as desired by the department as per IS, minimum CRI280 etc., complete with 5 years warranty with BIS Certification with BIS Certification. Makes: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL.(Ceased Material store) | Nos | 931
144 | Supply, Transportation of 12" (300mm) ISI, 900 RPM Heavy duty exhaust fan with metallic blades wiremesh with all accessories etc complete Makes : Crompton Almounard / Havells Turbo Force SP.(Ceased Material store) | Nos | 3183
145 | Labour charges for fixing the Light duty exhaust fan in wall with connections with twin core wire and masonary work of making hole, finishing etc., complete.(Ceased Material store) | Nos | 616
146 | Supply and transportation of 48" (1200mm) 5 star rated Sweep Ceiling Fan with all accessories etc., complete. Makes : Crompton HS Plus / Havells ES NEO / Orient Energy Star (Seminar hall) | Nos | 2137
147 | Supply and fixing of 2 Module Modular type Electronic step type Fan Regulator for sweep AC ceiling fans of 1200mm / 1420mm complete with connections. Makes of switches: Legrand Myrius / Million /Goldmedal Curve/ Anchor Roma viola / Havells Fabio / Panasonic Vision / Hager Insista /C&S Primo / Polycab Levana.(Seminar hall) | Nos | 521
148 | Labour charges for fixing of ceiling fan and regulator including transportation and giving connections with twin core wire etc., complete.(Seminar hall) | Nos | 145
149 | Supply , installation , testing and commissioning of 1000cfm cabinet type toilets exhaust fan 15mm static pressure suitable for high efficency motor. SITC of factory fabricated GI sheet metal ducts, along with necessary supports 24G TDF duct SITC toilet Exhust disc valves of 200mm dia. including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site, complete for finished item of work. (Toilets) | Job | 115000
150 | Supply and Installation of 800 Amps 3 Pole MCCB, Adjustable, Confirms to IS/IEG 60947-2 having Breaking Capacity 35 KA with cable end boxes on suitable angle iron frame work including all Labours charges massonry work etc complete with connections. Makes : Legrand Schneider / Siemens / L&T / Cabtree Xpro. (Transformer Yard) | Job | 100496
151 | Earth work excavation of Trench in hard ground soil and Sand filling shall be provided at the bottom of trench before laying the cable and laying of U.G cables from 95 Sqmm up to 420 sqmm covering the cable with bricks and back filling of Trench duly providing Cable route Indicators of size 152mm round / 102mm x 102mm / 152mm x 152mm at every 8 Mtrs distance embedded in C.C including cost and conveyance of materials and labour charges etc., complete.(Transformer Yard) | Rm | 212
152 | Laying of PVC armoured under ground cable from 120 Sq.mm to 400 Sqmm fixing on chromium plated metallic base saddles on wall as per IS 1255 and as directed by the department including cost and conveyance of all materials and labour charges etc., complete.(Transformer Yard) | Rm | 43
153 | Supply of 300 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) Makes :Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / Paragon(Transformer Yard) | Rm | 1595
154 | Termination of UG cables of 3.5 core 300 Sq.mm including with required Heavy duty cable glands, Lugs complete with all required accessories as directed by the department including cost and conveyance of all materials and labour charges etc., complete. Makes: SMI / Commet / Dowels / DMI / Jainson. | Rm | 1345
155 | Supply of 240 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) Makes :Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / Paragon(Transformer Yard) | Rm | 1306
156 | Termination of UG cables of 3.5 core 240 Sq.mm including with required Heavy duty cable glands, Lugs complete with all required accessories as directed by the department including cost and conveyance of all materials and labour charges etc., complete.(Transformer Yard) | Rm | 1084
157 | Supply & fixing of 2' x 1' , 36W , Clean room LED Bottom Openable Light Fixture's including point wiring & electrical switches, including cost and conveyance of all materials etc., complete for finished item of work. (MB Lab) | No | 6900
158 | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor panel made out of Nos.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Aluminium bus bar ( with rating of 0.8A/ Sqmm) supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges. | No | 275800
800A Aluminium Bus Bar with colour code.(0.8A/Sqmm).
Internal wiring with approved make cable
Earthing Flat: Providing suitable G.I Flat
Incoming:
i. 630 A, 3P, MCCB, 50 KA - 1 Nos. Makes: schenieder.
Metering Set:
i. 0- 630A Digital Ammeter with selector switch . - 1 Nos.
ii. 0-500V Digital Volt meter with selector switch - 1 Nos.
iii. R, Y, B Indication lamps of LED type - 3 Nos.
iv. 630/5A C.T coils - 3 Nos
v. 6A MCB - 03 No's
vi. Multifunctional Meter - 01 set
Outgoing:-
i. 400A, 3P, MCCB, 36/35 KA - 2 Nos, with 02 no's of Multifunctional Meters, Makes: schenieder.
ii. 250 A 3P MCCB, 35/36 KA - 1 Nos, with 01 no of Multifunctional Meters, Makes: schenieder.
iii. 125 A 3P MCCB, 25 KA - 6 Nos, with 06 no's of Multifunctional Meters, Makes: schenieder. Makes: schenieder.
iv. 63 A 3P MCCB, 16 KA - 2 Nos, with 02 no's of Multifunctional Meters, Makes: schenieder. Makes: schenieder.
v. 63A,10KA FP MCB with SPD type-2 –1Nos
vi. 3 KW DOL Starter for Drain pump - 01 no
159 | Supply and Run of 50mm x 6mm G.I Strip including cost of all accessories and labour charges etc., complete. (2.36Kg / Mtr) | Rm | 210
198 | Supply erection testing and commissioning 30KVA UPS System including cost of Supply, transportation and fixing of 12V 100 AH SMF batteries 26 No including wire leads.complete as per the Technical Specifications. (As per BOQ) | JOB | 1378000
199
200
201
202
203
204
205
206
207
208
209
210
211
212
213
214
215
216
217
218
219
220
221
222
223
224
225
226
227
228
229
230
231
232
233
234
235
236
237
238
239
240
241
242
243
244
245
246
247
248
249
250
251
252
253
254
255
256
257
258
259
260
261
262
263
264
265
266
267
268
269
270
271
272
273
274
275
276
277
278
279
280
281
282
283
284
285
286
287
288
289
290
291
292
293
294
295
296
297
298
299
300
301
302
303
304
305
306
307
308
309
310
311
312
313
314
315
316
317
318
319
320
321
322
323
324
325
326
327
328
329
330
331
332
333
334
335
336
337

## Plumbing
S.No | Desription | UOM | Rate (Rs.)
|  |  | IVFs | SOTC
1 | Supplying and fixing 15 mm brass body CP finish bib tap of not less than 300 grams weight screw type full turn with internal/external threaded connection conforming to IS 8931 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, overheads and contractors profit complete for finished item of work in all floors. at Gandhi Hospital | No | 881 | 540
2 | Supply and fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings SDR 13.5 to meet the requirement of ASTM-D 2846 and are produced in CTS Copper Tube Sizes 1/2inches to 2inches for hot and cold water IS 15778:2007 including cost and conveyance of all materials to site, labour charges for fixing, complete for finished item of work at all floor levels. 15.90mm OD pipe at Gandhi Hospital | Rmt | 199 | 270
3 | Supply and fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings SDR 13.5 to meet the requirement of ASTM-D 2846 and are produced in CTS Copper Tube Sizes 1/2inches to 2inches for hot and cold water IS 15778:2007 including cost and conveyance of all materials to site, labour charges for fixing,complete for finished item of work at all floor levels. 22.20mm OD pipe at Gandhi Hospital | Rmt | 229 | 360
4 | Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings -28.60mm OD pipe | Rmt |  | 450
5 | Supplying and fixing of SWR PVC pipes Prince/Sudhakar/ Kisan /Supreme or any ISI brand 4 Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, complete for finished item of work at all floor levels. APSS No. 1302 1319 and 1326 - 75mm dia at Gandhi Hospital | Rmt | 327 | 450
6 | Supplying and fixing of SWR PVC pipes Prince/Sudhakar/Kisan /Supreme or any ISI brand 4 Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, complete for finished item of work at all floor levels. APSS No. 1302 1319 and 1326- 110mm dia at Gandhi Hospital | Rmt | 444 | 540
7 | Supplying and fixing Bronze Gate/ Globe valve as per IS - 778 Class - I, Indian make heavy type including cost and conveyance of all materials , labour charges , overheads and contractors profit complete for finished item of work. 25mm Nominal bore at Gandhi Hospital | No | 1750 | 1440
8 | Supplying and fixing of 4inches 101.6mm multi floor trap with jali - UPVC/SWR pipe fittings as per site requirements with standard practice for all floors including cost and conveyance of all materials to site, labour charges ,etc., complete for finished item of work. at Gandhi Hospital | No | 220 | 270
9 | Supplying and fixing Indian make Flat Back Wash Hand Basin 1st quality conforming to IS:2556-Part-4:1972 of size 550mm x 400mm with 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963- 1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make heavy duty complete with standard CI brackets including wooden blocks ,1 No.12.70mm PVC connection with brass union nuts CP coated , angle stop cock 12.70mm dia. first quality Indian make heavy duty, 30mm dia. PVC flexible waste pipe 914.4mm length of 1st quality including cost and conveyance of all materials to site, labour charges, for finished item of work at Gandhi Hospital | No | 3800 | 3600
10 | Supply, Installation and commissioning approved make floor mounted Anglo Indian wash down EWC conforming to IS:2556 Part 8-2004 suit with P or S trap with dual flush porcelain cistern fixed on wash down EWC with all internal parts of dual flush cistern, ultra solid seat cover of approved make with rubber buffer and cap and 15 mm angle stop cock and 450 mm long PVC inter connection pipe wall flanges all of approved make etc. complete for finished item of work in all respects: TBSP-E.II-03 at Gandhi Hospital | No | 7590 | 6300
11 | Supplying and fixing Chromium plated finish brass body quarter turn Bibcock cum Health Faucet with 1m long tube and wall hook with necessary fittings etc., complete including cost and conveyance of all materials, labour charges, complete for finished item of work in all floors. at Gandhi Hospital | No | 4580 | 3600
12 | Supplying and fixing CP finish brass soap dish of approved make ISI quality including cost and conveyance of all materials, labour charges for fixing, for finished item of work in all floors at Gandhi Hospital | No | 872 | 1100
13 | Supplying and fixing TV shape mirror with plastic frame of size 609.6mm x 457.2mm, plywood back with NP screws 1st quality including cost and conveyance of all materials, labour charges, for finished item of work in all floors. at Gandhi Hospital | No | 727 | 630
14 | Supplying and fixing of CP finish brass wall mounted towel ring at Gandhi Hospital | No | 872 | 540
15 | Supplying and fixing 15 mm brass body CP finish self closing tap push type conforming to IS 1711 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, complete for finished item of work in all floors. at Gandhi Hospital | No | 418 | 720
16 | Supplying and fixing of 3" (75mm) Nahany trap with jali - UPVC/SWR pipe fittings as per site requirements with standard practice for all floors including cost and conveyance of all materials to site, labour charges , overheads & contractors profit etc., complete for finished item of work. | Nos | 133
17 | Supplying and fixing 50 mm Nominal Bore GI pipe Medium Grade properties & weight as per IS 1239 in ground or on wall with GI fittings such as elbows tees couplings, nipples, plugs including excavation for trenches and refilling the trenches ,chiselling masonry walls and making good the walls & floors to the original surface and fixing MS clamps on TW blocks on walls including cost and conveyance of all materials and labour charges , overheads & contractors profit complete for finished item of work except for GI bends union and GI connectors with checkout and socket Tata or Zenith make or equivalent. (For Autoclave) | Rmt | 599
18 | 580mm x 440mm long Orissa pan white glazed Water Closet | Nos |  | 5400
19 | Supplying and fixing15 mm nominal size 152.0 mm CP finish iron body shower rose 1st quality including cost and conveyance of all materials, labour charges , overheads & contractors profit for finished item of work in all floors. | Nos |  | 630
20 | Supply and Fixing of white glazed flat back bowl urinals | Nos |  | 2700
21 | Supplying and fixing of SWR PVC pipes (Prince/Sudhakar/Kisan/Supreme or any ISI brand) 4 Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, overheads & contractors profit complete for finished item of work at all floor levels. (APSS No. 1302 1319 & 1326) (All floors) | Rmt |  |  | 208 | DCA

## Air Conditioning
S.No | Description | UOM | Rate
SOTC
1 | Uni Directional Ceiling Laminar Airflow Systems | Nos | 465000
2 | Air Handling Units (AHUs) 11 TR | Nos | 1495000
3 | Condensing Units | Nos | 345000
4 | Uni Directional Ceiling Laminar Airflow Systems | Nos | 395000
5 | Air Handling Units (AHUs) 11 TR | Nos | 1495000
6 | Air Handling Units (AHUs) 8.5 TR | Nos | 1195000
7 | Condensing Units | Nos | 345000
8 | 1.50 TR with , 18000 BTU/Hr High Wall mount Split Air Conditioners | Nos | 150000
9 | 2.0 TR with , 24000 BTU/Hr High Wall mount Split Air Conditioners | Nos | 210000
10 | Voltage stabilizer for 4 KVA maximum load | Nos | 7000
11 | Voltage stabilizer for 5 KVA maximum load | Nos | 8500
12 | Ductable Air Conditioners 11.0 TR with ISEER ≥ 4 | Nos | 1200000
13 | Ductable Air Conditioners 8.5 TR with ISEER ≥ 4 | Nos | 1000000
14 | Ductable Air Conditioners 5.5 TR with ISEER ≥ 4 | Nos | 900000
IVFs
15 | Supply, transportation and installation of split AC unit 1.5 TR inverter type 3 Star capable of delivering 18000 BTU/hr and above with high wall mounted indoor unit and outdoor condensing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord , built-in stabilizer Voltage range 160- 264 volts and cordless remote control. Makes : Daikin / Thoshiba / O General at Gandhi Hospital | No | 48000
16 | Supply, transportation and installation of split AC unit 1.0 TR inverter type minimum 3 Star capable of delivering 12000 BTU/hr and above with high wall mounted indoor unit and outdoor condensing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord , built-in stabilizer Voltage range 160- 264 volts and cordless remote control. Makes: Daikin / Thoshiba/ O General at Gandhi Hospital | No | 40000
17 | Modular Double skin floor mounted EUROVENT Certified Air Handling Unit 3000CFM / 8.5 TR / 150mm SP made out of 45 plus or minus 2mm thick PUF insulated panels Thermal break aluminium profile frame work with 0.8mm thick pre painted / powder coated inner and outer skins comprising of mixing box with fresh air and return air dampers, pre filters with 10 and 5 microns combination filters in single frame, Interlaced/Intertwined DX Cooling Coil suitable for connecting 2 nos of 8.5TR capacity 1W plus 1S out door condensing units, SS304 drain pan with, blower section with Nicotra / Kruger make direct drive/ Plug type fan, vibration isolators, EFF1 motor and blower section with on/off switches to operate from outside, limit switch for the fan section access door with a view port, fine filter section with 3 microns filters inspection doors for all filter and fan sections and damper at the outlet of unit. Ports for differential pressure gauges across all filters and blower to measure differential pressure. AHU Make : VTS / Systemair, Make - Blower - Nicotra / Kruger ; Motor -crompton Greaves / Siemens ; Filter - Thermodyne / Freudenberg / Ultrafil at Gandhi Hospital | No | 590000
18 | SITC of filter module made out of heavy duty Aluminium powder coated extrusion with minimum of 13G . and to house 610 mm X 610 mm HEPA Filter at the rate 0.3 microns , 99.9997, H-14 Grade, Filter loading from clean room side with bewel gear arrangement damper with access from clean room suitable to house the following filter sizes pressure drop and Integrity testing ports into room. Includes SS capsule perforated diffuser. This includes all required supports and accessories etc. Capacity 1000 CFM. at Gandhi Hospital | No | 42000
19 | SITC of air cooled condensing units with two scroll compressors, air cooled condenser, power panel, vibration isolating pads, stand for ODU, thermostat, etc. of the following capacities. The nominal capacity of the condensing unit shall be as under. Air cooled condensing unit shall have horizontal discharge. All refrigerant piping accessories sight glass, drier, expansion valve, etc. shall be supplied with the condensing units and suitable to connect above AHUs. Refrigerant shall be R 407C / R 410A. Necessary thermostat, control wiring, etc. shall be included. Derating of the unit shall not be more than 15percentage under 45 deg. C ambient temperature. Condensing unit shall be capable of operating up 50 deg. C ambient temperature. 8.5 TR capacity At Gandhi Hospital | No | 182000
20 | SITC of Flange type, Flame proof FLP duct heaters of 5 kW capacity with Mineral Filled AISI SS304/SS321 Sheathed Tubular Heater with GI Helical fins, Tube dia 8.2mm min and Helical Finn dia 25mm min, enclosed in the frame, FLP Terminal box etc., Nickel Chromium Inner Element, Silicon Sealing to Restrict Moisture pickup, Silver brazed mounting plate etc., and heaters shall be controlled with PID thyrestor controller based on the analog output signal of 0-10 V DC of controller . And this should have saftey thermostat and cutouts and air stat etc. all safety controls. The capacities as follows and sizes of the heaters shall be as per the duct sizes and approved drawing. at Gandhi Hospital | No | 205000
21 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Liquid Line at Gandhi Hospital | Rmt | 1020
22 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Suction Line at Gandhi Hospital | Rmt | 1190
23 | SITC of CPVC drain piping with supports, clamps and 9 mm thk. Nitrile rubber tube insulation of the following sizes. Insulation shall have factory laminated glass cloth. 32mm Dia at Gandhi Hospital | Rmt | 670
24 | SITC of CPVC drain piping with supports, clamps and 9 mm thk. Nitrile rubber tube insulation of the following sizes. Insulation shall have factory laminated glass cloth. 25mm Dia at Gandhi Hospital | Rmt | 515
25 | SITC of Factory fabricated and boxed ducting using Aluminium Sheets / coils, should be fabricated as per SMACNA, galvanised hardware and supports, silicon sealant at all longitudinal joints, Galvanized /GI Electroplated iron angle flanges for all the joints, bracing angles and minimum 5mm thick neoprene rubber gasket.- Duct pressure testing at 75mm to be carried out before insulatiting the duct. pressure testing to be done as per SMACNA. Procedure to be approved by consultant. 20G - 1.0 mm Thick at Gandhi Hospital | Sqm | 2600
26 | SITC of Factory fabricated and boxed ducting using Aluminium Sheets / coils, should be fabricated as per SMACNA, galvanised hardware and supports, silicon sealant at all longitudinal joints, Galvanized /GI Electroplated iron angle flanges for all the joints, bracing angles and minimum 5mm thick neoprene rubber gasket.- Duct pressure testing at 75mm to be carried out before insulatiting the duct. pressure testing to be done as per SMACNA. Procedure to be approved by consultant. 22G - 0.8 mm Thick at Gandhi Hospital | Sqm | 2325
27 | Aluminium low leakage aerofoil design volume control dampers Suitable for manual and motorised operation At Gandhi Hospital | Sqm | 15800
28 | CBRI approved 16G GI Spring return actuated fire dampers rated for 90 minutes with limit switch. At Gandhi Hospital | Sqm | 25900
29 | SITC of SS perforated return raiser grilles with 10 microns filters with collar dampers At Gandhi Hospital | Sqm | 26300
30 | Extruded Al. powder coated EXHAUST / RETURN discrete grilles At Gandhi Hospital | Sqm | 8125
31 | SITC of Collar Dampers made of Al. extrusions with black powder coating for Grilles / Diffusers At Gandhi Hospital | Sqm | 7550
32 | SITC of Magnehelic gauges across pre and fine filter at AHUs including mounting arrangement, SS nozzles, food grade PVC tubing, etc. At Gandhi Hospital | No | 10500
33 | SITC of Magnehelic gauges to measure the room differential pressures in operation theatres with SS mounting box, SS nozzles, food grade PVC tubing, etc. At Gandhi Hospital | No | 12900
34 | SITC of Aluminium powder coated Fresh air and Exhaust Louvers of non- vision type with nylon mosquito net etc. At Gandhi Hospital | Sqm | 10300
35 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 32mm Thick for Exposed Supply Air duct and finished with UV Protective Paint. at Gandhi Hospital | Sqm | 1225
36 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Exposed Return Air Duct and finished with UV Protective Paint. at Gandhi Hospital | Sqm | 1075
37 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Supply air duct running inside the building. at Gandhi Hospital | Sqm | 785
38 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 19mm Thick for Return air running inside the building. at Gandhi Hospital | Sqm | 660
39 | Condensing units - VRF/VRV System : Supply, Installation, Nitrogen testing, Vacuuming and Commissioning of air cooled variable refrigerant flow modular type condensing units, each comprising of multiple scroll compressors all inverter driven, full charge of refrigerant gas R-410a including additional gas filling , lubricating oil and all accessories as per the specifications. The condensing units shall be suitable to work on cooling mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B . The COP of the system shall be greater than 4 under ARI conditions for 100percentage load . The condensing units shall be suitable for operation on 415 plus or minus 10percentage volts, 50Hz, 3 phase AC power supply and , outdoor units to be mounted on MS platform with suitable Vibration Isolation pads to avoid vibrations. All the supports and angle base frame structure to be duly black painted with synthetic epoxy paint. the condensing units shall be of following capacities: The VRF ODU should be capable of working with total capacity of connected indoor units ranging between 100percentage to 140percentage of ODU capacity . COP minimum 3.5. Make : Daikin / LG /O General / Toshiba. 16 HP At Gandhi Hospital | Set | 325000
40 | VRF Indoor Units : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 0.8 TR At Gandhi Hospital | No | 30700
41 | VRF Indoor Units : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.0 TR At Gandhi Hospital | No | 30700
42 | VRF Indoor Units : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.5 TR At Gandhi Hospital | No | 35000
43 | Cassette Units : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling mode.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 3.0 TR – 4 way At Gandhi Hospital | No | 50000
44 | Supply, Installation, Testing and Commissioning of Hard copper REFRIGERANT PIPING of 16swg various sizes with necessary supports, fittings, interconnecting the liquid and suction lines between the aircooled outdoor units and the indoor units. The piping shall be carried out of Hard drawn copper pipes of type K with soldered / brazed socket fittings. Isolating valves shall be provided to isolate each compressor, strainers, sight glass and any other component requiring proper operation and maintenance. Both the suction and liquid lines shall be insulated with 19mm thick closed cell insulation for above 25mm dia , 13mm thick for pipes below 25mm dia . The insulation finished with treated woven glass fiber reinforced covering for inside Piping and including making required holes in the wall and re finishing and water tight of holes after laying holes as per the specifications and approved drawings. At Gandhi Hospital | Lot | 400000
45 | Supply, Installation , Testing and Commissioning of Refnet joints to be provided in refrigerant pipe line. Material of construction for fittings shall be similar to refrigerant piping. At Gandhi Hospital | Set | 6191
46 | Supply and Installation of control cum transmission wiring of size 3C x 1.5 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing and accessories as At Gandhi Hospital | Rmt | 320
47 | Supply and Installation of cabling of size 2C x 1 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing and accessories as per the approved routing. At Gandhi Hospital | Rmt | 255
48 | Supply and installation of 2.2 TR 3 Star capable of delivering 21600 BTU/hr and above with operating on refrigerant R-32 / R-410 with condeser stand, layoing copper pipe of 15mm size of length 15 mt including Nitrile rubber insulation connected with 2.5 sqm x 4 core cable for power supply and equipped with drain pump. Makes : Daikin / Toshibha / Carrier / BlueStar / Hitachi or equivalent | Nos | 72225
49 | SITC of CPVC drain piping with supports, clamps of the following size. 25mm Dia at Gandhi Hospital | Rmt | 200
50 | Supply & Installation of MS Angle for Duct Support, Cable Tray Support and Condensing Unit Stand of size 40 X 40 x 5 mm Thick. | Kg | 190
51 | Supply & Installation of MS Angle for Duct Support, Cable Tray Support and Condensing Unit Stand of size 25 X 25 x 5 mm Thick. | Kg | 190
52 | Supply and installation of Canvas Connections For AHUS | Nos | 6500
53 | Condensing units - VRF/VRV System : Supply, Installation, Nitrogen testing , Vacuuming and Commissioning of air cooled variable refrigerant flow modular type condensing units, each comprising of multiple scroll compressors all inverter driven, full charge of refrigerant gas R-410a including additional gas filling , lubricating oil and all accessories as per the specifications. The condensing units shall be suitable to work on cooling mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B . The COP of the system shall be greater than 4 under ARI conditions for 100percentage load . The condensing units shall be suitable for operation on 415 plus or minus 10percentage volts, 50Hz, 3 phase AC power supply and , outdoor units to be mounted on MS platform with suitable Vibration Isolation pads to avoid vibrations. All the supports and angle base frame structure to be duly black painted with synthetic epoxy paint. the condensing units shall be of following capacities: The VRF ODU should be capable of working with total capacity of connected indoor units ranging between 100percentage to 140percentage of ODU capacity . COP minimum 3.5. Make : Daikin / LG / O General / Toshiba at MGMH Petlaburj 22 HP | Nos | 402500
54 | Cassette Units : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling mode.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 2.0 TR – 4 way at MGMH Petlaburj | Nos | 40000
55 | Modular Double skin floor mounted EUROVENT Certified Air Handling Unit 4400CFM / 11.0 TR / 150mm SP made out of 45 plus or minus 2mm thick PUF insulated panels Thermal break aluminium profile frame work with 0.8mm thick pre painted / powder coated inner and outer skins comprising of mixing box with fresh air and return air dampers, pre filters with 10 and 5 microns combination filters in single frame, Interlaced/Intertwined DX Cooling Coil suitable for connecting 2 nos of 11.0TR capacity 1W plus 1S out door condensing units, SS304 drain pan with , blower section with Nicotra / Kruger make direct drive/ Plug type fan, vibration isolators, EFF1 motor and blower section with on/off switches to operate from outside, limit switch for the fan section access door with a view port, fine filter section with 3 microns filters inspection doors for all filter and fan sections and damper at the outlet of unit. Ports for differential pressure gauges across all filters and blower to measure differential pressure. AHU Make : VTS / Systemair, Make - Blower - Nicotra / Kruger ; Motor - Crompton Greaves / Siemens ; Filter - Thermodyne / Freudenberg / Ultrafil at MGMH Petlaburj | Nos | 718500
56 | SITC of air cooled condensing units with two scroll compressors, air cooled condenser, power panel, vibration isolating pads, stand for ODU, thermostat, etc. of the following capacities. The nominal capacity of the condensing unit shall be as under. Air cooled condensing unit shall have horizontal discharge. All refrigerant piping accessories sight glass, drier, expansion valve, etc. shall be supplied with the condensing units and suitable to connect above AHUs. Refrigerant shall be R 407C / R 410A. Necessary thermostat, control wiring, etc. shall be included. Derating of the unit shall not be more than 15percentage under 45 deg. C ambient temperature. Condensing unit shall be capable of operating up 50 deg. C ambient temperature. 11.0 TR capacity at MGMH Petlaburj | Nos | 240750
57 | Supply and installation of AHUs stater on/off push button station for Remote control for inside IVF center with control wiring from AC panel to on /off push button station with necessary items. at Gandhi Hospital | No | 1540
DCA
58 | 1.5 TR Split AC | Nos | 137720
59 | 2 TR Split AC | Nos | 167760
60 | 5.5 TR DSU | Nos | 196000
61 | 8/8.5 TR DSU | Nos | 322000
62 | Supply Installation Commissioning and Validation of Heat Ventilation and Airconditioning HVAC System as detailed in the Technical Specifications | JOB | 12386544

## ELV
S.No | Desription | UOM | Rate (Rs.)
IVFs
1 | Supply, installation, testing and commissioning of 20nos LAN points with cat 6 cable and with suitable network rack and 5nos of telephone points with krone box to existing EPABEX. at Gandhi Hospital | Job | 383000
2 | Supply, installation, testing and commissioning of 1 no of Access control system with egress switch, Power Cable, communication cable to control panel with necessary required items Etc. at Gandhi Hospital | Job | 124000
3 | Supply, installation, testing and commissioning of 5nos IP Based CCTV cameras and Cat 6 Cable with NVR system. at Gandhi Hospital | Job | 182000
4 | Supply, installation, testing and commissioning of Audio and video recording of counseling rooms at Gandhi Hospital | Job | 138000
SOTC
5 | Telephone & EPABX System | Job | 1000000
6 | Local Area Network (LAN) System | Job | 1250000
7 | Biometric Access Control System | Nos | 300000
8 | CCTV CEILING CAMERA | Nos | 9500
9 | Recording in counselling room | Job | 155378
10 | Local Area Network (LAN) System | Job | 460242
DCA
11 | Differncial Pressure Gauge : Supply / Installation / Testing / Commissioning of Magnehelic gauges with suitable Box & Tubing Suitable to install in modular panel and AHU with nozzle & complete accesssories ( Range : 0 -10mm WC for inside clean room - Analog Type ) (MB Lab area) | Lot | 220500
12 | Double skin floor mounted exhaust unit of 1000cfm for Type-II - B(II) Bio Safety Cabinet 75mm static pressure suitable for high efficency motor. SITC of factory fabricated GI sheet metal ducts, along with necessary supports 24G TDF duct including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site, complete for finished item of work. (MB Lab) | Nos | 255000
13 | Supply , installation , testing and commissioning of 2 Door Interlocking System to restrict entry with Emergency push Button, including cost and conveyance of all materials etc., complete for finished item of work. (MB Lab) | Job | 51800
14 | Supply , installation , testing and commissioning of 7 Door Interlocking System to restrict entry with Emergency push Button, including cost and conveyance of all materials etc., complete for finished item of work. (MB Lab) | Job | 96500
15 | Supplying of Access Control System Cards with Reading Software to enable restricted access in the DCA Laboratory, including cost and conveyance of all materials etc., complete for finished item of work. | Nos | 230
16 | Supply erection testing and commissioning of Telephone lines including wires, jacks, distribution boxes with backmount frame, connector, powder coated metal body with lock and key arrangement, etc as per the Technical Specifications. | JOB | 150000
17 | Supply erection testing and commissioning of LAN System including Cat 6 RJ 45 outlets, Cat 6 UTP cable, network racks with power spike and accessories, 24 port and 48 port manageble switches etc as per the Technical Specifications. | JOB | 280000
18 | Supply installation testing and commissioning of IP based Digital Telephone EPABX System etc as per the Technical Specifications. | Job | 337000
19 | Supply erection testing and commissioning of Access Control System as per the Technical Specifications. | Nos | 150000

## FF
S.No | Desription | UOM | Rate (Rs.)
IVFs
1 | Supply, installation, testing and commissioning of Automatic Fire Alarm System which is including 30 nos of smoke Detectors 1nos manual call point, 1 no of Hooter with fire alarm cable connected to the existing fire control panel with necessary Required items etc.. at Gandhi Hospital | Job | 510000
2 | Supply and installation of Fire Extinguishers of CO2 4.50 Kg at Gandhi Hospital | No | 11225
3 | Supply and installation of ceiling mounted Fire Extinguishers of ABC MAP 90, 5.0 Kg stored pressure type at Gandhi Hospital | No | 7686
4 | Supply and installation of 2.0 Kg clean agent HCFC 123 Fire Extinguishers at Gandhi Hospital | No | 15065
5 | Supply and fixing of Fire escape signage Boards at Gandhi Hospital | Job | 56000
6 | Supply, Installation, testing and commissioning of EN54-2 Listed and LPCB approved based analog addressable fire control panel expandable by minimum 2 additional loops with minimum 80 character LCD display 4 access levels 1000 events, historical logging, flash E-PROM, 240 volts A C Power supply, automatic battery charger, 24V SLA batteries suitable for operating the entire system including tack back units and the hooters / strobes for a minimum of 4 hours in battery condition the panel shall have suitable power amplifiers for hooter / strobes the panel shall be capable beeing integrated with the BMS system and shall include cost of supply, installation of any additional modules or interfaces required for the same. The panel shall be completed as per the specification and as required for fixing of above Micro processor based Fire Alarm control panel with zonal indictions and battery back up as per detailed specifications. Makes: Ravel | Nos | 291366
SOTC
7 | Automatic Smoke Detection System | Job | 1425000
8 | Automatic Fire Alarm System | Job | 1400000
9 | Supply & Fixing of 4.5Kg, CO2 Type Fire Extinguisher. | Nos | 27000
10 | Supply and fixing of ABC stored pressure squeeze grip type fire extinguishers, 9 kg capacity. | Nos | 16000
11 | Supply and fixing of ABC Powder MAP 4 Kg Fire extinguisher | Nos | 11000
12 | Supply and fixing of 2 Kg Fire extinguisher Clean Agent | Nos | 22500
13 | Supply and fixing of Escape signage boards in Rigid Photo luminescent based glow | Nos | 2000
DCA
14 | Supply erection testing and commissioning Fire Detection and Alarm System including all accessories complete as per the Technical Specifications. | JOB | 959201
15 | Supply and Fixing of ABC Powder MAP 4 Kg Fire extinguisher complete as per the Technical Specifications. | Nos | 5670
16 | Supply and Fixing of ABC Powder MAP 2 Kg Fire extinguisher complete as per the Technical Specifications. | Nos | 4570

## MGPS
S.No | Desription | UOM | Rate (Rs.)
IVFs
1 | SITC of Oxygen Manifold Emergency for 1 plus 1 Cylinders, as per technical specifications. At Gandhi Hospital | Set | 20750
2 | SITC of Oxygen Outlets with matching probes, as per HTM-2022/02-01 of UK/NFPA99C of USA as per enclosed technical specifications - Imported At Gandhi Hospital | each | 2506
3 | SITC of Oxygen Flow meter with Humidifier, CE Certified with four digit number as per enclosed technical specifications - Imported At Gandhi Hospital | each | 1805
4 | SITC of Nitrous Oxide Manifold Emergency for 1 Cylinder, with high pressure Regulator, NRV, tailpipes etc. as per technical specifications At Gandhi Hospital | Set | 13250
5 | SITC of N20 Outlets with matching probes, as per HTM-2022/02-01 of UK/NFPA99C of USA as per enclosed technical specifications - Imported At Gandhi Hospital | each | 2506
6 | SITC of C02 Manifold for 2 Cylinders, with high pressure Regulator, NRV, tailpipes etc. as per technical specifications At Gandhi Hospital | Set | 20750
7 | SITC of C02 Outlets with matching probes, as per HTM-2022102- 01ofUK/NFPA99C of USA as per enclosed technical specifications - Imported At Gandhi Hospital | each | 2506
8 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 12mm COPPER PIPE at Gandhi Hospital | Rmt | 642
9 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 15mm COPPER PIPE at Gandhi Hospital | Rmt | 824
10 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 22mm COPPER PIPE at Gandhi Hospital | Rmt | 1191
11 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 28mm COPPER PIPE at Gandhi Hospital | Rmt | 1473
12 | SITC of Touch type LCD Area Alarm and Zonal Valve box- as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications imported for 3 gases at Gandhi Hospital | each | 275000
13 | SITC of Touch type LCD Area Alarm and Zonal Valve box- as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications imported for Master Main Alarm including all Gases at Gandhi Hospital | each | 375000
14 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 15mm 0D at Gandhi Hospital | each | 1938
15 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 22mm 0D at Gandhi Hospital | each | 2740
16 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 28mm 0D at Gandhi Hospital | each | 4378
17 | SITC of Bed Head Panel - as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications at Gandhi Hospital | each | 36750
18 | Fully Automatic Control Panel for Oxygen System: Supply, installation and commissioning of Fully Automatic control panel for unintrupted Oxygen supply | Set | 175180
19 | Trigas Emergency Manifold: SITC of Emergency Trigas Manifold maximum for 1+1 D-type Gas Cylinders complete with separate NRVs, tail pipes and brass fittings for each cylinders. | Set | 9620
20 | Fully Automatic Control Panel for Trigas System: Supply, installation and commissioning of Fully Automatic control panel for unintrupted Nirous Oxide supply. | Set | 175180
21 | Fully Automatic Control Panel for CO2 System: Supply, installation and commissioning of Fully Automatic control panel for unintrupted Nirous Oxide supply. | Set | 175180
22 | SITC of Medical Air-4 Outlet with matching probe as per HTM-2022/02-01 of UK/ NFPA 99C of USA as per enclosed technical Specification. | Nos | 12470
23 | 12 mm Valve for 12 mm OD Pipe Note: New item added | Nos. | 930
24 | Supply and installation of 46.7 liter size CO2 cylinders confirming to IS:7285 Part-2 (2017). The cylinder shall have an outer diameter of 232mm, a nominal length of 1365mm, and a minimum wall thickness of 5.3mm, ensuring robustness and safety during handling and storage. The cylinders shall have a capacity of 46.7 liters and comply with the standards set forth by the Indian Standards Institute. They shall be constructed from high-quality 37 Mn (Carbon Manganese) material, guaranteeing durability and reliability. The design shall feature a concave bottom and neck threading conforming to IS 3224:2002 14 TPI Type 4 - Size 2 specifications, facilitating secure connections and ease of use. The cylinder shall be capable of withstanding a test pressure of 250 BAR and have a working pressure of 150 BAR. The nominal tare weight of each cylinder shall be 51 kg. The cylinder includes first fill. | Nos | 20850
25 | Supply and installation of 46.7 liter size O2 cylinders confirming to IS:7285 Part-2 (2017). The cylinder shall have an outer diameter of 232mm, a nominal length of 1365mm, and a minimum wall thickness of 5.3mm, ensuring robustness and safety during handling and storage. The cylinders shall have a capacity of 46.7 liters and comply with the standards set forth by the Indian Standards Institute. They shall be constructed from high-quality 37 Mn (Carbon Manganese) material, guaranteeing durability and reliability. The design shall feature a concave bottom and neck threading conforming to IS 3224:2002 14 TPI Type 4 - Size 2 specifications, facilitating secure connections and ease of use. The cylinder shall be capable of withstanding a test pressure of 250 BAR and have a working pressure of 150 BAR. The nominal tare weight of each cylinder shall be 51 kg. The cylinder includes first fill. | Nos | 17850
26 | Supply and installation of 46.7 liter size Trigas cylinders confirming to IS:7285 Part-2 (2017). The cylinder shall have an outer diameter of 232mm, a nominal length of 1365mm, and a minimum wall thickness of 5.3mm, ensuring robustness and safety during handling and storage. The cylinders shall have a capacity of 46.7 liters and comply with the standards set forth by the Indian Standards Institute. They shall be constructed from high-quality 37 Mn (Carbon Manganese) material, guaranteeing durability and reliability. The design shall feature a concave bottom and neck threading conforming to IS 3224:2002 14 TPI Type 4 - Size 2 specifications, facilitating secure connections and ease of use. The cylinder shall be capable of withstanding a test pressure of 250 BAR and have a working pressure of 150 BAR. The nominal tare weight of each cylinder shall be 51 kg. The cylinder includes first fill. | Nos | 29250
27 | Supply and installation of 46.7 liter size N2O cylinders confirming to IS:7285 Part-2 (2017). The cylinder shall have an outer diameter of 232mm, a nominal length of 1365mm, and a minimum wall thickness of 5.3mm, ensuring robustness and safety during handling and storage. The cylinders shall have a capacity of 46.7 liters and comply with the standards set forth by the Indian Standards Institute. They shall be constructed from high-quality 37 Mn (Carbon Manganese) material, guaranteeing durability and reliability. The design shall feature a concave bottom and neck threading conforming to IS 3224:2002 14 TPI Type 4 - Size 2 specifications, facilitating secure connections and ease of use. The cylinder shall be capable of withstanding a test pressure of 250 BAR and have a working pressure of 150 BAR. The nominal tare weight of each cylinder shall be 51 kg. The cylinder includes first fill. | Nos | 33000
SOTC
28 | 28 mm dia. and 0.90 mm thick Copper Pipe Lines for Main lines | Rmt | 1750
29 | 42 mm dia. and 1.20 mm thick Copper Pipe Lines for Main lines | Rmt | 2250
30 | 54 mm dia. and 1.20 mm thick Copper Pipe Lines for Main lines | Rmt | 2950
31 | 12 mm dia. and 0.70 mm thick Copper Pipe Lines for distribution lines | Rmt | 650
32 | 15 mm dia. and 0.90 mm thick Copper Pipe Lines for distribution lines | Rmt | 950
33 | 22 mm dia. and 0.90 mm thick Copper Pipe Lines for distribution lines | Rmt | 1450
34 | 15 mm (1/2") Isolation Valves | Nos | 1500
35 | 22 mm (3/4") Isolation Valves | Nos | 2500
36 | 28 mm Isolation Valves | Nos | 3500
37 | 42 mm Isolation Valves | Nos | 4500
38 | 54 mm Isolation Valves | Nos | 5500
39 | Gas Outlet Points with probes for Oxygen with S Brackets | Nos | 2850
40 | 2 Gas Digital Area Alarm Panels | Nos | 25000
41 | 3 Gas Digital Area Alarm Panels | Nos | 30000
42 | 5 Gas Digital Area Alarm Panels | Nos | 40000
43 | Master Digital Alarm Panels | Nos | 50000
44 | BPC Flow meter with Humidifier bottle and L adapter | Nos | 2250
45 | L Type Adapter for Oxygen Flow meters | Nos | 1250
46 | Kit for conversion of Oxygen | Nos | 1650
47 | Suction Jars of 600 ml capacity | Nos | 3450
48 | Adapters for Vacuum | Nos | 750
49 | Adapters for Air | Nos | 750
50 | Adapters for Nitrous Oxide | Nos | 750
51 | Vacuum Tube | Nos | 550
52 | Bed Head wall panel horizontal 1500 mm long single railing | Nos | 35000
53 | Valve box -2 services | Nos | 9500
54 | Valve box -3 services | Nos | 14500
55 | Valve box -6 services | Nos | 22500
56 | 4 + 4 size of CO2 manifold System | Job | 40000
57 | 2 cylinder emergency manifold CO2 | Job | 14500
58 | Fully Automatic CO2 Control System | Job | 185000
59 | Aneste Iwata Make TFS 150 C9 Model, Compresso Two stage, Motor 15 HP & 57.18 CFM, 60 CFM Air Dryer with 2000 Ltrs Receiver Twin System (For Air4, Air7) | Job | 1895000
60 | Supporting structure for MGPS lines with Ismb Columns, beams, MS angles, Flats and square rods | Job | 795000
61 | 2x20 Oxygen Main manifold System | Job | 95000
62 | Electrical Control Panel for MGPS | Job | 145000
63 | Vaccum system Ingersoll Rand Make Model 15V x 10 Model with 5 HP Motor with 1000 Liters Reciever, Filters, Electricals, Etc Secretion Trap and Bacteria Filter | Job | 1495000
64 | Validation By Third Party Agency Charges per Each MOT | Each | 100000
65 | Anesthetic Gas Scavenging System (AGSS) | Job | 1213000
66 | 4 Gas Digital Alarm Panels : 4 Gas Digital Alarm Panel consisting of atl necessary accessories ie Pressure sensors,reguIators,hand valves ,pressure gauges ecL(Oxygen, Nitrous oxide, Medical Air, Vacuum) (for TIRs) | Nos | 42150
67 | 6 Gas Digital Alarm Panels : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. (for OTs) | Nos | 60008
68 | Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. (for TIRs) | Nos | 22201
69 | 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen. | Job | 48103
70 | 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | Job | 48103
71 | 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | Job | 17401
72 | Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED. | Job | 222013
73 | Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise & PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041. C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED | Job | 222013
DCA
74 | Supply Installation and Commissioning of PPFRP Exhaust System Polypropylene Fibre Reinforced Plastic as detailed in the Technical Specifications. | Job | 1800000
75 | Supply Installation and Commissioning of Gas Distribution System as detailed in the Technical Specifications. | JOB | 1298000

## Sheet2
S.No | Descriptio of item | UOM | QTY | IVF Gandhi Rate | Amount
1 | The Multipurpose Electro Hydraulic Mobile OT Table is designed for gynecological surgical procedures, featuring a wide range of adjustments for optimal patient positioning. It offers precise control with movement controls at the side of the table and a wired remote control handset and features like S. S. Arm Rest, Anaesthetic Screen, Lithotomy Leg Holders with Stirr-Ups, Leather Wristlets, Padded Leg Rest, Anti-static mattress, and an additional Poly-urethane mattress. Built with a Stainless Steel 304 frame and bottom, it ensures durability. The table top, reinforced with three-section stainless steel and radiolucent capabilities, allows for comprehensive patient support. Its flexibility includes 360° rotation, adjustable Trendelenburg, Reversed Trendelenburg, Head Section, Back Section, and Leg Section. Physical specifications include a 1900 mm x 525 mm top with an elevation range of 640mm to 1040mm, supporting patients up to 140 kg. Environmental considerations ensure operational efficiency in various conditions. | Nos | 1 | 210000 | 210000
2 | Fowler Two Function Bed with ABS Panel, ABS Side Railings, Wheels, Mattress Pillow, & Bed Fixing IV Road Features (Knee rest & Backrest) Size-L,84, W-42, H-24. The finished bed must be rust proof, pre-treated and treated with epoxy polyester antimicrobial powder coated to increase the bacteriostatic property. The bed must be quoted with washable cover of lasting quality. The mattress should be made of high-density PU foam of 100 mm thickness. | Nos | 5 | 39000 | 195000
3 | Bed side Table with ABS Plastic body construction having 1 drawer and an adequated space with openable door with handle of size | Nos | 5 | 9000 | 45000
|  |  |  | Total | 450000

## Sheet1
1 | gAicrerutL
2 | ptAdnaioat
3 | BecrIImeue
4 | TiesNopr
5 | cutrseFar
6 | noesuIg
7 | gYeienh
8 | uorsnen