## Sheet1
|  |  | New Freeze |  | VJ |  | Difference
S.No | Description | Nos | Supply | Erection | Supply | Erection | Supply | Erection
1 | Modular Double skin floor mounted EUROVENT Certified Air Handling Unit 3000CFM / 8.5 TR / 150mm SP made out of 45 plus or minus 2mm thick PUF insulated panels Thermal break aluminium profile frame work with 0.8mm thick pre painted / powder coated inner and outer skins comprising of mixing box with fresh air and return air dampers, pre filters with 10 and 5 microns combination filters in single frame, Interlaced/Intertwined DX Cooling Coil suitable for connecting 2 nos of 8.5TR capacity 1W plus 1S out door condensing units, SS304 drain pan with , blower section with Nicotra / Kruger make direct drive/ Plug type fan, vibration isolators, EFF1 motor and blower section with on/off switches to operate from outside, limit switch for the fan section access door with a view port, fine filter section with 3 microns filters inspection doors for all filter and fan sections and damper at the outlet of unit. Ports for differential pressure gauges across all filters and blower to measure differential pressure. AHU Make : VTS / Systemair, Make - Blower - Nicotra / Kruger ; Motor - Crompton Greaves / Siemens ; Filter - Thermodyne / Freudenberg / Ultrafil at Gandhi Hospital | 1 | 257484 | 25000 | 496000 | 22000 | -238516 | 3000
2 | SITC of air cooled condensing units with two scroll compressors, air cooled condenser, power panel, vibration isolating pads, stand for ODU, thermostat, etc. of the following capacities. The nominal capacity of the condensing unit shall be as under. Air cooled condensing unit shall have horizontal discharge. All refrigerant piping accessories sight glass, drier, expansion valve, etc. shall be supplied with the condensing units and suitable to connect above AHUs. Refrigerant shall be R 407C / R 410A. Necessary thermostat, control wiring, etc. shall be included. Derating of the unit shall not be more than 15percentage under 45 deg. C ambient temperature. Condensing unit shall be capable of operating up 50 deg. C ambient temperature. 8.5 TR capacity At Gandhi Hospital | 2 | 216000 | 25000 | 280000 | 52800 | -64000 | -27800
3 | SITC of Flange type, Flame proof FLP duct heaters of 5 kW capacity with Mineral Filled AISI SS304/SS321 Sheathed Tubular Heater with GI Helical fins, Tube dia 8.2mm min and Helical Finn dia 25mm min, enclosed in the frame, FLP Terminal box etc., Nickel Chromium Inner Element, Silicon Sealing to Restrict Moisture pickup, Silver brazed mounting plate etc., and heaters shall be controlled with PID thyrestor controller based on the analog output signal of 0-10 V DC of controller . And this should have saftey thermostat and cutouts and air stat etc. all safety controls. The capacities as follows and sizes of the heaters shall be as per the duct sizes and approved drawing. at Gandhi Hospital | 1 | 72500 | 8500 | 180752 | 8000 | -108252 | 500