## ROOM WISE
S.No | ROOM NAME | ROOM DIMENSIONS |  | LAB AREA IN SQM | FURNITURE DESCRIPTION | QTY IN NO'S | REMARKS | ELECTRICAL | [9 empty] | ELV |  |  |  |  | CIVIL | [12 empty] | PLUMBING | [9 empty] | NOT UNDER THE SCOPE OF THIS PROJECT ONLY TO BE MADE FOR FUNCTIONING OF THESE EQUIPMENT
[8 empty] | EXHAUST FAN/SYSTEM | POWER SOCKETS |  |  | SWITCH BOARDS |  | LIGHTS |  | FANS | AIR CONDITIONING | DATA | VOICE | SMOKE DETECTORS |  | PA SYSTEM | FALSE CEILING (SQM) | FLOORING(SQM) | SKIRTING (RMT) | HPL PARTITIONS (SQM) | DADOING (SQM) | WPC DOORS | SCIENTIFIC DOORS | UPVC WINDOWS | VENTILATORS | BRICK WORK |  | VIEW WINDOW (SQM) | PCGI PANELING (SQM) | BIB TAP | BRONZE GATE VALVE | MULTI FLOOR TRAP | WASH BASIN | EWC | 2 IN 1 FAUCET | SOAP DISH | TOWEL RING | MIRROR | SELF CLOSING TAP | EQUIPMENT PRPOSED | EXISTING | NEW PROCUREMENT | FUTURE PROCUREMENT | TOTAL
|  | L (mm) | B (mm) | [5 empty] | RP | UPS | MODULE |  |  | RP | UPS |  |  |  |  | ABOVE | BELOW | [10 empty] | 9 INCH | 4 INCH
1 | REFERENCE STANDARD ROOM | 4405 | 2700 | 11.8935 | REFRIGERATORS | 2 |  |  | 4 | 4 | 6M |  |  | 3 | 3 | 1 |  |  |  | 1 | 1 | 1 | 12 | 12 | 15 |  |  |  | 2.52 | 1.08 |  | 0.138 |  | 1.35 | 13
2 | INSTRUMENTATION ROOM-1 | 4405 | 11300 | 49.7765 | SITTING HEIGHT WORK BENCH | 9 | 2 CORNER CABINETS |  | 13 | 22 | 6M |  |  | 8 | 7 | 6 | 8TR DSU | 18 |  | 3 | 3 | 2 | 49.72 | 49.72 | 32 |  |  |  | 4.725 | 3.78 |  | 2.1 | 7.98
[5 empty] | CHAIRS TYPE-2 | 9
3 | BALANCE ROOM-1 | 3040 | 3240 | 9.8496 | ANTI VIBRATION TABLE | 5 |  |  |  | 5 | 6M |  |  | 2 | 2 | 1 | 2TR SPLIT | 5 |  | 1 | 1 | 1 | 9.8496 | 9.8496 | 13 |  |  |  | 2.1 | 1.08 |  | 0.138 | 11.1125
[5 empty] | CHAIRS TYPE-2 | 2 |  |  | 3 |  | 3M
4 | WET ANALYSIS LAB-1 | 10615 | 5805 | 61.6201 | STANDING HEIGHT WORK BENCH WITH SINK | 6 | 1 CORNER TABLE |  | 10 | 6 | 6M |  |  | 6 | 6 | 8 | 8.5 TR DSU | 3 |  | 3 | 3 | 2 | 61.48 | 61.48 | 32.84 |  |  |  | 4.725 | 3.24 |  | 0.414
[5 empty] | STANDING HEIGHT ISLAND WORK BENCH | 8 | OPPOSITE TO EACH
[5 empty] | ANTI VIBRATION TABLE | 3
[5 empty] | 2 TIER REAGENT RACKS | 4 |  |  | 8 | 2 | 6M | [6 empty] | 4
[5 empty] | SPOT EXTRACTORS | 6
[5 empty] | SINK | 3
[5 empty] | CHAIRS TYPE-2 | 8 | EXTRA TO BE ADDED
[5 empty] | VERTICAL STORAGE CABINET | 2
5 | DISSOLUTION ROOM-1 | 2640 | 5805 | 15.3252 | L SHAPE STANDING HEIGHT WORK BENCH WITH SINK | 2 |  |  | 4 | 4 | 6M |  |  | 3 | 3 | 2 |  | 6 |  | 1 | 1 | 1 | 15.312 | 15.312 | 16.88 |  |  |  | 6.93 | 1.08 |  | 4.807
[5 empty] | ANTI VIBRATION TABLE | 1
6 | WATER PURIFICATION ROOM-1 | 2595 | 3185 | 8.2651 | L SHAPE STANDING HEIGHT WORK BENCH WITH SINK | 1 |  |  | 5 | 2 | 6M |  |  | 2 | 2 | 1 | 1.5 TR SPLIT |  |  | 1 | 1 | 1 | 8.2651 | 8.2651 | 11.56 |  |  |  |  | 1.08 |  | 0.138 |  | 1.08
7 | WASH AREA-1 | 2595 | 2505 | 6.5005 | L SHAPE STANDING HEIGHT WORK BENCH WITH SINK | 1 |  |  | 6 | 2 | 6M |  |  | 2 | 2 |  |  |  |  | 1 | 1 | 1 | 6.5005 | 6.5005 | 10.2
8 | DOCCUMENTATION ROOM-1 | 3030 | 5805 | 17.5892 | WORK STATION | 8 |  |  | 16 | 8 | 6M |  |  | 3 | 3 | 2 | 2TR SPLIT | 8 |  | 1 | 1 | 1 | 17.5891 | 17.5891 | 17.67 |  |  |  | 2.52 | 2.16 |  | 0.276
[5 empty] | OVERHEAD STORAGE CABINETS | 11
[5 empty] | TASK CHAIRS | 8
[5 empty] | VERTICAL STORAGE CABINET | 1
9 | GENTS TOILETS | 3000 | 3425 | 10.275 |  |  |  | 1 | 1 |  | 3M |  |  | 4 | 2 |  |  |  |  | 1 | 1 |  | 10.275 | 10.275 |  | 11.13 | 26.88 | 2.1 | [7 empty] | 1 |  | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2
10 | LADIES TOILETS | 3000 | 3425 | 10.275 |  |  |  | 3 | 1 |  | 3M |  |  | 4 | 2 |  |  |  |  | 1 | 1 |  | 10.275 | 10.275 |  | 13.545 | 26.88 | 2.1 |  |  | 1.08 |  |  |  |  | 1 |  | 4 | 2 | 3 | 3 | 2 | 2 | 2 | 2
11 | DOCUMENTATION ROOM-2 | 6160 | 3440 | 21.1904 | WORK STATION | 8 |  |  | 16 | 8 | 6M |  |  | 3 | 3 | 2 | 2TR SPLIT | 8 |  | 1 | 1 | 1 | 21.1904 | 21.1904 | 19.2 |  |  |  | 2.52 | 2.16 |  | 0.276
[5 empty] | OVERHEAD STORAGE CABINETS | 11
[5 empty] | TASK CHAIRS | 8
[5 empty] | VERTICAL STORAGE CABINET | 1
12 | HOT ZONE ROOM | 6160 | 4950 | 30.492 | STANDING HEIGHT WORK BENCH | 6 |  |  | 18 | 6 | 6M |  |  | 6 | 6 | 4 |  |  |  | 2 | 2 | 2 | 30.492 | 30.492 | 22.22 |  |  |  | 2.52 | 1.08 |  | 0.138
[5 empty] | OVENS | 2
[5 empty] | FUME HOOD | 2 |  |  | 12 |  | 3M
[5 empty] | CORNER CABINETS | 2
13 | STAFF DINING ROOM | 6160 | 2425 | 14.938 | WALL MOUNTED DINING TABLE | 1 | [7 empty] | 3 | 3 | 2 | 2TR SPLIT |  |  | 1 | 1 |  | 14.938 | 14.938 | 17.17 |  |  |  | 2.52 | 1.08 |  | 0.138 |  |  |  | 1 |  | 1 | 1
[5 empty] | CHAIRS | 4
14 | DISSOLUTION ROOM-2 | 6160 | 2780 | 17.1248 | L SHAPE STANDING HEIGHT WORK BENCH WITH SINK | 1 |  |  | 4 | 8 | 6M |  |  | 3 | 3 | 2 |  | 12 |  | 1 | 1 | 1 | 17.1679 | 17.1679 | 17.894 |  |  |  | 4.725 | 1.08 |  | 0.138
[5 empty] | SPOT EXTRACTORS | 1
[5 empty] | CHAIRS TYPE-2 | 3
15 | WET ANALYSIS LAB-2 | 8715 | 5755 | 50.1548 | STANDING HEIGHT WORK BENCH WITH SINK | 6 | 1 CORNER TABLE |  | 10 | 7 | 6M |  |  | 8 | 8 | 8 | 8.5 TR DSU |  |  | 2 | 2 | 2 | 50.1112 | 50.1112 | 28.93 |  |  |  | 6.93 | 3.24 |  | 0.414 |  | 1.35
[5 empty] | STANDING HEIGHT ISLAND WORK BENCH | 6 | OPPOSITE TO EACH
[5 empty] | ANTI VIBRATION TABLE | 2
[5 empty] | 2 TIER REAGENT RACKS | 3 |  |  | 6 | 2 | 6M | [6 empty] | 2
[5 empty] | SPOT EXTRACTORS | 5
[5 empty] | SINK | 3
[5 empty] | CHAIRS TYPE-2 | 3 | EXTRA TO BE ADDED
[5 empty] | VERTICAL STORAGE CABINET | 1
16 | WATER PURIFICATION ROOM-2 | 3050 | 3190 | 9.7295 | L SHAPE STANDING HEIGHT WORK BENCH WITH SINK | 1 |  |  | 5 | 2 | 6M |  |  | 2 | 2 | 1 | 1.5 TR SPLIT |  |  | 1 | 1 | 1 | 9.7295 | 9.7295 | 12.48 |  |  |  |  | 2.16 |  | 0.276 |  | 1.35
17 | WASH AREA-2 | 3050 | 2460 | 7.503 | L SHAPE STANDING HEIGHT WORK BENCH WITH SINK | 1 |  |  | 8 | 1 | 6M |  |  | 2 | 2 |  |  |  |  | 1 | 1 | 1 | 7.503 | 7.503 | 11.02 |  |  |  |  | 1.08
18 | BALANCE ROOM-2 | 2830 | 5755 | 16.2867 | ANTI VIBRATION TABLE | 6 |  |  |  | 6 | 6M |  |  | 3 | 3 | 1 | 2TR SPLIT | 5 |  | 1 | 1 | 1 | 16.2725 | 16.2725 | 17.16 |  |  |  | 2.205 | 2.16 |  | 4.9047 |  | 1.35
[5 empty] | CHAIRS TYPE-2 | 1 |  |  | 6 |  | 3M
19 | INSTRUMENTATION ROOM-2 | 6795 | 5755 | 39.1052 | SITTING HEIGHT WORK BENCH | 8 | 2 CORNER CABINETS |  | 10 | 18 | 6M |  |  | 7 | 6 | 5 | 5.5 TR DSU | 15 |  | 1 | 1 | 1 | 39.0848 | 39.0848 | 25.39 |  |  |  | 2.52 | 5.4 |  | 0.69
[5 empty] | CHAIRS TYPE-2 | 8
20 | OFFICER ROOM-1 | 4405 | 3120 | 13.7436 | MANAGER WORK BENCH | 1 |  |  | 1 | 1 | 6M |  |  | 2 | 2 | 1 | 1.5TR SPLIT | 2 | 1 |  |  |  | 13.7436 | 13.7436 | 15.06 |  |  |  | 2.205 | 1.08
[5 empty] | MANAGER CHAIR | 1
[5 empty] | TASK CHAIRS | 2
[5 empty] | VERTICAL STORAGE CABINET | 2
21 | TOILET AT OFFICER ROOM-1 | 1500 | 1435 | 2.1525 |  |  |  | 1 | [5 empty] | 1 | 1 |  |  |  |  | 1 | 1 |  | 2.25 | 2.25 |  |  | 12.6 | 1.68 |  |  | 0.36 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
22 | OFFICER ROOM-2 | 4405 | 3050 | 13.4352 | MANAGER WORK BENCH | 1 |  |  | 1 | 1 | 6M |  |  | 2 | 2 | 1 | 1.5TR SPLIT | 2 | 1 |  |  |  | 13.7436 | 13.7436 | 15.06 |  |  |  | 2.205 | 1.08
[5 empty] | MANAGER CHAIR | 1
[5 empty] | TASK CHAIRS | 2
[5 empty] | VERTICAL STORAGE CABINET | 2
23 | TOILET AT OFFICER ROOM-2 | 1500 | 1435 | 2.1525 |  |  |  | 1 | [5 empty] | 1 | 1 |  |  |  |  | 1 | 1 |  | 2.25 | 2.25 |  |  | 12.6 | 1.68
24 | CORRIDOR-1 (OFFICER ROOMS) | 22110 | 1800 | 39.798 | [9 empty] | 6 | 2 |  |  |  |  | 3
25 | CORRIDOR-2 (WET ANALYSIS LAB-1) | 16000 | 1800 | 28.8 | [9 empty] | 3 | 2 |  |  |  |  | 1
26 | CORRIDOR-3 (HOT ZONE ROOM) | 19000 | 1800 | 34.2 | [9 empty] | 4 | 3 |  |  |  |  | 2
27 | CORRIDOR-4 (WET ANALYSIS LAB-2) | 7600 | 1800 | 13.68 | [9 empty] | 2 | 1 |  |  |  |  | 1
28 | CORRIDOR-5 (EMG EXIT) | 6500 | 1800 | 11.7 | [9 empty] | 2 | 1 |  |  |  |  | 1
| TOTAL |  |  | 567.5558 |  |  |  | 6 | 168 | 115 |  | 0 | 0 | 97 | 83 | 48 | 0 | 90 | 2 | 35 | 27 | 20 | 439.7429 | 439.7429 | 350.734 | 24.675 | 78.96 | 7.56 | 51.87 | 35.1 | 1.44 | 14.9857 | 19.0925 | 6.48 | 13 | 4 | 1 | 9 | 6 | 6 | 6 | 5 | 5 | 5 | 5
7.6
[8 empty] | 6m rp | 145
[8 empty] | 3m rp | 23
[8 empty] | 6m ups | 115
260
Note on R6: ASTA INFRA: TO BE CHECKED
Note on R10: ASTA INFRA: TO BE CHECKED
Note on R41: ASTA INFRA: TO BE CHECKED
Note on R53: ASTA INFRA: TO BE CHECKED

## ROOM WISE SCOPE
S.No | ROOM NAME | ROOM DIMENSIONS |  | LAB AREA IN SQM | FURNITURE DESCRIPTION | QTY IN NO'S | REMARKS | ELECTRICAL | [9 empty] | ELV |  |  |  |  | CIVIL | [12 empty] | PLUMBING | [9 empty] | NOT UNDER THE SCOPE OF THIS PROJECT ONLY TO BE MADE FOR FUNCTIONING OF THESE EQUIPMENT
[8 empty] | EXHAUST FAN/SYSTEM | POWER SOCKETS |  |  | SWITCH BOARDS |  | LIGHTS |  | FANS | AIR CONDITIONING | DATA | VOICE | SMOKE DETECTORS |  | PA SYSTEM | FALSE CEILING (SQM) | FLOORING(SQM) | SKIRTING (RMT) | HPL PARTITIONS (SQM) | DADOING (SQM) | WPC DOORS | SCIENTIFIC DOORS | UPVC WINDOWS | VENTILATORS | BRICK WORK |  | VIEW WINDOW (SQM) | PCGI PANELING (SQM) | BIB TAP | BRONZE GATE VALVE | MULTI FLOOR TRAP | WASH BASIN | EWC | 2 IN 1 FAUCET | SOAP DISH | TOWEL RING | MIRROR | SELF CLOSING TAP | EQUIPMENT PRPOSED | EXISTING | NEW PROCUREMENT | FUTURE PROCUREMENT | TOTAL
|  | L (mm) | B (mm) | [5 empty] | RP | UPS | MODULE |  |  | RP | UPS |  |  |  |  | ABOVE | BELOW | [10 empty] | 9 INCH | 4 INCH
1 | REFERENCE STANDARD ROOM | 4405 | 2700 | 11.8935 | REFRIGERATORS | 2 |  |  | 4 | 4 | 6M |  |  | 3 | 3 | 1 |  |  |  | 1 | 1 | 1 | 12 | 12 | 15 |  |  |  | 2.52 | 1.08 |  | 0.138 |  | 1.35 | 13
2 | INSTRUMENTATION ROOM-1 | 4405 | 11300 | 49.7765 | SITTING HEIGHT WORK BENCH | 9 | 2 CORNER CABINETS |  | 13 | 22 | 6M |  |  | 8 | 7 | 6 | 8TR DSU | 18 |  | 3 | 3 | 2 | 49.72 | 49.72 | 32 |  |  |  | 4.725 | 3.78 |  | 2.1 | 7.98
[5 empty] | CHAIRS TYPE-2 | 9
3 | BALANCE ROOM-1 | 3040 | 3240 | 9.8496 | ANTI VIBRATION TABLE | 5 |  |  |  | 5 | 6M |  |  | 2 | 2 | 1 | 2TR SPLIT | 5 |  | 1 | 1 | 1 | 9.8496 | 9.8496 | 13 |  |  |  | 2.1 | 1.08 |  | 0.138 | 11.1125
[5 empty] | CHAIRS TYPE-2 | 2 |  |  | 3 |  | 3M
4 | WET ANALYSIS LAB-1 | 10615 | 5805 | 61.6201 | STANDING HEIGHT WORK BENCH WITH SINK | 6 | 1 CORNER TABLE |  | 10 | 6 | 6M |  |  | 6 | 6 | 8 | 8.5 TR DSU | 3 |  | 3 | 3 | 2 | 61.48 | 61.48 | 32.84 |  |  |  | 4.725 | 3.24 |  | 0.414
[5 empty] | STANDING HEIGHT ISLAND WORK BENCH | 8 | OPPOSITE TO EACH
[5 empty] | ANTI VIBRATION TABLE | 3
[5 empty] | 2 TIER REAGENT RACKS | 4 |  |  | 8 | 2 | 6M | [6 empty] | 4
[5 empty] | SPOT EXTRACTORS | 6
[5 empty] | SINK | 3
[5 empty] | CHAIRS TYPE-2 | 8 | EXTRA TO BE ADDED
[5 empty] | VERTICAL STORAGE CABINET | 2
5 | DISSOLUTION ROOM-1 | 2640 | 5805 | 15.3252 | L SHAPE STANDING HEIGHT WORK BENCH WITH SINK | 2 |  |  | 4 | 4 | 6M |  |  | 3 | 3 | 2 |  | 6 |  | 1 | 1 | 1 | 15.312 | 15.312 | 16.88 |  |  |  | 6.93 | 1.08 |  | 4.807
[5 empty] | ANTI VIBRATION TABLE | 1
6 | WATER PURIFICATION ROOM-1 | 2595 | 3185 | 8.2651 | L SHAPE STANDING HEIGHT WORK BENCH WITH SINK | 1 |  |  | 5 | 2 | 6M |  |  | 2 | 2 | 1 | 1.5 TR SPLIT |  |  | 1 | 1 | 1 | 8.2651 | 8.2651 | 11.56 |  |  |  |  | 1.08 |  | 0.138 |  | 1.08
7 | WASH AREA-1 | 2595 | 2505 | 6.5005 | L SHAPE STANDING HEIGHT WORK BENCH WITH SINK | 1 |  |  | 6 | 2 | 6M |  |  | 2 | 2 |  |  |  |  | 1 | 1 | 1 | 6.5005 | 6.5005 | 10.2
8 | DOCCUMENTATION ROOM-1 | 3030 | 5805 | 17.5892 | WORK STATION | 8 |  |  | 16 | 8 | 6M |  |  | 3 | 3 | 2 | 2TR SPLIT | 8 |  | 1 | 1 | 1 | 17.5891 | 17.5891 | 17.67 |  |  |  | 2.52 | 2.16 |  | 0.276
[5 empty] | OVERHEAD STORAGE CABINETS | 11
[5 empty] | TASK CHAIRS | 8
[5 empty] | VERTICAL STORAGE CABINET | 1
9 | GENTS TOILETS | 3000 | 3425 | 10.275 |  |  |  | 1 | 1 |  | 3M |  |  | 4 | 2 |  |  |  |  | 1 | 1 |  | 10.275 | 10.275 |  | 11.13 | 26.88 | 2.1 | [7 empty] | 1 |  | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2
10 | LADIES TOILETS | 3000 | 3425 | 10.275 |  |  |  | 3 | 1 |  | 3M |  |  | 4 | 2 |  |  |  |  | 1 | 1 |  | 10.275 | 10.275 |  | 13.545 | 26.88 | 2.1 |  |  | 1.08 |  |  |  |  | 1 |  | 4 | 2 | 3 | 3 | 2 | 2 | 2 | 2
11 | DOCUMENTATION ROOM-2 | 6160 | 3440 | 21.1904 | WORK STATION | 8 |  |  | 16 | 8 | 6M |  |  | 3 | 3 | 2 | 2TR SPLIT | 8 |  | 1 | 1 | 1 | 21.1904 | 21.1904 | 19.2 |  |  |  | 2.52 | 2.16 |  | 0.276
[5 empty] | OVERHEAD STORAGE CABINETS | 11
[5 empty] | TASK CHAIRS | 8
[5 empty] | VERTICAL STORAGE CABINET | 1
12 | HOT ZONE ROOM | 6160 | 4950 | 30.492 | STANDING HEIGHT WORK BENCH | 6 |  |  | 18 | 6 | 6M |  |  | 6 | 6 | 4 |  |  |  | 2 | 2 | 2 | 30.492 | 30.492 | 22.22 |  |  |  | 2.52 | 1.08 |  | 0.138
[5 empty] | OVENS | 2
[5 empty] | FUME HOOD | 2 |  |  | 12 |  | 3M
[5 empty] | CORNER CABINETS | 2
13 | STAFF DINING ROOM | 6160 | 2425 | 14.938 | WALL MOUNTED DINING TABLE | 1 | [7 empty] | 3 | 3 | 2 | 2TR SPLIT |  |  | 1 | 1 |  | 14.938 | 14.938 | 17.17 |  |  |  | 2.52 | 1.08 |  | 0.138 |  |  |  | 1 |  | 1 | 1
[5 empty] | CHAIRS | 4
14 | DISSOLUTION ROOM-2 | 6160 | 2780 | 17.1248 | L SHAPE STANDING HEIGHT WORK BENCH WITH SINK | 1 |  |  | 4 | 8 | 6M |  |  | 3 | 3 | 2 |  | 12 |  | 1 | 1 | 1 | 17.1679 | 17.1679 | 17.894 |  |  |  | 4.725 | 1.08 |  | 0.138
[5 empty] | SPOT EXTRACTORS | 1
[5 empty] | CHAIRS TYPE-2 | 3
15 | WET ANALYSIS LAB-2 | 8715 | 5755 | 50.1548 | STANDING HEIGHT WORK BENCH WITH SINK | 6 | 1 CORNER TABLE |  | 10 | 7 | 6M |  |  | 8 | 8 | 8 | 8.5 TR DSU |  |  | 2 | 2 | 2 | 50.1112 | 50.1112 | 28.93 |  |  |  | 6.93 | 3.24 |  | 0.414 |  | 1.35
[5 empty] | STANDING HEIGHT ISLAND WORK BENCH | 6 | OPPOSITE TO EACH
[5 empty] | ANTI VIBRATION TABLE | 2
[5 empty] | 2 TIER REAGENT RACKS | 3 |  |  | 6 | 2 | 6M | [6 empty] | 2
[5 empty] | SPOT EXTRACTORS | 5
[5 empty] | SINK | 3
[5 empty] | CHAIRS TYPE-2 | 3 | EXTRA TO BE ADDED
[5 empty] | VERTICAL STORAGE CABINET | 1
16 | WATER PURIFICATION ROOM-2 | 3050 | 3190 | 9.7295 | L SHAPE STANDING HEIGHT WORK BENCH WITH SINK | 1 |  |  | 5 | 2 | 6M |  |  | 2 | 2 | 1 | 1.5 TR SPLIT |  |  | 1 | 1 | 1 | 9.7295 | 9.7295 | 12.48 |  |  |  |  | 2.16 |  | 0.276 |  | 1.35
17 | WASH AREA-2 | 3050 | 2460 | 7.503 | L SHAPE STANDING HEIGHT WORK BENCH WITH SINK | 1 |  |  | 8 | 1 | 6M |  |  | 2 | 2 |  |  |  |  | 1 | 1 | 1 | 7.503 | 7.503 | 11.02 |  |  |  |  | 1.08
18 | BALANCE ROOM-2 | 2830 | 5755 | 16.2867 | ANTI VIBRATION TABLE | 6 |  |  |  | 6 | 6M |  |  | 3 | 3 | 1 | 2TR SPLIT | 5 |  | 1 | 1 | 1 | 16.2725 | 16.2725 | 17.16 |  |  |  | 2.205 | 2.16 |  | 4.9047 |  | 1.35
[5 empty] | CHAIRS TYPE-2 | 1 |  |  | 6 |  | 3M
19 | INSTRUMENTATION ROOM-2 | 6795 | 5755 | 39.1052 | SITTING HEIGHT WORK BENCH | 8 | 2 CORNER CABINETS |  | 10 | 18 | 6M |  |  | 7 | 6 | 5 | 5.5 TR DSU | 15 |  | 1 | 1 | 1 | 39.0848 | 39.0848 | 25.39 |  |  |  | 2.52 | 5.4 |  | 0.69
[5 empty] | CHAIRS TYPE-2 | 8
20 | OFFICER ROOM-1 | 4405 | 3120 | 13.7436 | MANAGER WORK BENCH | 1 |  |  | 1 | 1 | 6M |  |  | 2 | 2 | 1 | 1.5TR SPLIT | 2 | 1 |  |  |  | 13.7436 | 13.7436 | 15.06 |  |  |  | 2.205 | 1.08
[5 empty] | MANAGER CHAIR | 1
[5 empty] | TASK CHAIRS | 2
[5 empty] | VERTICAL STORAGE CABINET | 2
21 | TOILET AT OFFICER ROOM-1 | 1500 | 1435 | 2.1525 |  |  |  | 1 | [5 empty] | 1 | 1 |  |  |  |  | 1 | 1 |  | 2.25 | 2.25 |  |  | 12.6 | 1.68 |  |  | 0.36 |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
22 | OFFICER ROOM-2 | 4405 | 3050 | 13.4352 | MANAGER WORK BENCH | 1 |  |  | 1 | 1 | 6M |  |  | 2 | 2 | 1 | 1.5TR SPLIT | 2 | 1 |  |  |  | 13.7436 | 13.7436 | 15.06 |  |  |  | 2.205 | 1.08
[5 empty] | MANAGER CHAIR | 1
[5 empty] | TASK CHAIRS | 2
[5 empty] | VERTICAL STORAGE CABINET | 2
23 | TOILET AT OFFICER ROOM-2 | 1500 | 1435 | 2.1525 |  |  |  | 1 | [5 empty] | 1 | 1 |  |  |  |  | 1 | 1 |  | 2.25 | 2.25 |  |  | 12.6 | 1.68
24 | CORRIDOR-1 (OFFICER ROOMS) | 22110 | 1800 | 39.798 | [9 empty] | 6 | 2 |  |  |  |  | 3
25 | CORRIDOR-2 (WET ANALYSIS LAB-1) | 16000 | 1800 | 28.8 | [9 empty] | 3 | 2 |  |  |  |  | 1
26 | CORRIDOR-3 (HOT ZONE ROOM) | 19000 | 1800 | 34.2 | [9 empty] | 4 | 3 |  |  |  |  | 2
27 | CORRIDOR-4 (WET ANALYSIS LAB-2) | 7600 | 1800 | 13.68 | [9 empty] | 2 | 1 |  |  |  |  | 1
28 | CORRIDOR-5 (EMG EXIT) | 6500 | 1800 | 11.7 | [9 empty] | 2 | 1 |  |  |  |  | 1
| TOTAL |  |  | 567.5558 |  |  |  | 6 | 168 | 115 |  | 0 | 0 | 97 | 83 | 48 | 0 | 90 | 2 | 35 | 27 | 20 | 439.7429 | 439.7429 | 350.734 | 24.675 | 78.96 | 7.56 | 51.87 | 35.1 | 1.44 | 14.9857 | 19.0925 | 6.48 | 13 | 4 | 1 | 9 | 6 | 6 | 6 | 5 | 5 | 5 | 5
7.6
[8 empty] | 6m rp | 145
[8 empty] | 3m rp | 23
[8 empty] | 6m ups | 115
260
Note on R6: ASTA INFRA: TO BE CHECKED
Note on R10: ASTA INFRA: TO BE CHECKED
Note on R41: ASTA INFRA: TO BE CHECKED
Note on R53: ASTA INFRA: TO BE CHECKED

## Furniture & Accessories BOQ
Second Floor Chemistry Lab
Furniture & Accessories BOQ
S.No | Description of Work | Quantity | Unit
1 | Room - 1 Documentation Room 6160 X 3440 MM (21.19 Sqm)
1.1 | Vertical Storage Cabinet | 1 | Nos
* 1000mm W x 450mm D x 2100mm H
* GI with Powder Coating
1.2 | Linear Workstation | 8 | Nos
Size: C 50- 1050X600X1200
* System: Connect 50mm thk tile based system * Size of the workstations are mentioned below * Height of the partation is 1800mm * Height of the table top is 727mm from floor level * 25mm thk pre laminate table top with PVC edge band * Gabel ends: Prelaminate gable ends considered under tabletop for support * Seperater: 30mm Thk Frame with Fabric considered between every two workstation * Finishes : 1st mod laminate tiles & 2nd mod Ino * Magnetic pinup tile, 1no laminate marker tile rest of are all fabric tiles per workstation * Electricals: Below the table top race ways are cosnidered at two different levels
1.2.1 | 3 Drawer Laminate Pedestal of size 400w X 450d X 680ht with levellers | 8 | Nos
1.2.2 | Metal Keyboard Tray | 8 | Nos
1.2.3 | Metal CPU Trolley | 8 | Nos
1.2.4 | Task chairs | 8 | Nos
* SPECIFICATIONS: * Back Height - Medium Back * Back Finish - Mesh with Lumbar Support * Back Mesh Colour - Black * Seat Finish - Fabric Olive Green * Seat Fabric Colour - Black * Seat Height Adjustment - Pneumatic * Armrests Type - 1 D arm * Base Type - 5-Star in Black Nylon
1.3 | Over Head Wall Storage Cabinet | 11 | Nos
* 750mm W x 350mm D x 600mm H
* GI with Powder Coating
2 | Room - 2 Hot Zone Room 6160 X 4950 MM (30.49 Sqm)
2.1 | 5' Bench Top Fume Hood
* 1500 x 1000 × 2350mm (W D H)
* MOC GI with Powder Coating
* FRP lined Interiors
* 6mm Tampered Safety Glass for Sash
Standard Base Cabinets - 2 Nos
* Light Fixture
* Filler Panels
* Dished Granite Work Top 18mm with finishing
* 3 Modular Cover frame with 6/16 A Switch & Sockets - 15 nos
* Remote Control Valves - 3 No's.
* PP Cup Sink
* Bottle Trap
* PVC Skirting
2.2 | Standing Height Work Bench
* 6160 × 750 x 900mm (W D H)
* GI with Powder Coating
* Black Granite Worktop
* Granite Skirting
* Standing Height Under Bench Frame - 1 No's.
* Standing Height Under Bench Cabinets Door + Drawer 600mm - 2 No's.
* Standing Height Under Bench Cabinets Door + Drawer 750mm - 2 No's.
* 750 mm Leg Space with openable panel - 3 No's.
* Filler Panels
* Service Drop - 1 No's
* Black Granite Support
* Electrical Race Way
* PVC Skirting
3 | ROOM - 3 : Dinning Room 6160 X 2425 MM (14.93 Sqm)
4 | ROOM - 4 : Dissolution Room 6160 X 2780 MM (17.12 Sqm)
4.1 | J Shape Sitting Height Work Bench with Sink Unit | 1 | Nos
* (4980 + 3560 + 2875 ) × 900 × 900mm (W D H)
* GI with Powder Coating
* Black Granite Worktop
* Granite Skirting
* Sitting Height Under Bench Cabinets Door + Drawer 600mm - 5 No's.
* Sitting Height Under Bench Cabinets Door + Drawer 750mm - 4 No's.
* 750 mm Leg Space with openable panel - 4 No's.
* Corner Sink Cabinet - 2 No's.
* PP Sink Unit - 2 No's
* Water Faucet with Necessary Hardware
* Peg Board
* PP Bottle Trap for Drain
* Dual Eye Washer
* Filler Panels
* Service Drop - 1 No's
* Black Granite Support
* Electrical Race Way
* PVC Skirting
4.2 | Lab Chairs | 3 | Nos
Comsat lab Chair with Seat and Back Cushion,Art Leather Finish, Foot rest Chrome Plated, Chrome Plated Gaslift Height Adjustment with 270 mm Ht, Chrome plated metal spider base, powder coated base plate, with Wheels, Finish Chrome Plated
5 | ROOM - 5 : Water Purification Room 3050 X 3190 MM (9.73 Sqm)
5.1 | L Shape Standing Height Work Bench with Sink Unit | 1 | Nos
* (2015 + 1030 + 2156 ) × 750 × 900mm (W D H)
* GI with Powder Coating
* Black Granite Worktop
* Granite Skirting
* Standing Height Under Bench Cabinets Door + Drawer 600mm - 3 No's.
* Standing Height Under Bench Cabinets Door + Drawer 750mm - 1 No's.
* 750 mm Leg Space with openable panel - 2 No's.
* Corner Sink Cabinet - 1 No's.
* PP Sink Unit - 1 No's
* Water Faucet with Necessary Hardware
* Peg Board
* PP Bottle Trap for Drain
* Dual Eye Washer
* Filler Panels
* Service Drop - 1 No's
* Black Granite Support
* Electrical Race Way
* PVC Skirting
6 | ROOM - 6 : Wash Area 3050 X 2460 MM (7.50 Sqm)
6.1 | L Shape Standing Height Work Bench with Sink Unit | 1 | Nos
* (3050 + 1737 ) × 750 × 900mm (W D H)
* GI with Powder Coating
* Black Granite Worktop
* Granite Skirting
* Standing Height Under Bench Cabinets Door + Drawer 600mm - 4 No's.
* 750 mm Leg Space with openable panel - 1 No's.
* Corner Sink Cabinet - 1 No's.
* PP Sink Unit - 1 No's
* GI Fabricated Canopy - 1 No's
* Water Faucet with Necessary Hardware - 1 No's
* Peg Board - 1 No's
* PP Bottle Trap for Drain - 1 No's
* Dual Eye Washer - 1 No's
* Filler Panels
* Service Drop - 1 No's
* Black Granite Support
* Electrical Race Way
* PVC Skirting
7 | ROOM - 7 : Wet Analysis Lab 8715 X 5755 MM (50.15 Sqm)
7.1 | Standing Height Work Bench with Sink Unit | 1 | Nos
* 14315 × 750 × 900mm (W D H
* GI with Powder Coating
* Black Granite Worktop
* Granite Skirting
* Standing Height Under Bench Cabinets Door + Drawer 750mm - 6 No's.
* 750 mm Leg Space with openable panel - 9 No's.
* Sink Cabinet - 4 No's.
* PP Sink Unit - 4 No's
* Water Faucet with Necessary Hardware
* Peg Board
* PP Bottle Trap for Drain
* Dual Eye Washer
* Filler Panels
* Service Drop - 1 No's
* Black Granite Support
* Electrical Race Way
* PVC Skirting
7.2 | Standing Height Island Work Bench | 1 | Nos
*4800 x 1500 × 900mm (W D H)
* GI with Powder Coating
* Black Granite Worktop
* Granite Skirting
* Granite for Reagent Rack
* Standing Height Under Bench Cabinets Door + Drawer 500mm - 4 No's.
* Standing Height Under Bench Cabinets Door + Drawer 750mm - 4 No's.
* 750 mm Leg Space with openable panel - 6 No's.
* Service Drop - 1 No's
* Filler Panels
* Double Sided 2 Tier Reagent Rack with 300mm Depth
* Black Granite Support
* Electrical Race Way
* PVC Skirting
7.3 | Standing Height Anti-Vibration Table | 2 | Nos
750mm W x 600mm D x 900mm H
* GI with Powder Coating
* Black Granite Worktop
7.4 | Lab Chairs | 3 | Nos
Comsat lab Chair with Seat and Back Cushion, Art Leather Finish, Foot rest Chrome Plated, Chrome Plated Gaslift Height Adjustment with 270 mm Ht, Chrome plated metal spider base, powder coated base plate, with Wheels, Finish Chrome Plated
7.5 | Vertical Storage Cabinet | 2 | Nos
* 1000mm W x 450mm D x 2100mm H
* GI with Powder Coating
8 | ROOM - 8 : Balance Room 2830 X 5755 MM (16.28 Sqm)
8.1 | Standing Height Anti-Vibration Table | 6 | Nos
750mm W x 600mm D x 900mm H
* GI with Powder Coating
* Black Granite Worktop
8.2 | Lab Chairs | 2 | Nos
Comsat lab Chair with Seat and Back Cushion, Art Leather Finish, Foot rest Chrome Plated, Chrome Plated Gaslift Height Adjustment with 270 mm Ht, Chrome plated metal spider base, powder coated base plate, with Wheels, Finish Chrome Plated
9 | ROOM - 9 : Instrumentation Room 6795 X 5755 MM (39.10 Sqm)
9.1 | C Shape Sitting Height Work Bench | 1 | Nos
* 6160 × 750 x 900mm (W D H)
* GI with Powder Coating
* Black Granite Worktop
* Granite Skirting
* Standing Height Under Bench Frame - 1 No's.
* Sitting Height Under Bench Cabinets Door + Drawer 600mm - 2 No's.
* Sitting Height Under Bench Cabinets Door + Drawer 750mm - 2 No's.
* Sitting Height Under Bench Corner Cabinets - 2 No's.
* 750 mm Leg Space with openable panel - 8 No's.
* Filler Panels
* Service Drop - 1 No's
* Black Granite Support
* Electrical Race Way
* PVC Skirting
9.2 | Lab Chairs | 8 | Nos
Comsat lab Chair with Seat and Back Cushion, Art Leather Finish, Foot rest Chrome Plated, Chrome Plated Gaslift Height Adjustment with 270 mm Ht, Chrome plated metal spider base, powder coated base plate, with Wheels, Finish Chrome Plated
10 | ROOM - 10 : Officer Room - 1 4405 X 3120 MM (13.74 Sqm)
10.1 | Workstation Size: 1500×600/Side; 900×450 Combo storage | 1 | Nos
* System : KD @, 727mm Ht
* Size of the table tops are mentioned below
* Height of the table top is 727mm FFL
* Table top: 25mm thk pre laminate table top with PVC edge band
* Legs: Laminate Legs,
* Modesty: 18mm thk prelam modesty
* Storage: 18mm thk prelam combo storage
* Electricals; 450mm W Aluminum flapup with metal switch mounting box and plate
10.2 | Manger Chair | 1 | Nos
* SPECIFICATIONS:
* Back Height - High back with head rest
* Back Finish - Mesh
* Back Mesh Colour - ( choice of colours)
* Seat Finish - Colour Fabric Olive Green
* Seat Height Adjustment - Pneumatic
* Armrests Type - 1D
* Base Type - 5-Star in Black Nylon.
10.3 | Task chairs | 2 | Nos
* SPECIFICATIONS:
* Back Height - Medium Back
* Back Finish - Mesh with Lumbar Support
* Back Mesh Colour - Black
* Seat Finish - Fabric Olive Green
* Seat Fabric Colour - Black
* Seat Height Adjustment - Pneumatic
* Armrests Type - 1 D arm
* Base Type - 5-Star in Black Nylon
10.4 | Vertical Storage Cabinet | 2 | Nos
* 1000mm W x 450mm D x 2100mm H
* GI with Powder Coating
11 | ROOM - 11 : Officer Room - 2 4405 X 3050 MM (13.43 Sqm)
11.1 | Workstation Size: 1500×600/Side; 900×450 Combo storage | 1 | Nos
* System : KD @, 727mm Ht
* Size of the table tops are mentioned below
* Height of the table top is 727mm FFL
* Table top: 25mm thk pre laminate table top with PVC edge band
* Legs: Laminate Legs,
* Modesty: 18mm thk prelam modesty
* Storage: 18mm thk prelam combo storage
* Electricals; 450mm W Aluminum flapup with metal switch mounting box and plate
11.2 | Manger Chair | 1 | Nos
* SPECIFICATIONS:
* Back Height - High back with head rest
* Back Finish - Mesh
* Back Mesh Colour - ( choice of colours)
* Seat Finish - Colour Fabric Olive Green
* Seat Height Adjustment - Pneumatic
* Armrests Type - 1D
* Base Type - 5-Star in Black Nylon.
11.3 | Task chairs | 2 | Nos
* SPECIFICATIONS:
* Back Height - Medium Back
* Back Finish - Mesh with Lumbar Support
* Back Mesh Colour - Black
* Seat Finish - Fabric Olive Green
* Seat Fabric Colour - Black
* Seat Height Adjustment - Pneumatic
* Armrests Type - 1 D arm
* Base Type - 5-Star in Black Nylon
11.4 | Vertical Storage Cabinet | 2 | Nos
* 1000mm W x 450mm D x 2100mm H
* GI with Powder Coating
12 | ROOM - 12 : Reference Standard Room - 2 4405 X 2700 MM (11.89 Sqm)
13 | ROOM - 13 : Instrumentation Room - 2 4405 X 11300 MM (49.78 Sqm)
13.1 | C Shape Sitting Height Work Bench | 1 | Nos
* 6160 × 750 x 900mm (W D H)
* GI with Powder Coating
* Black Granite Worktop
* Granite Skirting
* Standing Height Under Bench Frame - 1 No's.
* Sitting Height Under Bench Cabinets Door + Drawer 600mm - 2 No's.
* Sitting Height Under Bench Cabinets Door + Drawer 750mm - 2 No's.
* Sitting Height Under Bench Corner Cabinets - 2 No's.
* 750 mm Leg Space with openable panel - 8 No's.
* Filler Panels
* Service Drop - 1 No's
* Black Granite Support
* Electrical Race Way
* PVC Skirting
13.2 | Lab Chairs | 9 | Nos
Comsat lab Chair with Seat and Back Cushion, Art Leather Finish, Foot rest Chrome Plated, Chrome Plated Gaslift Height Adjustment with 270 mm Ht, Chrome plated metal spider base, powder coated base plate, with Wheels, Finish Chrome Plated
14 | ROOM - 14 : Balance Room - 2 3040 X 3240 MM (9.85 Sqm)
14.1 | Standing Height Anti-Vibration Table | 5 | Nos
750mm W x 600mm D x 900mm H
* GI with Powder Coating
* Black Granite Worktop
14.2 | Lab Chairs | 2 | Nos
Comsat lab Chair with Seat and Back Cushion, Art Leather Finish, Foot rest Chrome Plated, Chrome Plated Gaslift Height Adjustment with 270 mm Ht, Chrome plated metal spider base, powder coated base plate, with Wheels, Finish Chrome Plated
15 | ROOM - 15 : Wet Analysis Lab 10615 X 5805 MM (61.62 Sqm)
15.1 | Standing Height Work Bench with Sink Unit | 1 | Nos
* 14315 × 750 × 900mm (W D H
* GI with Powder Coating
* Black Granite Worktop
* Granite Skirting
* Standing Height Under Bench Cabinets Door + Drawer 750mm - 6 No's.
* 750 mm Leg Space with openable panel - 9 No's.
* Sink Cabinet - 4 No's.
* PP Sink Unit - 4 No's
* Water Faucet with Necessary Hardware
* Peg Board
* PP Bottle Trap for Drain
* Dual Eye Washer
* Filler Panels
* Service Drop - 1 No's
* Black Granite Support
* Electrical Race Way
* PVC Skirting
15.2 | Standing Height Island Work Bench | 1 | Nos
*4800 x 1500 × 900mm (W D H)
* GI with Powder Coating
* Black Granite Worktop
* Granite Skirting
* Granite for Reagent Rack
* Standing Height Under Bench Cabinets Door + Drawer 500mm - 4 No's.
* Standing Height Under Bench Cabinets Door + Drawer 750mm - 4 No's.
* 750 mm Leg Space with openable panel - 6 No's.
* Service Drop - 1 No's
* Filler Panels
* Double Sided 2 Tier Reagent Rack with 300mm Depth
* Black Granite Support
* Electrical Race Way
* PVC Skirting
15.3 | Standing Height Anti-Vibration Table | 3 | Nos
750mm W x 600mm D x 900mm H
* GI with Powder Coating
* Black Granite Worktop
15.4 | Lab Chairs | 6 | Nos
Comsat lab Chair with Seat and Back Cushion, Art Leather Finish, Foot rest Chrome Plated, Chrome Plated Gaslift Height Adjustment with 270 mm Ht, Chrome plated metal spider base, powder coated base plate, with Wheels, Finish Chrome Plated
15.5 | Vertical Storage Cabinet | 2 | Nos
* 1000mm W x 450mm D x 2100mm H
* GI with Powder Coating
16 | ROOM - 16 : Dissolution Room 2650 X 5805 MM (15.32 Sqm)
16.1 | J Shape Sitting Height Work Bench with Sink Unit | 1 | Nos
* (4980 + 3560 + 2875 ) × 900 × 900mm (W D H)
* GI with Powder Coating
* Black Granite Worktop
* Granite Skirting
* Sitting Height Under Bench Cabinets Door + Drawer 600mm - 1 No's.
* Sitting Height Under Bench Cabinets Door + Drawer 750mm - 2 No's.
* 750 mm Leg Space with openable panel - 2 No's.
* Corner Sink Cabinet - 1 No's.
* PP Sink Unit - 1 No's
* Water Faucet with Necessary Hardware
* Peg Board
* PP Bottle Trap for Drain
* Dual Eye Washer
* Filler Panels
* Service Drop - 1 No's
* Black Granite Support
* Electrical Race Way
* PVC Skirting
16.2 | Lab Chairs | 2 | Nos
Comsat lab Chair with Seat and Back Cushion,Art Leather Finish, Foot rest Chrome Plated, Chrome Plated Gaslift Height Adjustment with 270 mm Ht, Chrome plated metal spider base, powder coated base plate, with Wheels, Finish Chrome Plated
17 | ROOM - 17 : Water Purification Room 2595 X 3185 MM (8.27 Sqm)
17.1 | L Shape Standing Height Work Bench with Sink Unit | 1 | Nos
* (2015 + 1030 + 2156 ) × 750 × 900mm (W D H)
* GI with Powder Coating
* Black Granite Worktop
* Granite Skirting
* Standing Height Under Bench Cabinets Door + Drawer 600mm - 2 No's.
* Standing Height Under Bench Cabinets Door + Drawer 750mm - 1 No's.
* 750 mm Leg Space with openable panel - 2 No's.
* Corner Sink Cabinet - 1 No's.
* PP Sink Unit - 1 No's
* Water Faucet with Necessary Hardware
* Peg Board
* PP Bottle Trap for Drain
* Dual Eye Washer
* Filler Panels
* Service Drop - 1 No's
* Black Granite Support
* Electrical Race Way
* PVC Skirting
18 | ROOM - 18 : Wash Area 2595 X 2505 MM (6.50 Sqm)
18.1 | L Shape Standing Height Work Bench with Sink Unit | 1 | Nos
* (3050 + 1737 ) × 750 × 900mm (W D H)
* GI with Powder Coating
* Black Granite Worktop
* Granite Skirting
* Standing Height Under Bench Cabinets Door + Drawer 600mm - 4 No's.
* 750 mm Leg Space with openable panel - 1 No's.
* Corner Sink Cabinet - 1 No's.
* PP Sink Unit - 1 No's
* GI Fabricated Canopy - 1 No's
* Water Faucet with Necessary Hardware - 1 No's
* Peg Board - 1 No's
* PP Bottle Trap for Drain - 1 No's
* Dual Eye Washer - 1 No's
* Filler Panels
* Service Drop - 1 No's
* Black Granite Support
* Electrical Race Way
* PVC Skirting
19 | Room - 19 Documentation Room 5805 X 3030 MM (17.58 Sqm)
19.1 | Vertical Storage Cabinet | 1 | Nos
* 1000mm W x 450mm D x 2100mm H
* GI with Powder Coating
19.2 | Linear Workstation | 8 | Nos
Size: C 50- 1050X600X1200
* System: Connect 50mm thk tile based system * Size of the workstations are mentioned below * Height of the partation is 1800mm * Height of the table top is 727mm from floor level * 25mm thk pre laminate table top with PVC edge band * Gabel ends: Prelaminate gable ends considered under tabletop for support * Seperater: 30mm Thk Frame with Fabric considered between every two workstation * Finishes : 1st mod laminate tiles & 2nd mod Ino * Magnetic pinup tile, 1no laminate marker tile rest of are all fabric tiles per workstation * Electricals: Below the table top race ways are cosnidered at two different levels
19.2.1 | 3 Drawer Laminate Pedestal of size 400w X 450d X 680ht with levellers | 8 | Nos
19.2.2 | Metal Keyboard Tray | 8 | Nos
19.2.3 | Metal CPU Trolley | 8 | Nos
19.2.4 | Task chairs | 8 | Nos
* SPECIFICATIONS: * Back Height - Medium Back * Back Finish - Mesh with Lumbar Support * Back Mesh Colour - Black * Seat Finish - Fabric Olive Green * Seat Fabric Colour - Black * Seat Height Adjustment - Pneumatic * Armrests Type - 1 D arm * Base Type - 5-Star in Black Nylon
19.3 | Over Head Wall Storage Cabinet | 11 | Nos
* 750mm W x 350mm D x 600mm H
* GI with Powder Coating

## Civil
S.No | Item Code | Description | Units | Qty | R/Unit
CIVIL WORKS
Dismantling
|  | Dismantling clearing away and carefully stacking useful materials for re use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges etc complete for Brick masonry | Cum | 40
|  | Dismantling clearing away and carefully stacking useful materials for re use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges etc complete for Flooring | Sqm | 550
|  | Dismantling clearing away and carefully stacking useful materials for re use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges complete Reinforced cement concrete | Cum | 12
|  | Dismantling clearing away and carefully stacking useful materials for re use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges complete Unreinforced cement concrete up to 15cm thickness | Cum | 10
|  | Dismantling clearing away and carefully stacking useful materials for re use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges etc complete for False Ceiling | Sqm | 500
|  | Dismantling doors windows and clear storey windows Ventilators etc wood or steel shutters including Chowkhats architraves hold fasts and other attachments etc and stacking them within 100m lead including labour charge etc complete for finished item of work. Not exceeding 3 sqm in area. | No | 59
|  | Conveyance of un useful excavated earth debris to a distance of 21 KM for disposal including hire charges of T and P labour charges etc complete for finished item of work. | Cum | 50
|  | Dismantling,Clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual pre-measurements before diamantling including all labour charges etc., complete. Not Exceeding 3 sqm in area (Wooden partitions / cupboards) | Sqm | 2
|  | Dismantling doors, windows, and clear storey windows, Ventilators etc., (wood or steel) shutters including chowkhats, architraves, hold fasts and other attachments etc., and staking them with in 100m lead including labour charges etc., complete for finished item of work. Exceeding 3 sqm in area | No | 2
Brick Masonry & Plastering
|  | Reinforced Masonry for partition walls 100 mm thick in CM 1:4 prop. as per Technical Specifications APSS No. of 509 | Sqm | 65
|  | Brick Masonry in CM 1:6 prop as per Technical Specifications. APSS No. 501 and 504 | Cum | 25
|  | Supply and placing of the Reinforced Cement Concrete M 20 grade Nominal Mix as per Technical specifications For Lintels | Cum | 2
|  | Plastering 12mm thick in two coats with base coat of 8mm thick in CM 1:6 and topcoat of 4mm thick in CM 1:4 as per Technical Specification SS 901 903 and 904 | Sqm | 450
|  | Plastering 20mm thick in two coats with base coat of 16mm thick in CM 1:6 and top coat of 4mm thick in CM 1:4 as per Technical Specification SS 901 903 and 904 | Sqm | 50
Flooring
|  | Flooring with Double Charged vitrified tiles of size 600 x 600 mm as per Technical Specifications | Sqm | 500
|  | Providing skirting to internal walls to 10 cm height with Double Charged vitrified tiles of size 600x600 as per Technical Specification | Rmt | 550
|  | Providing specialized high performance acrylic polymer modified elastomeric cementitious waterproof coating to the terrace walls internal portion of the bathroom and toilets internal portion of the water tanks Pg.no 729 SOR No TBSCQ.VII 04 as per Technical Specifications. | Sqm | 30
|  | Providing impervious coat to exposed RCC roof slab surfaces as per Technical Specifications | Sqm | 30
|  | Filling with light weight concrete in Cement Concrete (1:5:10) prop. Ax per Technical Specifications | Cum | 5
|  | Flooring with non skid full body ceramic floor tiles as per Technical Specifications | Sqm | 30
|  | Providing dadooing to walls with glazed full body porcelain wall tiles as per Technical Specifications. | Sqm | 90
Expansion joint Treatment
|  | Providing specialized polysulphide sealant treatment to the expansion joints as per Technical Specifications. Sl.no 732 SOR. No TBSCQ.VII 07, including fixing of 24 gauge alluminium sheet over expansion joint | JOB | 1
|  | Supply, erection and fixing of Emergency Exit Door Panic Door with Metal door frames and door shutters made of galvanized steel as per Technical Specifications. | No | 1
Doors & Windows
|  | Supplying and fixing of Unplasticised PolyVinyl Chloride UPVC 3 track sliding Windows and with 7.5mm thick Aluminium Grill as per Technical Specifications. | Sqm | 40
|  | Providing False Ceiling as per Technical Specifications. | Sqm | 485
|  | Painting coat Water Based Cement Primer of Interior Grade I and Two coats of Acrylic Emulsion Paint over Wall putty of White Cement or Polymer or Cement based: as per Technical Specifications. | Sqm | 1540
|  | Painting coat Water Based Cement Primer of Exterior Grade II and two coats of Acrylic Emulsion paint over Exterior grade Texture ready mixed paint with sand texture as per Technical Specifications. | Sqm | 60
|  | Effluent Collection Tank: Earthwork excavation, PCC 1:4:8 150mm thick , RCC M25 300mm thick base Base Slab, RCC M 25 230mm side walls, Supply, fabricating, erecting and fixing in position trusses of approved design with structural steel other than MS circular tubes including roof frame work, Supply and Installation of two 5000 Litres HDPE Tanks with Pumping System 1 Running and 1 Stand by inside the constructed RCC structure complete as per Technical specifications for finished item of work as approved by the Engineer-in-Charge. | JOB
|  | Providing and Fixing of Scientific Doors as per Technical Specifications. | Sqm | 60
|  | Providing Thermo Mechanically Treated (TMT) (Fe-500/500D/550D from Primary producer TATA, SAIL, VSP.JSW&Shyam Steel etc as per IS 1786-2008) of different diameters for RCC works, including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting. bending, placing in position, tying including sales and other taxes on all materials etc. ,and overheads & contractors profit complete for finished item of work. APSS No. 126) For Chajjas & Lintels | MT | 0.3
|  | Flooring with 16 to 18 mm thick high polished granite st slabs black colour as approved by the Engineer-in-Charge of length not less than 2.43 mts set over base coat of cement mortar (1:8) , 20mm thick using screened sand over CC bed already laid or RCC roof slab including neat grey cement slurry of hy like consistency spread @ 3.3 Kg per sqm and jointed neatly with white cement paste mixed with pigment of matching shade to full depth including cost and conveyance of all materials like cement , sand , water , granite slabs etc., to work site and all operational, incidental labour & lift charges, half rounding the edge , polishing charges and all other taxes on all materials, cost of base coat and overheads & contractors profit complete for finished item of work for platforms (S.S.701 & special) (At room entry) | Sqm | 5
|  | Supplying and fixing of 30mm thick Wood Plastic Composite (WPC) Door shutter, comprising of 70% virgin polymer, 15% wood powder (fiber), and the remaining 15% additives, the door shutter shall be water resistant, fire resistant and termite resistant, with Tensile Strength not less than 170 Kgf/cm2 and the door shutters surface finished deco paint etc., complete excluding cost of hinges, latches, aldrops etc., and including ISI marked Stainless Steel fixtures 3 Nos. butt hinges (IS:205) of 75mm long, 1 No. aldrop (IS:15834) 200 mm long, 1 No. tower bolt (IS:15833) of 100 mm x 10mm dia, 1 No. 105mm long handles (IS:208), including labour charges for fixing the frame in position, fixing the shutter to the frame etc., including overheads & contractors profit complete for finished item of work as per APSS 1001 & 1002. (The vertical frame of door shall be embedded in flooring for deth of not less than 10mm) (1000mm x 2100mm) (Toilets) | Sqm | 8
|  | Providing and fixing factory made solid Wood Polymer Composite (WPC) single extruded Door Frame section of 100*65 MM with encapsulation of 6 MM rigid layer on all external surfaces. The door frame will have a rebate of 32MM/ 37 MM. The two Vertical members are to be joined together with the horizontal member using 8x75MM long MS Star full thread screws to be used with reverse forward speed control hand rilling machine. The ready/assembled door frame is fixed to wall using Z Hand fast 300 MM long hold fast. (For Toilets) | Rmt | 25
|  | Supply and fixing of Aluminium Frame work with supporting Aluminium sections of size 40×25mm of 2mm thick for outer frame & verticals ,of size 40x20mm of 2mm thick High Pressure Laminated (HPL) Cubicals including fixing the required number of screws bolts,ss butt hinges ss tower bolt ,ss handles and also silicon jell and nut including labour charges for fixing the frame in position using High Pressure Laminated Boards Sheet, including cost and conveyance of all materials etc., complete as directed as approved by Engineer-in-charge during execution including overheads & contractors profit etc., complete for finished item of work. (For Toilets) | Sqm | 30
|  | Supply and Fixing of name Boards with approved names on Acrylic sheet including cost of materials, cutting printing names and fixing particulars location labour charges etc., complete for finished item of work Acrylic 3mm signage boards for Size 6"x24" | Nos | 35
Plumbing
S.No | Item Code | Description | Units | Qty | R/Unit
|  | Supplying and fixing 15 mm brass body CP finish bib tap of not less than 300 grams weight screw type full turn with internal/external threaded connection conforming to IS 8931 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, overheads and contractors profit complete for finished item of work in all floors. | No | 2
|  | Supply and fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings SDR 13.5 to meet the requirement of ASTM-D 2846 and are produced in CTS Copper Tube Sizes 1/2inches to 2inches for hot and cold water IS 15778:2007 including cost and conveyance of all materials to site, labour charges for fixing, complete for finished item of work at all floor levels. 15.90mm OD pipe | Rmt | 90
|  | Supply and fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings SDR 13.5 to meet the requirement of ASTM-D 2846 and are produced in CTS Copper Tube Sizes 1/2inches to 2inches for hot and cold water IS 15778:2007 including cost and conveyance of all materials to site, labour charges for fixing,complete for finished item of work at all floor levels. 22.20mm OD pipe | Rmt | 60
|  | Supplying and fixing of SWR PVC pipes Prince/Sudhakar/ Kisan /Supreme or any ISI brand 4 Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, complete for finished item of work at all floor levels. APSS No. 1302 1319 and 1326 - 75mm dia | Rmt | 60
|  | Supplying and fixing of SWR PVC pipes Prince/Sudhakar/Kisan /Supreme or any ISI brand 4 Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, complete for finished item of work at all floor levels. APSS No. 1302 1319 and 1326- 110mm dia | Rmt | 60
|  | Supplying and fixing Bronze Gate/ Globe valve as per IS - 778 Class - I, Indian make heavy type including cost and conveyance of all materials , labour charges , overheads and contractors profit complete for finished item of work. 25mm Nominal bore | No | 7
|  | Supplying and fixing of 4inches 101.6mm multi floor trap with jali - UPVC/SWR pipe fittings as per site requirements with standard practice for all floors including cost and conveyance of all materials to site, labour charges ,etc., complete for finished item of work. | No | 10
|  | Supplying and fixing Indian make Flat Back Wash Hand Basin 1st quality conforming to IS:2556-Part-4:1972 of size 550mm x 400mm with 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963- 1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make heavy duty complete with standard CI brackets including wooden blocks ,1 No.12.70mm PVC connection with brass union nuts CP coated , angle stop cock 12.70mm dia. first quality Indian make heavy duty, 30mm dia. PVC flexible waste pipe 914.4mm length of 1st quality including cost and conveyance of all materials to site, labour charges, for finished item of work | No | 6
|  | Supply, Installation and commissioning approved make floor mounted EWC conforming to IS:2556 Part 8-2004 suit with P or S trap with dual flush porcelain cistern fixed on wash down EWC with all internal parts of dual flush cistern, ultra solid seat cover of approved make with rubber buffer and cap and 15 mm angle stop cock and 450 mm long PVC inter connection pipe wall flanges all of approved make etc. complete for finished item of work in all respects: TBSP-E.II-03 | No | 7
|  | Supplying and fixing Chromium plated finish brass body quarter turn Bibcock cum Health Faucet with 1m long tube and wall hook with necessary fittings etc., complete including cost and conveyance of all materials, labour charges, complete for finished item of work in all floors. | No | 7
|  | Supplying and fixing CP finish brass soap dish of approved make ISI quality including cost and conveyance of all materials, labour charges for fixing, for finished item of work in all floors | No | 6
|  | Supplying and fixing TV shape mirror with plastic frame of size 609.6mm x 457.2mm, plywood back with NP screws 1st quality including cost and conveyance of all materials, labour charges, for finished item of work in all floors. | No | 6
|  | Supplying and fixing of CP finish brass wall mounted towel ring | No | 6
|  | Supplying and fixing 15 mm brass body CP finish self closing tap push type conforming to IS 1711 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, complete for finished item of work in all floors. | No | 6
|  | Supply and Fixing of white glazed flat back bowl urinals | Nos | 2
|  | Supply and fixing of Aluminium Frame work with supporting Aluminium sections of size 40×25mm of 2mm thick for outer frame & verticals ,of size 40x20mm of 2mm thick High Pressure Laminated (HPL) Cubicals including fixing the required number of screws bolts,ss butt hinges ss tower bolt ,ss handles and also silicon jell and nut including labour charges for fixing the frame in position using High Pressure Laminated Boards Sheet, including cost and conveyance of all materials etc., complete as directed as approved by Engineer-in-charge during execution including overheads & contractors profit etc., complete for finished item of work. (For Toilets) | Sqm | 30
|  | Providing and placing on terrace (at all floor levels) polyetheylene water storage tank with double layer approved brand and manufacture with cover and suitable locking arrangement and making necessary holes for inlet and outlets and over flow pipes but without fittings and base support for tanks including cost and conveyance of all materials and labour charges , overheads & contractors profit complete for finished item of work. (Storage Tanks) -1000 Ltr | Nos | 1
|  | Description | Units | Qty
|  | 1.5 TR Split AC | No | 4
|  | 2 TR Split AC | No | 5
|  | 8.5 / 11 TR DSU | No | 4
|  | Supply Installation and Commissioning of PPFRP Exhaust System Polypropylene Fibre Reinforced Plastic as detailed in the Technical Specifications | JOB | 1
PPFRP

## LAB Furniture
S.No | Item Code | Description | Units | Qty | R/Unit
|  | C Shaped Sitting Height Work Bench (750mm) | No | 2
|  | J Shaped Sitting Height work Bench with Sink (750mm) | No | 1
|  | Standing Height Works Bench (900mm) | No | 2
|  | Standing Height Work Bench with Sink | No | 2
|  | L Shaped Standing Height Work Bench with Sink | No | 6
|  | Standing Height Island Work Bench | No | 2
|  | Standing Height Anti Vibration Tables | No | 17
|  | Vertical Storage Cabinet | No | 10
|  | Sitting Height Work Bench (750mm) | No
|  | Overhead Wall Storage Cabinets | No | 22
|  | Lab Chairs Type II | No | 30
|  | Task Chairs | No | 10
|  | Manager Chair | No | 2
|  | Linear work Stations | No | 2
|  | Manager Work Station | No | 2
|  | Spot Extractors | No | 22
|  | 5 Feet Bench Top Fume Hood | No | 2

## Plumbing
S.No | Item Code | Description | Units | Qty | R/Unit
|  | Supplying and fixing 15 mm brass body CP finish bib tap of not less than 300 grams weight screw type full turn with internal/external threaded connection conforming to IS 8931 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, overheads and contractors profit complete for finished item of work in all floors. | No | 2
|  | Supply and fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings SDR 13.5 to meet the requirement of ASTM-D 2846 and are produced in CTS Copper Tube Sizes 1/2inches to 2inches for hot and cold water IS 15778:2007 including cost and conveyance of all materials to site, labour charges for fixing, complete for finished item of work at all floor levels. 15.90mm OD pipe | Rmt | 90
|  | Supply and fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings SDR 13.5 to meet the requirement of ASTM-D 2846 and are produced in CTS Copper Tube Sizes 1/2inches to 2inches for hot and cold water IS 15778:2007 including cost and conveyance of all materials to site, labour charges for fixing,complete for finished item of work at all floor levels. 22.20mm OD pipe | Rmt | 60
|  | Supplying and fixing of SWR PVC pipes Prince/Sudhakar/ Kisan /Supreme or any ISI brand 4 Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, complete for finished item of work at all floor levels. APSS No. 1302 1319 and 1326 - 75mm dia | Rmt | 60
|  | Supplying and fixing of SWR PVC pipes Prince/Sudhakar/Kisan /Supreme or any ISI brand 4 Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, complete for finished item of work at all floor levels. APSS No. 1302 1319 and 1326- 110mm dia | Rmt | 60
|  | Supplying and fixing Bronze Gate/ Globe valve as per IS - 778 Class - I, Indian make heavy type including cost and conveyance of all materials , labour charges , overheads and contractors profit complete for finished item of work. 25mm Nominal bore | No | 7
|  | Supplying and fixing of 4inches 101.6mm multi floor trap with jali - UPVC/SWR pipe fittings as per site requirements with standard practice for all floors including cost and conveyance of all materials to site, labour charges ,etc., complete for finished item of work. | No | 10
|  | Supplying and fixing Indian make Flat Back Wash Hand Basin 1st quality conforming to IS:2556-Part-4:1972 of size 550mm x 400mm with 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963- 1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make heavy duty complete with standard CI brackets including wooden blocks ,1 No.12.70mm PVC connection with brass union nuts CP coated , angle stop cock 12.70mm dia. first quality Indian make heavy duty, 30mm dia. PVC flexible waste pipe 914.4mm length of 1st quality including cost and conveyance of all materials to site, labour charges, for finished item of work | No | 6
|  | Supply, Installation and commissioning approved make floor mounted EWC conforming to IS:2556 Part 8-2004 suit with P or S trap with dual flush porcelain cistern fixed on wash down EWC with all internal parts of dual flush cistern, ultra solid seat cover of approved make with rubber buffer and cap and 15 mm angle stop cock and 450 mm long PVC inter connection pipe wall flanges all of approved make etc. complete for finished item of work in all respects: TBSP-E.II-03 | No | 7
|  | Supplying and fixing Chromium plated finish brass body quarter turn Bibcock cum Health Faucet with 1m long tube and wall hook with necessary fittings etc., complete including cost and conveyance of all materials, labour charges, complete for finished item of work in all floors. | No | 7
|  | Supplying and fixing CP finish brass soap dish of approved make ISI quality including cost and conveyance of all materials, labour charges for fixing, for finished item of work in all floors | No | 6
|  | Supplying and fixing TV shape mirror with plastic frame of size 609.6mm x 457.2mm, plywood back with NP screws 1st quality including cost and conveyance of all materials, labour charges, for finished item of work in all floors. | No | 6
|  | Supplying and fixing of CP finish brass wall mounted towel ring | No | 6
|  | Supplying and fixing 15 mm brass body CP finish self closing tap push type conforming to IS 1711 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, complete for finished item of work in all floors. | No | 6
|  | Supply and Fixing of white glazed flat back bowl urinals | Nos | 2
|  | Supply and fixing of Aluminium Frame work with supporting Aluminium sections of size 40×25mm of 2mm thick for outer frame & verticals ,of size 40x20mm of 2mm thick High Pressure Laminated (HPL) Cubicals including fixing the required number of screws bolts,ss butt hinges ss tower bolt ,ss handles and also silicon jell and nut including labour charges for fixing the frame in position using High Pressure Laminated Boards Sheet, including cost and conveyance of all materials etc., complete as directed as approved by Engineer-in-charge during execution including overheads & contractors profit etc., complete for finished item of work. (For Toilets) | Sqm | 30
|  | Providing and placing on terrace (at all floor levels) polyetheylene water storage tank with double layer approved brand and manufacture with cover and suitable locking arrangement and making necessary holes for inlet and outlets and over flow pipes but without fittings and base support for tanks including cost and conveyance of all materials and labour charges , overheads & contractors profit complete for finished item of work. (Storage Tanks) -1000 Ltr | Nos | 1

## ELV
S.No | Item Code | Description | Units | Qty | R/Unit
|  | Supply erection testing and commissioning Fire Detection and Alarm System including all accessories complete as per the Technical Specifications. | JOB | 1
Fire Alarm
|  | Supply and Fixing of ABC Powder MAP 4 Kg Fire extinguisher complete as per the Technical Specifications. | No | 10
|  | Supply and Fixing of ABC Powder MAP 2 Kg Fire extinguisher complete as per the Technical Specifications. | No | 10
|  | Supply and fixing of Photoluminiscent Safety Signages and Lab Name Boards etc as per the Technical Specifications. | JOB | 1
Extinguishers & Signages
|  | Supply erection testing and commissioning 30KVA UPS System. | Nos | 1
|  | Supply, transportation and fixing of 12V 100 AH SMF batteries 32 No including wire leads.complete as per the Technical Specifications. | Nos | 32
UPS
|  | Supply erection testing and commissioning of Teleph lines including wires, jacks, distribution boxes with backmount frame, connector, pwder coated metal body with lock and key arrangement, etc as per the Technical Specifications. | JOB | 1
Telephone
|  | Supply erection testing and commissioning of LAN System including Cat 6 RJ 45 outlets, Cat 6 UTP cable, network racks with power spike and accessories, 24 port and 48 port manageble switches etc as per the Technical Specifications.-90 Pts | JOB | 1
LAN System
|  | Supply Installation testing and commissioning of Public Address System etc as per the Technical Specifications.- 20 Pts | JOB | 1
Public Address
|  | Supply installation testing and commissioning of IP based Digital Teleph EPABX System etc as per the Technical Specifications. | No | 1
EPBAX
|  | Supply erection testing and commissioning of Access Control System as per the Technical Specifications. | No | 2
|  | Supplying of Access Control System Cards with Reading Software to enable restricted access in the DCA Laboratory, including cost and conveyance of all materials etc., complete for finished item of work. |  | 25
Access Control

## Electrical
S.No | Item Code | Description | Units | Qty | R/Unit
Conduit Pipe
|  | Supply and Laying of ISI 25mm outer dia heavy grade with IS:9537 part 3 rigid PVC pipe concealed in Roof Slabs with all required PVC / Metallic Deep Boxes including masonary work and labour charges etc., complete. Makes : Sudhakar / Finolex / Modi / VIP / Precision / Universal / Million Plast / Gold / Polycab / DEC | RM | 450
|  | Supply and laying of ISI 25mm outer dia medium grade, with IS:9537 part 3 rigid PVC concealed in wall with all required PVC / Metallic Junction Boxes including masonary work and labour charges etc., Makes:- Sudhakar / Finolex / Modi / VIP / Precision / Universal / Million Plast / Gold / Polycab / DEC. | RM | 3400
|  | Supply and erecting PVC / GI / MS Galvanished fan hook box with hook in RCC slab including all Labour charges etc., complete. | EACH | 60
WIRING
|  | Wiring with run of 2 of 1.5 Sqmm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specification for Copper cable. in existing PVC conduit pipe including Supply and fixing of Jumbo Ceiling rose and 6A/10A ISI Mark 1way Modular switch with required modular box and cover frame in existing Surface or Concealed pipe wiring including cost and conveyance of all material and all labour charges etc., complete for light, Fan, Exhaust fan and bell points in R.B. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). Makes of switches : Legrand Arteor / Schneider Zen celo / Hywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | POINT | 300
|  | Supply and fixing of 10A 3/2 Pin 2 Module Modular Socket with shutter with 6 / 10A 1 Way 1 Module Modular Switch, 3 Module box with cover frame in Common switch board including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B. Makes of switches : Legrand Arteor / Schneider Zen celo / Hywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | Each | 70
|  | Supply and fixing of 6 / 10A 1 Way 1 Module Modular Switches - 2 Nos and 10A 3/2 Pin 2 Module Modular Socket with shutter - 2 Nos Modular type with cover plate and GI switch box fixing on separate board including all labour charges etc., complete. Makes of switches : Legrand Arteor / Schneider Zen celo / Hywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | Each | 40
|  | Supply and fixing of 16A / 6A 2 Module Combi Socket Modular Socket with shutter with 16A/20A 1 Way 1 Module Modular Switch fixed on suitable size Modular box with required cover frame including with connections, cost and conveyance of all material and all labour charges etc., complete Makes of switches : Legrand Arteor / Schneider Zen celo / Hywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | Each | 300
|  | Supply and fixing of following switches and sockets modular type on suitable size Modular deep box with cover frame including cost and coveyance of all material and all labour charges etc., complete with following configurations 1) 16A / 6A 2 Module Combi Socket Modular Socket with shutter - 1 No 2) 16A/20A 1 Way 1 Module Modular Switch. - 1 No 3) 10A 3/2 Pin 2 Module Modular Socket with shutter - 1 Nos. 4) 6 / 10A 1 Way 1 Module Modular Switch – 1 Nos. including cost and coveyance of all material and all labour charges etc., complete for Computer, LAB and OTs Use Makes of switches : Legrand Arteor / Schneider Zen celo / Hywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | Each | 50
|  | Supply and fixing of following switches and sockets modular type on suitable size Modular deep box with cover frame including cost and coveyance of all material and all labour charges etc., complete with following configurations. 1) 16A / 6A 2 Module Combi Socket Modular Socket with shutter - 2 Nos 2) 16A/20A 1 Way 1 Module Modular Switch. - 2 Nos 3) 10A 3/2 Pin 2 Module Modular Socket with shutter - 2 Nos. 4) 6 / 10A 1 Way 1 Module Modular Switch - 2 Nos. including cost and coveyance of all material and all labour charges etc., complete for LAB,ICU's and OTs Use Makes of switches : Legrand Arteor / Schneider Zen celo / Hywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | Each | 70
RUN of MAINS
|  | Supply and Run of 1 of 1.5 sq.mm (Earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specification for Copper cable. specifications for Copper cable in the existing conduict pipe for earth continuity inlcuding all labour charges etc., complete. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | RM | 1700
|  | Supply and Run of 3 of 2.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable of in existing conduit pipe for individual lighting circuits including labour charges etc., complete as required for switch boards. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | RM | 2600
|  | Supply and Run of 3 of 4.0 sq mm (phase neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable of in existing pipe for power points and AC Sockets inlcuding all labour charges etc., complete. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | RM | 2100
|  | Supply and Run of 3 of 6.0 sq mm (phase neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable of in existing pipe for SPNDB's incoming inlcuding all labour charges etc., complete. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | RM | 600
|  | Supply and Run of 5 of 6.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable in the existing conduict pipe for run of mains from VTPN / Panel Board to TPN DB"s with pin type lugs and connections etc., complete. [for LDBs & 4P MCB's ] Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | RM | 550
|  | Supply and Run of 5 of 10.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable in the existing conduict pipe for run of mains from VTPN / Panel Board to TPN DB"s with pin type lugs and connections etc., complete. [for PDBs] Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | RM | 550
DISTRIBUTION BOARDS
|  | Supply and fixing of 20A SP Plug and Socket with 20A SP MCB with SS enclosure including connections for Flush Mounting etc.,complete for AC's. Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. | Each | 10
|  | Supply and fixing of FP Metal Enclosure with IP 20 Protection DB Make with 1 No 63A, 10 KA DP MCB including internal connection and labour charges for Flush Mounting etc.,complete. Makes of Enclousure : Legrand / Schneider / Siemens / L&T / Crabtree Xpro / ABB / C&S MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. | Each | 10
|  | Supply and fixing of 4 Way (8+12) TPN DB Horizontal with IP 43 Protection as per IS:13032 with 1 No., of 32A FP MCB 10KA, C/D Curve ISI Mark as incomer and 12 Nos 6-32 A 10KA SP MCBs 10KA, C/D Curve ISI Mark as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. (For Lighting DBs) DB Makes : Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro / ABB / C&S MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. | Each | 8
|  | Supply and fixing of 4 Way (8+12) TPN DB Horizontal with IP 43 Protection as per IS:13032 with 1 No., of 63A FP MCB 10KA, C/D Curve ISI Mark as incomer and 12 Nos 6-32 A 10 KA SP MCBs 10KA, C/D Curve ISI Mark as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. (For Power DBs& UPS DB's) DB Makes :Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro / ABB / C&S MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. | Each | 8
|  | Supply and fixing of 8 Way VTPN DB with IP 43 Protection as per IS:13032 with 1 No., of 125A 4P MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted as incomer with 8 Nos of 63A TP MCBs 10KA, C/D Curve ISI Mark as Out goings including internal connections and labour charges for FLUSH Mounting etc., complete. DB Makes :Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. MCCB Makes : L&T- D sine / Schneider-NS NSX / Legrand -DP X3 / Siemens-3V / Hager-h3 / C&S -Winbreak. | Each | 4
|  | Supply and fixing of cable adopteres box with cover for DBs including, massanory work etc., complete., Makes : Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro | Each | 20
|  | Supply and Installation of 63A 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 KA with thermal magnetic release with suitable SS Enclosure and angle iron frame work on wall / floor including all Labours charges massonry work etc complete with connections. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3VL / Hager-h3/C&S -Winbreak. | Each | 2
|  | Supply and Installation of 125 Amps 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release with suitable SS Enclosure and angle iron frame work on wall / floor including all Labours charges massonry work etc complete with connections. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3VL / Hager-h3/C&S -Winbreak. | Each | 4
Earthings
|  | Providing independent earthing for Important equipment with 40mm dia 'B' class 2.5m long G.I pipe and 19mm dia 'B' class G.I pipe of 0.3mtr. long connected with reducer providing G.I funnel with mesh enclosed in C.C/ brick massonry chamber of 450m x 450m x 400mm withR.C.C. Slab cover duly providing staggered holes filling with 20Kg Salt and 40Kg Charcoal or 40Kg bentonite powder from the bottom of the pipe giving earth connection from electrode through G.I strip of 40 x 6mm x 200mm length with all accessories and labour charges complete, as per IS specifications 732/1982 (Part II) | Each | 2
|  | Providing independent earthing by exacavating a pit to a depth of 2.25Mtr in all soils as per size specified in the data for Sophisticated Electronic equipment with 600mm x 600mm x 3.15mm thick copper plate rigidly fixed to 19mm dia 'B' Class G.I Pipe of 2.5Mtr lengthwith funnel as per National Electric Code and earth connection from electrode GI strip of 40mm x 5mm x 200mm length to be bolted with nut bolts to G.I.pipe including 25mm x 3mm copper strip of 6Mtrs length connected from plate to GI strip including filling with 20Kg Salt and 40Kg Charcoal or 40Kg bentonite powder from the bottom of the pipe and providing CC / Brick massonry chamber 450mmX450mmX400mm and covered with R.C.C. Slab including all accessories and labour charges etc complete as per IS specification 732/1982 (Part II). | Each | 4
|  | Supply and Run of 25mm x 6mm G.I Strip including cost of all accessories and labour charges etc., complete. | RM | 120
|  | Supply and Run of 25mm x 3mm copper strip (Cuurrent Carrying Capacity 270A) including cost of all accessories and labour charges etc., complete. | RM | 60
FIXTURES
|  | Supply, transportation and fixing of 22W +/ 10% , >/ 2300 lumens, 1200mm length LED light housing made with alluminium anodised body, wide operating voltage with PF≥0.9, Surge protection: > 2KV, THD<10%, with inbuilt driver and frosted cover CCT: 3000K - 6500K as desired by the department as per IS, minimum CRI≥80 etc., complete with 5 years warranty with BIS Certification with BIS Certification LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Goldmedal.. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. Make & Model will be Approved by the Head Office / Engineer-in-charge. | Each | 20
|  | Supply, transportation and fixing 32-36W (>=3240 Lumens) 2' x2' (600mm x 600mm) slim panel Recessed / Surface LED luminaire Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >90 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% with non integrated driver etc., complete with 2 years warranty with BIS Certification. LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Goldmedal.. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. Make & Model will be Approved by the Head Office / Engineer-in-charge. | Each | 80
|  | Supply, transportation and fixing of 18 W +/-10% (>= 1800 Lumens) LED Down Light Recessed / Surface mounting round / square with housing made of Powder coated Pressure die cast aluminium housing with extended heat sink, with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor > 0.9, Surge protection: > 2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI >80, and THD is less than 15% etc., complete with 5 years warranty with BIS Certification. LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Goldmedal.. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. Make & Model will be Approved by the Head Office / Engineer-in-charge. | Each | 80
|  | Supply, Transportation of energy efficient fan, 1200 mm sweep, aluminium body, consuming 28 W, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) motor, class of insulation: B, 3 no's blades, 30 cm long down rod, 2 no's canopies, shackle'kit, safety rope, copper winding, Power Factor greater than 0.90, Service Value (CMMAV) greater than 8.5, Air delivery minimum 235 CMM, 350 RPM( tolerance as per IS:374-2019), THD less than 10%. with remote or compatible to electronic step type regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise = 75 degree C(max), insulation resistance more than 2 mega ohm, suitable for 230V, 50 HZ, single phase AC supply, earthing etc., including all standard accessories etc., complete. Makes : Atomberg (Efficio ) / Havells / Orient / Halonix | Each | 60
|  | Supply and fixing of Modular type Stepped electronic regulator for sweep AC ceiling fans of 1200mm / 1400mm complete with connections. Makes : Legrand Arteor / Schneider Zen celo / Hywell Blenge Plus / Crabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T Englaze. | Each | 60
|  | Labour charges for Fixing of Ceiling fan including giving connections with twin core wire etc., complete. | Each | 60
|  | Supply and erecting 19/20mm steel tube down rod of meter length with bolts & nuts duly painted with matching colour of fan complete. | Each | 60
|  | Supply,Transportation of 12" (300mm) ISI, 900 RPM Heavy duty exhaust fan with metallic blades wiremesh with all accessories etc complete. Makes : Crompton / Almounard / Havells Turbo Force. | Each | 10
|  | Labour charges for fixing of Exhaust fan in wall with necessary connections and masonary work including material of making hole, finishing etc., complete. | Each | 10
|  | Supply and fixing of GI louver shutter including GI mesh to avoid birds entry with necessary materials suitable for 300mm(12 inches) Exhaust fan. | Each | 10
CABLE TRAYS PERFORATED
|  | Supply and Installation of 150mm x 50mm x 2mm thick GI perforated cable tray with out cover along with required angle supports, with coupler plates, Anchor bolts and nuts etc complete and the tray should be fitted on the wall / Ceiling etc. complete. Makes: DEC/MNR/ H FAB or equivalent | MTR | 50
|  | Supply and Installation of 300mm x 50mm x 2mm thick GI perforated cable tray with out cover along with required angle supports, with coupler plates, Anchor bolts and nuts etc complete and the tray should be fitted on the wall / Ceiling etc. complete. Makes: DEC/MNR/ H FAB or equivalent | MTR | 100
|  | Supply , fabrication and transportation of MS channel iron/ angle iron /flats including two coats of aluminium paint and coat of red oxide paint including all labour charges etc complete. | KG | 150
Lighting Panel
|  | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor Type MV panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Alluminium busbar ( with rating of 0.8A/ Sqmm)supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, flexibiltioy to accept the up four out going cables and necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges. | Each | 1
Incomer: Supply of 160A 4-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 kA with thermal magnetic release Panel Mounted-1 No Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH
Outgoing: Supply of 125 A 3-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 kA with thermal magnetic release Panel Mounted-6 Nos Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH
Supply of 63 A 3-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 kA with thermal magnetic release Panel Mounted-4 Nos Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH
0-415V volt Digital meter of size 96x96mm on exisiting box / panel board including connections etc., complete of CONZERVE / ELMEASURE / MECO / HPL MAKE. - 1 No.
0-100 / 200 / 400 / 600 /1000 - 5A CT Digital Ammeter of size 96x96mm on existing box / panel board including connections etc., complete of CONZERVE / ELMEASURE / MECO / HPL MAKE. - 1 No.
Analog selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete. L&T / C&S / SALZAR / HPL MAKE. - 2 Nos
Analog LED indicator lamps on the existing box / panel board.L&T / C&S / SALZAR / HPL MAKE. - 3 Nos.
32A fuse bases with 2A control fuses. Makes : C&S / GM / Million / Gold Medal-3 Nos
Analog LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete. KAPPA MAKE. - 3 Nos.
Labour charges etc complete with connections for Finished item of work.
Power Panel
|  | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor Type MV panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Alluminium busbar ( with rating of 0.8A/ Sqmm)supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, flexibiltioy to accept the up four out going cables and necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges. | Each | 1
Incomer: Supply of 250A 4-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 36 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH
Outgoings: Supply of 160A 3-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH -4 Nos
Supply of 125 A 3-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH- 4Nos
63A / 60A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 KA with thermal magnetic release Panel Mounted.- 6 Nos. Makes : L&T- D shine / Schneider-NS NSX / Legrand -DP X3 / Siemens-3VL / Hagerh3 / C&S -Winbreak - 6 Nos
0-415V volt Digital meter of size 96x96mm on exisiting box / panel board including connections etc., complete of CONZERVE / ELMEASURE / MECO / HPL MAKE. - 1 No.
0-100 / 200 / 400 / 600 /1000 - 5A CT Digital Ammeter of size 96x96mm on existing box / panel board including connections etc., complete of CONZERVE / ELMEASURE / MECO / HPL MAKE. - 1 No.
Analog selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete. L&T / C&S / SALZAR / HPL MAKE. - 2 Nos
Analog LED indicator lamps on the existing box / panel board.L&T / C&S / SALZAR / HPL MAKE. - 3 Nos.
32A fuse bases with 2A control fuses. Makes : C&S / GM / Million / Gold Medal-3 Nos
Analog LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete. KAPPA MAKE. - 3 Nos.
Labour charges etc complete with connections for Finished item of work.
UG Cable
Supply of the Following XLPE insulated, 1100V grade armoured alluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) Makes : Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / RR kable / Finecab / RPG.
|  | 50 Sqmm 3.5 Core | RM | 125
|  | 70 Sqmm 3.5 Core | RM | 125
LT Cable laying
|  | Earth work excavation of Trench in hard ground soil and Sand filling shall be provided at the bottom of trench before laying the cable and laying of U.G cables from 95 Sqmm up to 400 sqmm covering the cable with bricks and back filling of Trench duly providing route indicator at every 8 Mtrs distance embedded in C.C including cost and conveyance of materials and labour charges etc., complete. | RM | 10
|  | Laying of PVC armoured under ground cable up to 70 Sqmm fixing on chromium plated metallic base saddles on wall / Cable tray as per IS 1255 and as directed by the department including cost and conveyance of all materials and labour charges etc., complete. | RM | 390
LT Cable terminations
Providing Termination for UG cables for following XLPE insulated armoured cable with fixing of heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket, with required lugs etc complete. Makes: SMI / Commet / Dowels.
|  | 50 Sqmm 3.5 Core | Each | 4
|  | 70 Sqmm 3.5 Core | Each | 4

## Lab Equipment
S.No | Description | Units | Qty (2.4 Cr) | Qty (2.5 Cr) | Total | R/Unit as Dept | Amount
1 | High Performance Liquid Chromatography (HPLC) PDA Detector Extra attached to the instrument | No | 2 | 2 | 4 | 6000000 | 24000000
2 | UV-vis Spectrophoto meter | No | 4 | 4 | 8 | 800000 | 6400000
3 | Disintegration Test Apparatus | No | 2 | 2 | 4 | 200000 | 800000
4 | Dissolution apparatus normal with bath | No | 6 | 6 | 12 | 1000000 | 12000000
5 | Water purification system | No | 2 | 2 | 4 | 1500000 | 6000000
6 | Thermostatic water bath | No |  | 3 | 3 | 30000 | 90000
7 | Sonicator | No |  | 3 | 3 | 100000 | 300000
8 | pH meters | No |  | 4 | 4 | 50000 | 200000
9 | Vertical Hot air ovens | No | 2 |  | 2 |  | 0
10 | Refrigerators | No | 3 |  | 3 |  | 0
11 | Racks for keeping glassware | No | 5 |  | 5 |  | 0
12 | Dissolution Auto sampler with bath | No | 5 |  | 5 |  | 0
13 | Glassware washing machine | No | 2 |  | 2 |  | 0
14 | Muffle furnace | No |  |  | 0 |  | 0
15 | Dissolution media Degasser with dispenser | No |  |  | 0 |  | 0
16 | Hot Air oven | No |  |  | 0 |  | 0
17 | Autotitrator with Karlfisher | No |  |  | 0 |  | 0
18 | Centrifuge | No |  |  | 0 |  | 0
19 | Shaker | No |  |  | 0 |  | 0
20 | Mobile Phase Filtration set up | No |  |  | 0 |  | 0
21 | Analytical balance with printer | No |  |  | 0 |  | 0
22 | Rough balance | No |  |  | 0 |  | 0
| UV/VIS Spectrophotometer | No | 4
| HPLC (Gradient) with PDA, dtector, Auto sampler & essential Columns | No | 2
| Water purification system | No | 2
| Thermostatic water bath | No | 3
| Disintegration apparatus | No | 2
| Dissolution apparatus | No | 6
| pH Meter | No | 4
| Sonicator | No | 3
| UV/VIS Spectrophotometer | No | 4
| HPLC (Gradient) with PDA, dtector, Auto sampler & essential Columns | No | 2
| Water purification system | No | 2
| Disintegration apparatus | No | 2
| Dissolution apparatus | No | 6

## Room Wise BOQ
Second Floor Chemistry Lab
Room wise BOQ
S.No | Description | Quantity | Unit
1 | Documentation Room (ROOM - 1)
1.1 | Vertical Storage Cabinet | 1 | Nos
1.2 | Linear Workstation | 8 | Nos
1.3 | Over Head Wall Storage Cabinet | 11 | Nos
1.4 | 2.0 Tr Split AC | 1 | Nos
2 | Hot Zone Room (ROOM - 2)
2.1 | 5' Bench Top Fume Hood | 2 | Nos
2.2 | Standing Height Work Bench | 1 | Nos
2.3 | Oven | 2 | Nos
3 | Dinning Room (ROOM - 3)
3.1 | Dinning Tabale (Wall MOUNTED) | 1 | Nos
3.2 | Chairs | 4 | Nos
3.3 | Sink | 1 | Nos
3.4 | 2.0 Tr Split AC | 1 | Nos
4 | Dissolution Room (ROOM - 4)
4.1 | J Shape Sitting Height Work Bench with Sink Unit | 1 | Nos
4.2 | Lab Chairs | 3 | Nos
4.3 | Spot Extractor | 1 | Nos
5 | Water Purification Room (ROOM - 5)
5.1 | L Shape Standing Height Work Bench with Sink Unit | 1 | Nos
5.2 | 1.5 Tr Split AC | 1 | Nos
6 | Wash Area (ROOM - 6)
6.1 | L Shape Standing Height Work Bench with Sink Unit | 1 | Nos
7 | Wet Analysis Lab - 1 (ROOM - 7)
7.1 | Standing Height Work Bench with Sink Unit | 1 | Nos
7.2 | Standing Height Island Work Bench | 1 | Nos
7.3 | Standing Height Anti-Vibration Table | 2 | Nos
7.4 | Lab Chairs | 3 | Nos
7.5 | Vertical Storage Cabinet | 2 | Nos
7.6 | Spot Extractor | 5 | Nos
7.7 | Ductable Split Unit (8.5 / 11 Tr) | 1 | Nos
8 | Balance Room (ROOM - 8)
8.1 | Standing Height Anti-Vibration Table | 6 | Nos
8.2 | Lab Chairs | 2 | Nos
8.3 | 2.0 Tr Split AC | 1 | Nos
9 | Instrumentation Room (ROOM - 9)
9.1 | C Shape Sitting Height Work Bench | 1 | Nos
9.2 | Lab Chairs | 8 | Nos
9.3 | Ductable Split Unit (5.0 /8.5 Tr) | 1 | Nos
10 | Officer Room - 1 (ROOM - 10)
10.1 | Workstation Size: 1500×600/Side; 900×450 Combo storage | 1 | Nos
10.2 | Manger Chair | 1 | Nos
10.3 | Task chairs | 2 | Nos
10.4 | Vertical Storage Cabinet | 2 | Nos
10.5 | 1.5 / 2.0 Tr Split AC | 1 | Nos
11 | Officer Room - 2 (ROOM - 11)
11.1 | Workstation Size: 1500×600/Side; 900×450 Combo storage | 1 | Nos
11.2 | Manger Chair | 1 | Nos
11.3 | Task chairs | 2 | Nos
11.4 | Vertical Storage Cabinet | 2 | Nos
11.5 | 1.5 / 2.0 Tr Split AC | 1 | Nos
12 | Reference Standard Room - 2 (ROOM - 12)
12.1 | Refrigerartor | 2 | Nos
13 | Instrumentation Room - 2 (ROOM - 13)
13.1 | C Shape Sitting Height Work Bench | 1 | Nos
13.2 | Lab Chairs | 9 | Nos
13.3 | Ductable Split Unit (8.5 / 11 Tr) | 1 | Nos
14 | Balance Room - 2 (ROOM - 14)
14.1 | Standing Height Anti-Vibration Table | 5 | Nos
14.2 | Lab Chairs | 2 | Nos
14.3 | 2.0 Tr Split AC | 1 | Nos
15 | Wet Analysis Lab - 2 (ROOM - 15)
15.1 | Standing Height Work Bench with Sink Unit | 1 | Nos
15.2 | Standing Height Island Work Bench | 1 | Nos
15.3 | Standing Height Anti-Vibration Table | 3 | Nos
15.4 | Lab Chairs | 6 | Nos
15.5 | Vertical Storage Cabinet | 2 | Nos
15.6 | Spot Extractor | 6 | Nos
15.7 | Ductable Split Unit (8.5 / 11 Tr) | 1 | Nos
16 | Dissolution Room - 2 (ROOM - 16)
16.1 | J Shape Sitting Height Work Bench with Sink Unit | 1 | Nos
16.2 | Lab Chairs | 2 | Nos
16.3 | Standing Height Anti-Vibration Table | 1 | Nos
17 | Water Purification Room (ROOM - 17)
17.1 | L Shape Standing Height Work Bench with Sink Unit | 1 | Nos
17.2 | 1.5 Tr Split AC | 1 | Nos
18 | Wash Area (ROOM - 18)
18.1 | L Shape Standing Height Work Bench with Sink Unit | 1 | Nos
19 | Documentation Room - 2 (ROOM - 19 )
19.1 | Vertical Storage Cabinet | 1 | Nos
19.2 | Linear Workstation | 8 | Nos
19.3 | Over Head Wall Storage Cabinet | 11 | Nos
19.4 | 2.0 Tr Split AC | 1 | Nos
20 | Gents Toilet
20.1 | All Plumbing Items, Sanitry fittings complete as specifed in the Technical Specifications | 1 | Job
21 | Ladies Toilet
21.2 | All Plumbing Items, Sanitry fittings complete as specifed in the Technical Specifications | 1 | Job

## Room Wise ELE
Room wise BOQ
S.No | Description | Quantity | Unit
1 | Documentation Room (ROOM - 1)
Lights
Fans
Sockets
Others
2 | Hot Zone Room (ROOM - 2)
Lights
Fans
Sockets
Others
3 | Dinning Room (ROOM - 3)
Lights
Fans
Sockets
Others
4 | Dissolution Room (ROOM - 4)
Lights
Fans
Sockets
Others
5 | Water Purification Room (ROOM - 5)
Lights
Fans
Sockets
Others
6 | Wash Area (ROOM - 6)
Lights
Fans
Sockets
Others
7 | Wet Analysis Lab - 1 (ROOM - 7)
Lights
Fans
Sockets
Others
8 | Balance Room (ROOM - 8)
Lights
Fans
Sockets
Others
9 | Instrumentation Room (ROOM - 9)
Lights
Fans
Sockets
Others
10 | Officer Room - 1 (ROOM - 10)
Lights
Fans
Sockets
Others
11 | Officer Room - 2 (ROOM - 11)
Lights
Fans
Sockets
Others
12 | Reference Standard Room - 2 (ROOM - 12)
Lights
Fans
Sockets
Others
13 | Instrumentation Room - 2 (ROOM - 13)
Lights
Fans
Sockets
Others
14 | Balance Room - 2 (ROOM - 14)
Lights
Fans
Sockets
Others
15 | Wet Analysis Lab - 2 (ROOM - 15)
Lights
Fans
Sockets
Others
16 | Dissolution Room - 2 (ROOM - 16)
Lights
Fans
Sockets
Others
17 | Water Purification Room (ROOM - 17)
Lights
Fans
Sockets
Others
18 | Wash Area (ROOM - 18)
Lights
Fans
Sockets
Others
19 | Documentation Room - 2 (ROOM - 19 )
Lights
Fans
Sockets
Others
20 | Gents Toilet
Lights
Fans
Sockets
Others
21 | Ladies Toilet
Lights
Fans
Sockets
Others

## Equipment
S.No | Name of Instruments | No.of Instrument Required | Approx.Cost(in Rs.) | Total Cost (in Rs.)
1 | UV/VIS Spectrophotometer | 4 | 800000 | 3200000
2 | HPLC (Gradient) with PDA, dtector, Auto sampler & essential Columns | 2 | 6000000 | 12000000
3 | Water purification system | 2 | 1500000 | 3000000
4 | Thermostatic water bath | 3 | 30000 | 90000
5 | Disintegration apparatus | 2 | 200000 | 400000
6 | Dissolution apparatus | 6 | 1000000 | 6000000
7 | pH Meter | 4 | 50000 | 200000
8 | Sonicator | 3 | 100000 | 300000
1 | UV/VIS Spectrophotometer | 4 | 800000 | 3200000
2 | HPLC (Gradient) with PDA, dtector, Auto sampler & essential Columns | 2 | 6000000 | 12000000
3 | Water purification system | 2 | 1500000 | 3000000
4 | Disintegration apparatus | 2 | 200000 | 400000
5 | Dissolution apparatus | 6 | 1000000 | 6000000

## Lift
S.No | Item Code | Description | Units | Qty | R/Unit
Passenger Lift (8 Person)
|  | Supplying, installation, commissioning, testing, putting into operation and handing over of 8 Persons Passenger Lift (544 Kgs) with following specifications. The contractor shall produce after sales service support for 2 years during warranty period from the supplier and obtain approval from the engineer-in-charge for making any payment for this. Make : Kone / OTIS / Johnson / Schindler / MITSUBISHI. Make & Model will be Approved by the Engineer-in-charge. Scope of work: Engineering Fabrication, Manufacturing, Inspection and testing, packing forwarding, transportation to site, unloading at site, transportation, Erection and Commis-sioning, trial run and carrying our Performance / Acceptance Tests at site and Handing over of complete El-evator. Erection and Commissioning Spares is part of your scope and the same will be taken back after the commissioning is over. | Job | 1
I) No. of elevators - 1
ii) Type & Capacity : 8 Passenger lift (544 Kgs) with Gearless with Machine Room.
iii ) Speed Approximately : 1.00m/sec
iv) Type of Drive: MICRO PROCESSOR BASED VVVF
v) Location of Machine Room: Above Lift well
vi) Travel : G+2.
vii) Serving: 3 Stops , 3 Levels and 3 Openings
viii) Well Size approximately: 1840 mm wide x 2080 mm deep
ix) Power Supply : 415 V, 3 phase 50 Hz, AC
x) Auxiliary required: Single Phase 220 V, 50 Hz Ac
xi) Car size (clear inside) approx.: 1200 mm wide x 1200 mm
deep x 2100 height.
xii) Car Enclosure: Stainless steel Hairline AISI441
Handrail:Round Bend Handrail Painted Traffic Black at Rear Wall
a) Flooring - 3 mm Pattern (PVC) Dark grey with flecks
Car skirting material: Stainless steel Hairline AISI441
b) Car Illumination : Integrated roof MS40 Stainless Steel Mini
spot LED light
xiii) Electric Light/Fan: LED / 400 mm
xiv) No. of Entrances: 3 at front side.
xv) Car Entrance: Stainless Steel Hairline Finish center opening sliding power operated door.
xvi) Landing Entrance: Stainless Steel Hairline Finish center opening power door.
xvii) Door size : 800 mm wide x 2000 mm internal height
xviii) Control: Micro Processor based simplex full collective control with or without attendant operation.
xix) Indicators: Car & Landings: Dot matrix digital type direction and Position Indicaters with Stainless steel face plates.
xx) Other Feature Included:
1.Correction drive to next level
2.Emergency Alarm @ Main Floor
3.Car Call backwards
4.Overload function, constant indication/Buzzer
5.Bypass load Function
6.Auto Cut off Fan and Light
7.Manual Rescue Operation
8.Centralized Hoisting for lesser vibration and smooth travel
9.Pit Ladder
10.Micro movement Led Based Buttons
11.L.W.D. (Load Weighing Device)
12.Direction & Position Indicator In Car & Landing
13.Advanced Car Position Indication
14.Automatic Brake Test function every 11hours
15.Every run brake supervision
16.Phase reversal functioning
17.Signal Fixtures
18.+10% to –10% Voltage Fluctuation Withstanding Capacity
19.Door Close Button
20.Door Open Button
21.Car Emergency Light
22.Fireman Drive
23.Curtain of Light 169 Beams
24.Accurate Relevelling, Automatic, Closed Door
25.E, With emerg.opening device
26.Emergency Rescue Device with audio announcer
27. 2 Way Dedicated Intercom
28.Nudging service
29.Attendant Service
30.Mini spot LED light
31.B, 2 Hours Fire rated
Additional Features:
1.Minor Builders Work
2.Landing Push Button In Landing Door Frames
3.Floor Annunciator With Music
4.Vandal Proof S.S. Button With S.S. Cover
5.Push Button - Orange L E D Illumination
6.Call Register Signal And Vf Door Operator
7.Full Car Operating Panel
8.Dot Matrix Led D & P Indicators In Car & Landings -Orange Colour
9.False Ceiling In Car
10.Free Service For two Years
11.Infra Red Door Screen
12.Provision For Music
13.Scaffolding
14.SS Handrail

## Estimate -Civ
Establishment of Vascula Access Centers to cater the needs of dialysis patients at Osmania General Hospital, Hyderabad.(Civil, Electrical and AC works)
Civil Works
Sl. no | Description of work | Measurements | [5 empty] | Rate |  | Amount
|  | No. |  | L (M) | B (M) | D (M) | QTY | per | RS
1 | Dismantling clearing away and carefully stacking useful materials for re use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges etc complete for Brick masonry
| SSO Room long wall | 1 | 1 | 4.4 | 3.2 | 0.23 | 3.24
| Coding room short wall | 1 | 1 | 4.4 | 3.2 | 0.23 | 3.24
| Room long wall | 1 | 1 | 5.8 | 3.2 | 0.23 | 4.27
| Room short wall | 1 | 1 | 3.05 | 3.4 | 0.15 | 1.56
| door opening | 1 | 1 | 1 | 2.1 | 0.23 | 0.48
| Toilets long wall | 1 | 1 | 6.16 | 3.4 | 0.15 | 3.14
| Toilet short wall | 1 | 2 | 1.8 | 3.1 | 0.15 | 1.67
| door opening | 1 | 2 | 1 | 2.1 | 0.23 | 0.97
| Emergency exit opening | 1 | 2 | 1.8 | 2.1 | 0.23 | 1.74
| Toilets door openings | 1 | 2 | 1 | 2.1 | 0.23 | 0.97
| Documentation Room short wall | 1 | 1 | 6.16 | 3.4 | 0.15 | 3.14
| door opening | 1 | 3 | 1 | 2.1 | 0.23 | 1.45
| door opening | 1 | 1 | 1 | 2.1 | 0.23 | 0.48
| Brick wall support for RCC platform (Granite) | 1 | 70 | 0.75 | 0.85 | 0.15 | 6.69
[7 empty] | 33.04 | cum | 312 | 10308
2 | Dismantling clearing away and carefully stacking useful materials for re use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges etc complete for Flooring
| SSO Room | 1 | 1 | 4.4 | 3.31 |  | 14.56
| Coding Room | 1 | 1 | 4.4 | 7.82 |  | 34.41
| Lab room | 1 | 1 | 1.27 | 1.5 |  | 1.91
| Room | 1 | 1 | 2.4 | 4.19 |  | 10.06
| Sterility testing | 1 | 1 | 4.38 | 4.19 |  | 18.35
| Room | 1 | 1 | 4.19 | 1.77 |  | 7.42
| Passage 1 | 1 | 1 | 7.46 | 1.5 |  | 11.19
| Passage 2 | 1 | 1 | 5.8 | 1 |  | 5.8
| Room | 1 | 1 | 3.05 | 1.8 |  | 5.49
| Room | 1 | 1 | 3.05 | 3.89 |  | 11.86
| Chemical Lab | 1 | 1 | 5.46 | 5.8 |  | 31.67
| Room | 1 | 1 | 3 | 5.8 |  | 17.4
| Ladies Toilet | 1 | 1 | 6.16 | 1.8 |  | 11.09
| Gents Toilet | 1 | 1 | 6.16 | 1.8 |  | 11.09
| Room | 1 | 1 | 6.16 | 5.6 |  | 34.5
| Documentation Room | 1 | 1 | 6.16 | 7.52 |  | 46.32
| Room | 1 | 1 | 6.16 | 2.85 |  | 17.56
| Room | 1 | 1 | 3.05 | 3.19 |  | 9.73
| Room | 1 | 1 | 3.05 | 2.46 |  | 7.5
| Wet Analysis lab | 1 | 1 | 7.26 | 5.75 |  | 41.75
| Instrumenttion room | 1 | 1 | 9.85 | 5.75 |  | 56.64
| Office Room | 1 | 1 | 4.4 | 3.12 |  | 13.73
| Office Room | 1 | 1 | 4.4 | 3.05 |  | 13.42
| Corridor | 1 | 2 | 18.58 | 1.8 |  | 66.89
| Corridor | 1 | 1 | 11 | 1.8 |  | 19.8
| Corridor | 1 | 1 | 17.42 | 1.8 |  | 31.36
[7 empty] | 551.5 | Sqm | 17 | 9376
3 | Dismantling clearing away and carefully stacking useful materials for re use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges complete Reinforced cement concrete
| Room | 1 | 1 | 2.7 | 0.9 | 0.15 | 0.36
| Chemical Lab | 1 | 1 | 3 | 0.9 | 0.15 | 0.41
|  | 1 | 1 | 2.4 | 0.9 | 0.15 | 0.32
|  | 1 | 1 | 6.16 | 1 | 0.15 | 0.92
|  | 1 | 1 | 4.25 | 0.85 | 0.15 | 0.54
| Room beside Wet Analysis lab | 1 | 1 | 3.04 | 0.8 | 0.15 | 0.36
|  | 1 | 1 | 2.04 | 0.8 | 0.15 | 0.24
| Wet Analysis lab | 1 | 1 | 3.04 | 0.75 | 0.15 | 0.34
|  | 1 | 1 | 2.8 | 0.85 | 0.15 | 0.36
|  | 1 | 1 | 1.05 | 0.85 | 0.15 | 0.13
|  | 1 | 1 | 6.56 | 1 | 0.15 | 0.98
|  | 1 | 1 | 3.53 | 0.85 | 0.15 | 0.45
|  | 1 | 1 | 2.87 | 0.85 | 0.15 | 0.37
| Instrumenttion room | 1 | 1 | 2.72 | 0.85 | 0.15 | 0.35
|  | 1 | 1 | 4.28 | 0.85 | 0.15 | 0.55
|  | 1 | 1 | 9.1 | 0.85 | 0.15 | 1.16
|  | 1 | 1 | 1.41 | 0.85 | 0.15 | 0.18
|  | 1 | 1 | 4.66 | 0.85 | 0.15 | 0.59
[7 empty] | 8.61 | cum
4 | Dismantling clearing away and carefully stacking useful materials for re use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges complete Unreinforced cement concrete up to 15cm thickness
5 | Dismantling clearing away and carefully stacking useful materials for re use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges etc complete for False Ceiling
| SSO Room | 1 | 1 | 4.4 | 3.31 |  | 14.56
| Coding Room | 1 | 1 | 4.4 | 7.82 |  | 34.41
| Passage 1 | 1 | 1 | 7.46 | 1.5 |  | 11.19
| Passage 2 | 1 | 1 | 5.8 | 1 |  | 5.8
| Room | 1 | 1 | 3.05 | 1.8 |  | 5.49
| Room | 1 | 1 | 3.05 | 3.89 |  | 11.86
| Chemical Lab | 1 | 1 | 5.46 | 5.8 |  | 31.67
| Room | 1 | 1 | 3 | 5.8 |  | 17.4
| Ladies Toilet | 1 | 1 | 6.16 | 1.8 |  | 11.09
| Gents Toilet | 1 | 1 | 6.16 | 1.8 |  | 11.09
| Room | 1 | 1 | 6.16 | 5.6 |  | 34.5
| Documentation Room | 1 | 1 | 6.16 | 7.52 |  | 46.32
| Room | 1 | 1 | 6.16 | 2.85 |  | 17.56
| Room | 1 | 1 | 3.05 | 3.19 |  | 9.73
| Room | 1 | 1 | 3.05 | 2.46 |  | 7.5
| Wet Anayslis lab | 1 | 1 | 7.26 | 5.75 |  | 41.75
| Instrumenttion room | 1 | 1 | 9.85 | 5.75 |  | 56.64
| Office Room | 1 | 1 | 4.4 | 3.12 |  | 13.73
| Toilet | 1 | 1 | 1.5 | 1.45 |  | 2.18
| Toilet | 1 | 1 | 1.5 | 1.45 |  | 2.18
| Office Room | 1 | 1 | 4.4 | 3.05 |  | 13.42
[7 empty] | 400.07 | Sqm
6 | Dismantling doors windows and clear storey windows Ventilators etc wood or steel shutters including Chowkhats architraves hold fasts and other attachments etc and stacking them within 100m lead including labour charge etc complete for finished item of work. Not exceeding 3 sqm in area.
| SSO Room | 1 | 2 |  |  |  | 2
| Coding Room | 1 | 5 |  |  |  | 5
| Microbiology lab | 1 | 17 |  |  |  | 17
| Chemical Lab | 1 | 4 |  |  |  | 4
| Corner room | 1 | 1 |  |  |  | 1
| Toilet | 1 | 4 |  |  |  | 4
| Room beside toilets | 1 | 2 |  |  |  | 2
| Documentation Room | 1 | 5 |  |  |  | 5
| Wet Analysis room | 1 | 2 |  |  |  | 2
| Wet analysis lab | 1 | 7 |  |  |  | 7
| Instrumenttion room | 1 | 4 |  |  |  | 4
| Officer Room | 1 | 3 |  |  |  | 3
| Officer Room | 1 | 3 |  |  |  | 3
[7 empty] | 59 | Nos | 274 | 16166
7 | Dismantling doors windows and clear storey windows Ventilators etc wood or steel shutters including Chowkhats architraves hold fasts and other attachments etc and stacking them within 100m lead including labour charge etc complete for finished item of work. Exceeding 3 sqm in area.
| Microbiology lab | 1 | 1 |  |  |  | 1
| Instrumenttion room | 1 | 1 |  |  |  | 1
[7 empty] | 2 | Nos | 368 | 736
8 | Dismantling doors windows and clear storey windows Ventilators etc wood or steel shutters including Chowkhats architraves hold fasts and other attachments etc and stacking them within 100m lead including labour charge etc complete for finished item of work. Not exceeding 3 sqm in area.
| Chemical Lab | 1 | 4 | 0.5 | 0.5 |  | 1
| wet analysis lab | 1 | 4 | 0.5 | 0.5 |  | 1
| Instrumenttion room | 1 | 4 | 0.5 | 0.5 |  | 1
[7 empty] | 3 | Sqm
9 | wall cladding removal
| Microbiology lab | 1 | 1 | 2.87 | 1.2 |  | 3.44
|  | 1 | 1 | 3.89 | 1.2 |  | 4.67
| Chemical Lab | 1 | 1 | 22.53 | 1.2 |  | 27.04
|  | 1 | 1 | 1.8 | 1.2 |  | 2.16
| Ladies Toilet | 1 | 1 | 6.37 | 2.1 |  | 13.38
| Gents Toilet | 1 | 1 | 6.37 | 2.1 |  | 13.38
|  | 1 | 1 | 3.74 | 2.1 |  | 7.85
| Wet analysis room | 1 | 1 | 14.5 | 1.2 |  | 17.4
| Wet analysis lab | 1 | 1 | 3.04 | 1.2 |  | 3.65
|  | 1 | 1 | 8.28 | 1.2 |  | 9.94
|  | 1 | 1 | 28.93 | 1.2 |  | 34.72
| Instrumenttion room | 1 | 1 | 31.24 | 1.2 |  | 37.49
| Toilet | 1 | 1 | 5.85 | 2.1 |  | 12.29
| Toilet | 1 | 1 | 5.85 | 2.1 |  | 12.29
| wash area | 1 | 1 | 2.72 | 2.1 |  | 5.71
| wash area | 1 | 1 | 2.72 | 2.1 |  | 5.71
[7 empty] | 211.12 | Sqm
10 | Masonry work 100 mm thick in CM (1:4) prop (cement: Screened sand) in super structure with Aerated (Cellular) Autoclaved Concrete Blocks conforming to IS:2185 (Part-3) - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600x 200 x 100 mm from approved source having minimum crushing strength of 3 N/Sq.m including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, including sales & other taxes on all materials, all operational, incidental and labour charges such as mixing cement mortar, constructing masonry, scaffolding charges, lift charges, curing, etc., complete but excluding seigniorage charges for finished item of work. (APSS No. 501 & 504). Brick work
| Balance room short wall | 1 | 1 | 3.04 | 3.4 |  | 10.34
| Wet analysis lab short wall | 1 | 1 | 5.8 | 3.4 |  | 19.72
| door deduction | -1 | 1 | 1 | 2.1 |  | -2.1
| Water purification room short wall | 1 | 1 | 2.6 | 3.4 |  | 8.84
| Toilet partition wall | 1 | 1 | 3.42 | 3.4 |  | 11.63
| Hot zone room short wall | 1 | 1 | 3 | 3.4 |  | 10.2
| Hot zone room long wall | 1 | 1 | 6.16 | 3.4 |  | 20.94
[7 empty] | 79.57 | Sqm | 1107 | 88084
11 | Masonry work in CM (1:6) prop (cement: Screened sand) in super structure with Aerated (Cellular) Autoclaved Concrete Blocks conforming to IS:2185 (Part-3) - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600x 230 x 200 mm from approved source having minimum crushing strength of 3 N/Sq.m including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, including sales & other taxes on all materials, all operational, incidental and labour charges such as mixing cement mortar, constructing masonry, scaffolding charges, lift charges, curing, etc., complete but excluding seigniorage charges for finished item of work. (APSS No. 501 & 504).
| wet analysis lab door closing | 1 | 1 | 1 | 2.1 | 0.23 | 0.48
| wash area door closing | 1 | 1 | 1 | 2.1 | 0.23 | 0.48
| dissolution room long wall | 1 | 1 | 5.8 | 3.4 | 0.23 | 4.54
| door deduction | -1 | 1 | 1.05 | 2.1 | 0.23 | -0.51
| door deduction | -1 | 1 | 1.05 | 2.1 | 0.23 | -0.51
| Ladies Toilet door closing | 1 | 1 | 1 | 2.1 | 0.23 | 0.48
| Gents Toilet door closing | 1 | 1 | 1 | 2.1 | 0.23 | 0.48
| Documentation Room long wall | 1 | 2 | 6.16 | 3.4 | 0.23 | 9.63
| door closing | 1 | 1 | 1 | 2.1 | 0.23 | 0.48
| Balance room long wall | 1 | 1 | 5.75 | 3.4 | 0.23 | 4.5
| door deduction | -1 | 1 | 1 | 2.1 | 0.23 | -0.48
| Reference room window | 1 | 1 | 1.2 | 0.5 | 0.23 | 0.14
| Instrumenttion room 1&2 window | 1 | 2 | 0.9 | 0.5 | 0.23 | 0.21
|  | 1 | 5 | 1.2 | 0.5 | 0.23 | 0.69
|  | 1 | 1 | 2.4 | 0.5 | 0.23 | 0.28
| Balance room window | 1 | 2 | 1.2 | 0.5 | 0.23 | 0.28
| dissolution room 2 window | 1 | 1 | 1.5 | 0.5 | 0.23 | 0.17
| Water purification room 2 window | 1 | 1 | 0.9 | 0.5 | 0.23 | 0.1
|  | 1 | 2 | 1.5 | 0.5 | 0.23 | 0.35
|  | 1 | 1 | 1.8 | 0.5 | 0.23 | 0.21
| wash area 2 window | 1 | 1 | 1.2 | 0.5 | 0.23 | 0.14
| documentation room window | 1 | 2 | 1.2 | 0.5 | 0.23 | 0.28
|  | 1 | 2 | 1.8 | 0.5 | 0.23 | 0.41
| documentation room-2 window | 1 | 2 | 1.2 | 0.5 | 0.23 | 0.28
|  | 1 | 1 | 1.8 | 0.5 | 0.23 | 0.21
|  | 1 | 1 | 2.4 | 0.5 | 0.23 | 0.28
| Balance room 2 window | 1 | 1 | 1.2 | 0.5 | 0.23 | 0.14
[7 empty] | 23.74 | cum | 9444 | 224201
12 | Supply and placing of the Design Mix Concrete M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Concrete Batching Plant with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials, centering using Casurina Ballies, Bamboos, Wooden Reapers, Runners, Wood Posts, Steel Plates etc., including all operational, incidental and labour charges such as weigh batching, machine mixing, lifting of concrete manually, laying concrete, curing, overheads & contractors profit etc., complete but excluding cost of steel and its fabrication charges for finished item of work (APSS No. 402). For Lintels
| Balance room 1 | 1 | 1 | 1.35 | 0.15 | 0.15 | 0.03
| Wet analysis laab | 1 | 1 | 1.35 | 0.23 | 0.15 | 0.05
| dissolution room | 1 | 1 | 1.35 | 0.23 | 0.15 | 0.05
| Water purification room | 1 | 1 | 1.35 | 0.23 | 0.15 | 0.05
| Wash area | 1 | 1 | 1.35 | 0.23 | 0.15 | 0.05
| Gents Toilet | 1 | 1 | 1.3 | 0.23 | 0.15 | 0.04
| Ladies Toilet | 1 | 1 | 1.3 | 0.23 | 0.15 | 0.04
| Hot zone room | 1 | 1 | 1.3 | 0.23 | 0.15 | 0.04
| staff dining room | 1 | 1 | 1.3 | 0.23 | 0.15 | 0.04
| Wet analysis lab 2 | 1 | 2 | 1.3 | 0.23 | 0.15 | 0.09
| Balance room 2 | 1 | 1 | 1.3 | 0.23 | 0.15 | 0.04
[7 empty] | 0.52 | cum | 14878 | 7737
13 | Plastering 12mm thick in two coats using screened sand with base coat of 8mm thick in CM (1:6) and top coat of 4mm thick in CM (1:4) with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales & other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and overheads & contractors profit complete for finished item of work. (SS 901,903 & 904).
| Balance room short wall | 1 | 2 | 3.04 | 3.4 |  | 20.67
| Wet analysis lab short wall | 1 | 2 | 5.8 | 3.4 |  | 39.44
| door deduction | -1 | 2 | 1 | 2.1 |  | -4.2
| Water purification room short wall | 1 | 2 | 2.6 | 3.4 |  | 17.68
| Toilet partition wall | 1 | 2 | 3.42 | 3.4 |  | 23.26
| Hot zone room short wall | 1 | 2 | 3 | 3.4 |  | 20.4
| Hot zone room long wall | 1 | 2 | 6.16 | 3.4 |  | 41.89
| wet analysis lab door closing | 1 | 2 | 1 | 2.1 |  | 4.2
| wash area door closing | 1 | 2 | 1 | 2.1 |  | 4.2
| dissolution room long wall | 1 | 2 | 5.8 | 3.4 |  | 39.44
| door deduction | -1 | 2 | 1.05 | 2.1 |  | -4.41
| door deduction | -1 | 2 | 1.05 | 2.1 |  | -4.41
| Ladies Toilet door closing | 1 | 2 | 1 | 2.1 |  | 4.2
| Gents Toilet door closing | 1 | 2 | 1 | 2.1 |  | 4.2
| Documentation Room long wall | 1 | 2 | 6.16 | 3.4 |  | 41.89
| door closing | 1 | 2 | 1 | 2.1 |  | 4.2
| Balance room long wall | 1 | 2 | 5.75 | 3.4 |  | 39.1
| door deduction | -1 | 2 | 1 | 2.1 |  | -4.2
| Reference room window | 1 | 1 | 1.2 | 0.5 |  | 0.6
| Instrumenttion room 1&2 window | 1 | 2 | 0.9 | 0.5 |  | 0.9
|  | 1 | 5 | 1.2 | 0.5 |  | 3
|  | 1 | 2 | 2.4 | 0.5 |  | 2.4
| Balance room window | 1 | 2 | 1.2 | 0.5 |  | 1.2
| dissolution room 2 window | 1 | 1 | 1.5 | 0.5 |  | 0.75
| Water purification room 2 window | 1 | 2 | 0.9 | 0.5 |  | 0.9
|  | 1 | 2 | 1.5 | 0.5 |  | 1.5
|  | 1 | 1 | 1.8 | 0.5 |  | 0.9
| wash area 2 window | 1 | 1 | 1.2 | 0.5 |  | 0.6
| documentation room window | 1 | 2 | 1.2 | 0.5 |  | 1.2
|  | 1 | 2 | 1.8 | 0.5 |  | 1.8
| documentation room-2 window | 1 | 2 | 1.2 | 0.5 |  | 1.2
|  | 1 | 1 | 1.8 | 0.5 |  | 0.9
|  | 1 | 2 | 2.4 | 0.5 |  | 2.4
| Balance room 2 window | 1 | 1 | 1.2 | 0.5 |  | 0.6
| window jam and door jam | [5 empty] | 100
[7 empty] | 408.4 | Sqm | 656 | 267910
14 | Plastering 20mm thick in two coats using screened sand with base coat of 16mm thick in CM(1:6) and top coat of 4mm thick in CM(1:4) with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales & other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and overheads & contractors profit complete for finished item of work .(SS 901,903 & 904).
| Reference room window | 1 | 1 | 1.2 | 0.5 |  | 0.6
| Instrumenttion room 1&2 window | 1 | 2 | 0.9 | 0.5 |  | 0.9
|  | 1 | 5 | 1.2 | 0.5 |  | 3
|  | 1 | 2 | 2.4 | 0.5 |  | 2.4
| Balance room window | 1 | 2 | 1.2 | 0.5 |  | 1.2
| dissolution room 2 window | 1 | 1 | 1.5 | 0.5 |  | 0.75
| Water purification room 2 window | 1 | 2 | 0.9 | 0.5 |  | 0.9
|  | 1 | 2 | 1.5 | 0.5 |  | 1.5
|  | 1 | 1 | 1.8 | 0.5 |  | 0.9
| wash area 2 window | 1 | 1 | 1.2 | 0.5 |  | 0.6
| documentation room window | 1 | 2 | 1.2 | 0.5 |  | 1.2
|  | 1 | 2 | 1.8 | 0.5 |  | 1.8
| documentation room-2 window | 1 | 2 | 1.2 | 0.5 |  | 1.2
|  | 1 | 1 | 1.8 | 0.5 |  | 0.9
|  | 1 | 2 | 2.4 | 0.5 |  | 2.4
| Balance room 2 window | 1 | 1 | 1.2 | 0.5 |  | 0.6
[7 empty] | 20.85 | Sqm | 682 | 14220
15 | Flooring with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM (1:8) prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab , including neat cement slurry of honey like consistancy spread @ 3.3 kgs per Sqm. and jointed neately with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site (excluding cost of C.C. bed) including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in-charge etc.,and overheads & contractors profit complete for finished item of work. (APSS No.701 & 707).
| Reference Standard Room | 1 | 1 | 4.4 | 2.7 |  | 11.88
| Instrumentation Room-1 | 1 | 1 | 4.4 | 11.3 |  | 49.72
| Balance Room-1 | 1 | 1 | 3.04 | 3.24 |  | 9.85
| Wet Analysis Lab-1 | 1 | 1 | 10.61 | 5.8 |  | 61.54
| Dissolution Room-1 | 1 | 1 | 2.64 | 5.8 |  | 15.31
| Water Purification Room-1 | 1 | 1 | 2.59 | 3.18 |  | 8.24
| Wash Area-1 | 1 | 1 | 2.59 | 3.18 |  | 8.24
| Doccumentation Room-1 | 1 | 1 | 3 | 5.8 |  | 17.4
| Doccumentation Room-2 | 1 | 1 | 6.16 | 3.44 |  | 21.19
| Hot Zone Room | 1 | 1 | 6.16 | 4.95 |  | 30.49
| Staff Dining Room | 1 | 1 | 6.16 | 2.42 |  | 14.91
| Dissolution Room-2 | 1 | 1 | 6.16 | 2.78 |  | 17.12
| Wet Analysis Lab-2 | 1 | 1 | 8.71 | 5.75 |  | 50.08
| Water Purification Room-2 | 1 | 1 | 3 | 3.19 |  | 9.57
| Wash Area-2 | 1 | 1 | 3 | 2.46 |  | 7.38
| Balance Room-2 | 1 | 1 | 2.83 | 5.75 |  | 16.27
| Instrumentation Room-2 | 1 | 1 | 6.79 | 5.75 |  | 39.04
| Officer Room-1 | 1 | 1 | 4.4 | 3.12 |  | 13.73
| Officer Room-2 | 1 | 1 | 4.4 | 3 |  | 13.2
| Corridor-1 (Officer Rooms) | 1 | 1 | 18.58 | 1.8 |  | 33.44
| Corridor-2 (Wet Analysis Lab-1) | 1 | 1 | 17.42 | 1.8 |  | 31.36
| Corridor-3 (Hot Zone Room) | 1 | 1 | 18.58 | 1.8 |  | 33.44
| Corridor-4 (Wet Analysis Lab-2) | 1 | 1 | 11 | 1.8 |  | 19.8
[7 empty] | 533.2 | Sqm | 1317 | 702224
16 | Providing skirting to internal walls to 10 cm height with soluble salt porcelain vitrified tiles screen printed and polished of thickness between 8 to 10mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630(Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707)
| Reference Standard Room | 1 | 2 | 4.4 |  |  | 8.8
|  | 1 | 2 | 2.7 |  |  | 5.4
| door deduction | -1 | 1 | 1.05 |  |  | -1.05
| Instrumentation Room-1 | 1 | 2 | 4.4 |  |  | 8.8
|  | 1 | 2 | 11.3 |  |  | 22.6
| door deduction | -1 | 1 | 1.05 |  |  | -1.05
| Balance Room-1 | 1 | 2 | 3.04 |  |  | 6.08
|  | 1 | 2 | 3.24 |  |  | 6.48
| door deduction | -1 | 1 | 1 |  |  | -1
| Wet Analysis Lab-1 | 1 | 2 | 10.61 |  |  | 21.22
|  | 1 | 2 | 5.8 |  |  | 11.6
| door deduction | -1 | 3 | 1.05
| door deduction | -1 | 1 | 1.2
| Dissolution Room-1 | 1 | 2 | 2.64 |  |  | 5.28
|  | 1 | 2 | 5.8 |  |  | 11.6
| door deduction | -1 | 1 | 1.05
| Water Purification Room-1 | 1 | 2 | 2.59 |  |  | 5.18
|  | 1 | 2 | 3.18 |  |  | 6.36
| door deduction | -1 | 1 | 1.05 |  |  | -1.05
| Wash Area-1 | 1 | 2 | 2.59 |  |  | 5.18
|  | 1 | 2 | 2.5 |  |  | 5
| door deduction | -1 | 1 | 1.05 |  |  | -1.05
| Doccumentation Room-1 | 1 | 2 | 3.03 |  |  | 6.06
|  | 1 | 2 | 5.8 |  |  | 11.6
| door deduction | -1 | 1 | 1.2 |  |  | -1.2
| Doccumentation Room-2 | 1 | 2 | 6.16 |  |  | 12.32
|  | 1 | 2 | 3.44 |  |  | 6.88
| door deduction | -1 | 1 | 1.2 |  |  | -1.2
| Hot Zone Room | 1 | 2 | 6.16 |  |  | 12.32
|  | 1 | 2 | 4.95 |  |  | 9.9
| door deduction | -1 | 1 | 1.2 |  |  | -1.2
| Staff Dining Room | 1 | 2 | 6.16 |  |  | 12.32
|  | 1 | 2 | 2.42 |  |  | 4.84
| door deduction | -1 | 1 | 1.2 |  |  | -1.2
| Dissolution Room-2 | 1 | 2 | 6.16 |  |  | 12.32
|  | 1 | 2 | 2.78 |  |  | 5.56
| door deduction | -1 | 1 | 1.2 |  |  | -1.2
| Wet Analysis Lab-2 | 1 | 2 | 8.71 |  |  | 17.42
|  | 1 | 2 | 5.75 |  |  | 11.5
| door deduction | -1 | 4 | 1.05 |  |  | -4.2
| door deduction | -1 | 1 | 1.2 |  |  | -1.2
| Water Purification Room-2 | 1 | 2 | 3.05 |  |  | 6.1
|  | 1 | 2 | 3.19 |  |  | 6.38
| door deduction | -1 | 1 | 1.05 |  |  | -1.05
| Wash Area-2 | 1 | 2 | 3.05 |  |  | 6.1
|  | 1 | 2 | 2.46 |  |  | 4.92
| door deduction | -1 | 1 | 1.05 |  |  | -1.05
| Balance Room-2 | 1 | 2 | 2.83 |  |  | 5.66
|  | 1 | 2 | 5.75 |  |  | 11.5
| door deduction | -1 | 2 | 1.05 |  |  | -2.1
| Instrumentation Room-2 | 1 | 2 | 6.79 |  |  | 13.58
|  | 1 | 2 | 5.75 |  |  | 11.5
| door deduction | -1 | 1 | 1.05 |  |  | -1.05
| door deduction | -1 | 1 | 1.2 |  |  | -1.2
| Officer Room-1 | 1 | 2 | 4.4 |  |  | 8.8
|  | 1 | 2 | 3.12 |  |  | 6.24
| door deduction | -1 | 2 | 1 |  |  | -2
| Officer Room-2 | 1 | 2 | 4.4 |  |  | 8.8
|  | 1 | 2 | 3.12 |  |  | 6.24
| door deduction | -1 | 2 | 1 |  |  | -2
| Corridor-1 (Officer Rooms) | 1 | 2 | 18.58 |  |  | 37.16
| door deduction | -1 | 4 | 1 |  |  | -4
| staircase deduction | -1 | 1 | 2.46 |  |  | -2.46
| Corridor-2 (Wet Analysis Lab-1) | 1 | 2 | 17.42 |  |  | 34.84
|  | 1 | 2 | 1.8 |  |  | 3.6
| door deduction | -1 | 3 | 1.2 |  |  | -3.6
| corridor deduction | -1 | 2 | 1.8 |  |  | -3.6
| Corridor-3 (Hot Zone Room) | 1 | 2 | 18.58 |  |  | 37.16
| door deduction | -1 | 3 | 1.2 |  |  | -3.6
| corridor deduction | -1 | 1 | 1.8 |  |  | -1.8
| Corridor-4 (Wet Analysis Lab-2) | 1 | 2 | 11 |  |  | 22
|  | 1 | 2 | 1.8 |  |  | 3.6
| door deduction | -1 | 3 | 1.2 |  |  | -3.6
| door deduction | -1 | 1 | 1 |  |  | -1
| corridor deduction | -1 | 2 | 1.8 |  |  | -3.6
[7 empty] | 432.49 | Rmt | 117 | 50601
17 | Providing impervious coat to exposed RCC roof slab surfaces to required slopes with CM (1:3) prop. using screened sand 20mm thick (average) mixed with integral cement water proofing liquid confirming to IS: 2645-2003 manufactured by reputed manufacturers as approved by Engineer-in-charge at 1 Kg per one bag of cement, laid over roof slab when it is green, finished smooth with a floating coat of neat cement and thread lining at regular intervals of 45cmx45cm including cost and conveyance of all materials like cement, sand, water proofing compound, water etc., to site, including sales & other taxes on all materials and operational, incidental, and labour charges for mixing mortar, laying, lift charges, rendering smooth and thread lining, curing including rounding off junctions of wall and slab etc., and overheads & contractors profit complete for finished item of work. (APSS No. 901 & 903).
| Gents Toilet | 1 | 1 | 3 | 3.42 |  | 10.26
| Ladies Toilet | 1 | 1 | 3 | 3.42 |  | 10.26
| Toilet @officer rooms | 1 | 2 | 1.5 | 1.43 |  | 4.29
[7 empty] | 24.81 | Sqm | 675 | 16747
18 | Filling with light weight concrete in Cement Concrete (1:5:10) proportion using brick jelly for low roofs including cost and conveyance of all materials like cement, sand, brick bats etc., to site including cost of all labour charges for laying concrete, ramming, curing, overheads & contractors profit etc., complete for finished item of work. (APSS. No. 402)
| Gents Toilet | 1 | 1 | 3 | 3.42 | 0.5 | 5.13
| Ladies Toilet | 1 | 1 | 3 | 3.42 | 0.5 | 5.13
| Toilet @officer rooms | 1 | 2 | 1.5 | 1.43 | 0.5 | 2.15
[7 empty] | 12.41 | cum | 5269 | 65388
19 | Flooring with non-skid full body ceramic floor tiles of size 300mm x 300mm and thickness between 7 - 8mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630(Part 1 to 15) of any colour and finish in all shades and designs as approved by Engineer-in-charge, set over base coat of cement mortar (1:8), 12mm thick using screened sandover CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread @ 3.3 Kgs per Sqm & jointed epoxy emulsion grout/ synthetic /resin adhesive in width of 3-5 mm with Nylonspacers excluding cost of tiles neatly with to full depth mixed with pigment of matching shade, including cost of all materials like cement, screened sand , water and tiles etc., and overheads & contractors profit complete for finished item of work. (In toilets) (APSS No.701 & 707) .
| Gents Toilet | 1 | 1 | 3 | 3.42 |  | 10.26
| Ladies Toilet | 1 | 1 | 3 | 3.42 |  | 10.26
| Toilet @officer rooms | 1 | 2 | 1.5 | 1.43 |  | 4.29
[7 empty] | 24.81 | Sqm | 1377 | 34163
20 | Providing dadooing to walls with glazed full body porcelain wall tiles of size 300 x 600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete overheads & contractors profit complete for finished item of work.
| Gents Toilet | 1 | 2 | 3 | 2.1 |  | 12.6
|  | 1 | 2 | 3.42 | 2.1 |  | 14.36
| door deduction | -1 | 1 | 1 | 2.1 |  | -2.1
| Ladies Toilet | 1 | 2 | 3 | 2.1 |  | 12.6
|  | 1 | 2 | 3.42 | 2.1 |  | 14.36
| door deduction | -1 | 1 | 1 | 2.1 |  | -2.1
| Toilet @officer rooms | 1 | 4 | 1.5 | 2.1 |  | 12.6
|  | 1 | 4 | 1.43 | 2.1 |  | 12.01
| door deduction | -1 | 2 | 0.8 | 2.1 |  | -3.36
| Wash area | 1 | 2 | 1.2 | 2.1 |  | 5.04
|  | 1 | 2 | 0.6 | 2.1 |  | 2.52
[7 empty] | 78.53 | Sqm | 1035 | 81279
21 | Supply, erection and fixing of Emergency Exit Door Panic Door with Metal door frames and door shutters made of galvanized steel as per Technical Specifications.
| Emergency exit corridor | 1 | 1 |  |  |  | 1
[7 empty] | 1 | Nos
22 | Providing and Fixing of Scientific Doors as per Technical Specifications.
| Reference Standard Room | 1 | 1 | 1.05 | 2.1 |  | 2.21
| Instrumentation Room-1 | 1 | 2 | 1.05 | 2.1 |  | 4.41
| Balance Room-1 | 1 | 1 | 1.05 | 2.1 |  | 2.21
| Wet Analysis Lab-1 | 1 | 1 | 1.2 | 2.1 |  | 2.52
| Dissolution Room-1 | 1 | 1 | 1.2 | 2.1 |  | 2.52
|  | 1 | 1 | 1.05 | 2.1 |  | 2.21
| Water Purification Room-1 | 1 | 1 | 1.05 | 2.1 |  | 2.21
| Wash Area-1 | 1 | 1 | 1.05 | 2.1 |  | 2.21
| Doccumentation Room-1 | 1 | 1 | 1.2 | 2.1 |  | 2.52
| Doccumentation Room-2 | 1 | 1 | 1.2 | 2.1 |  | 2.52
| Hot Zone Room | 1 | 1 | 1.2 | 2.1 |  | 2.52
| Staff Dining Room | 1 | 1 | 1.2 | 2.1 |  | 2.52
| Dissolution Room-2 | 1 | 1 | 1.2 | 2.1 |  | 2.52
| Wet Analysis Lab-2 | 1 | 1 | 1.2 | 2.1 |  | 2.52
|  | 1 | 1 | 1.05 | 2.1 |  | 2.21
| Water Purification Room-2 | 1 | 1 | 1.05 | 2.1 |  | 2.21
| Wash Area-2 | 1 | 1 | 1.05 | 2.1 |  | 2.21
| Balance Room-2 | 1 | 2 | 1 | 2.1 |  | 4.2
| Instrumentation Room-2 | 1 | 1 | 1.2 | 2.1 |  | 2.52
| Officer Room-1 | 1 | 1 | 1 | 2.1 |  | 2.1
| Officer Room-2 | 1 | 1 | 1 | 2.1 |  | 2.1
[7 empty] | 53.17 | Sqm
23 | Supplying and fixing of Unplasticised PolyVinyl Chloride UPVC 3 track sliding Windows and with 7.5mm thick Aluminium Grill as per Technical Specifications.
| Reference Standard Room | 1 | 1 | 1.2 | 0.9 |  | 1.08
| Instrumentation room | 1 | 2 | 0.9 | 0.9 |  | 1.62
|  | 1 | 2 | 1.2 | 0.9 |  | 2.16
| Balance room | 1 | 2 | 1.2 | 0.9 |  | 2.16
| Wet analysis lab | 1 | 2 | 1.2 | 0.9 |  | 2.16
|  | 1 | 1 | 2.4 | 0.9 |  | 2.16
| Dissolution room | 1 | 1 | 1.5 | 0.9 |  | 1.35
| Water purification room | 1 | 1 | 1.2 | 0.9 |  | 1.08
| Doccummentation room | 1 | 2 | 1.5 | 0.9 |  | 2.7
| Doccummentation room | 1 | 1 | 0.9 | 0.9 |  | 0.81
| Hot Zone Room | 1 | 3 | 1.5 | 0.9 |  | 4.05
|  | 1 | 1 | 1.8 | 0.9 |  | 1.62
| Staff Dining Room | 1 | 1 | 0.9 | 0.9 |  | 0.81
| Dissolution room | 1 | 1 | 1.5 | 0.9 |  | 1.35
| Water purification room | 1 | 1 | 1.2 | 0.9 |  | 1.08
| Wash area | 1 | 1 | 1.2 | 0.9 |  | 1.08
| Wet analysis lab | 1 | 2 | 1.8 | 0.9 |  | 3.24
| Balance room | 1 | 1 | 1.2 | 0.9 |  | 1.08
| Instrumentation room | 1 | 2 | 1.2 | 0.9 |  | 2.16
|  | 1 | 1 | 1.8 | 0.9 |  | 1.62
|  | 1 | 1 | 2.4 | 0.9 |  | 2.16
| Officer room | 1 | 1 | 1.2 | 0.9 |  | 1.08
| Officer room | 1 | 1 | 1.2 | 0.9 |  | 1.08
[7 empty] | 39.69 | Sqm
24 | Providing and fixing in true horizontal level 14 mm - Mineral Fiber sheet 595 x 595 (Square / Tegular) Fissura fine model edge tiles with a Humidity Resistance of 90% RH,Average NRC 0.50, Light Reflectance >80%, Thermal Conductivity λ= 0.052 to 0.057 w/mk, Fire Performance Class 0/Class 1 using hot dipped Galvanized Steel section exposed surface with pre-coated capping, main Tee of size 24 x 32 mm at every 1200 mm c/c maximum and rotary stitched cross tee of size 24 x 27 mm at every 600 mm c/c and sub-cross tee of size 24 mm x 25 mm at 1200 mm c/c and wall angle of size 19 x 19 mm fixed to periphery of the wall and the above grid is suspended at every 1200 mm c/c in both directions using 2.0 mm thick pre-straightened GI Wire including cost and conveyance of all materials and labour charges such as cutting , fixing of standing of frame work exposing roof making, overheads & contractor profit etc., complete for finished item of work in all floor in all floors.
| Reference Standard Room | 1 | 1 | 4.4 | 2.7 |  | 11.88
| Instrumentation Room-1 | 1 | 1 | 4.4 | 11.3 |  | 49.72
| Balance Room-1 | 1 | 1 | 3.04 | 3.24 |  | 9.85
| Wet Analysis Lab-1 | 1 | 1 | 10.61 | 5.8 |  | 61.54
| Dissolution Room-1 | 1 | 1 | 2.64 | 5.8 |  | 15.31
| Water Purification Room-1 | 1 | 1 | 2.59 | 3.18 |  | 8.24
| Wash Area-1 | 1 | 1 | 2.59 | 3.18 |  | 8.24
| Doccumentation Room-1 | 1 | 1 | 3 | 5.8 |  | 17.4
| Gents Toilet | 1 | 1 | 3 | 3.42 |  | 10.26
| Ladies Toilet | 1 | 1 | 3 | 3.42 |  | 10.26
| Doccumentation Room-2 | 1 | 1 | 6.16 | 3.44 |  | 21.19
| Hot Zone Room | 1 | 1 | 6.16 | 4.95 |  | 30.49
| Staff Dining Room | 1 | 1 | 6.16 | 2.42 |  | 14.91
| Dissolution Room-2 | 1 | 1 | 6.16 | 2.78 |  | 17.12
| Wet Analysis Lab-2 | 1 | 1 | 8.71 | 5.75 |  | 50.08
| Water Purification Room-2 | 1 | 1 | 3 | 3.19 |  | 9.57
| Wash Area-2 | 1 | 1 | 3 | 2.46 |  | 7.38
| Balance Room-2 | 1 | 1 | 2.83 | 5.75 |  | 16.27
| Instrumentation Room-2 | 1 | 1 | 6.79 | 5.75 |  | 39.04
| Officer Room-1 | 1 | 1 | 4.4 | 3.12 |  | 13.73
| Toilet @officer rooms | 1 | 1 | 1.5 | 1.43 |  | 2.15
| Officer Room-2 | 1 | 1 | 4.4 | 3 |  | 13.2
| Toilet @officer rooms | 1 | 1 | 1.5 | 1.43 |  | 2.15
[7 empty] | 439.98 | Sqm | 1272 | 559655
25 | Supply & application of one coat water based cement primer of interior grade I and two coats of acrylic emulsion paint having VOC (Volatile Organic Compound) content less than 50 grams/litre for internal walls including cost and conveyance of all materials to site, sales & other taxes, incidental, operational and all labour charges etc., and overheads & contractors profit complete for finished item of work in all floors.
| Reference Standard Room | 1 | 2 | 4.4 | 3 |  | 26.4
|  | 1 | 2 | 2.7 | 3 |  | 16.2
| door deduction | -1 | 1 | 1.05 | 2.1 |  | -2.21
| window deduction | -1 | 1 | 1.2 | 0.9 |  | -1.08
| Instrumentation Room-1 | 1 | 2 | 4.4 | 3 |  | 26.4
|  | 1 | 2 | 11.3 | 3 |  | 67.8
| door deduction | -1 | 1 | 1.05 | 2.1 |  | -2.21
| window deduction | -1 | 2 | 0.9 | 0.9 |  | -1.62
|  | -1 | 2 | 1.2 | 0.9 |  | -2.16
| Balance Room-1 | 1 | 2 | 3.04 | 3 |  | 18.24
|  | 1 | 2 | 3.24 | 3 |  | 19.44
| door deduction | -1 | 1 | 1 | 2.1 |  | -2.1
| window deduction | -1 | 1 | 1.2 | 0.9 |  | -1.08
| Wet Analysis Lab-1 | 1 | 2 | 10.61 | 3 |  | 63.66
|  | 1 | 2 | 5.8 | 3 |  | 34.8
| door deduction | -1 | 3 | 1.05 | 2.1 |  | -6.62
| door deduction | -1 | 1 | 1.2 | 2.1 |  | -2.52
| window deduction | -1 | 1 | 2.4 | 0.9 |  | -2.16
| window deduction | -1 | 2 | 1.2 | 0.9 |  | -2.16
| Dissolution Room-1 | 1 | 2 | 2.64 | 3 |  | 15.84
|  | 1 | 2 | 5.8 | 3 |  | 34.8
| door deduction | -1 | 1 | 1.05 | 2.1 |  | -2.21
| window deduction | -1 | 2 | 1.2 | 0.9 |  | -2.16
| Water Purification Room-1 | 1 | 2 | 2.59 | 3 |  | 15.54
|  | 1 | 2 | 3.18 | 3 |  | 19.08
| door deduction | -1 | 1 | 1.05 | 2.1 |  | -2.21
| window deduction | -1 | 1 | 1.2 | 0.9 |  | -1.08
| Wash Area-1 | 1 | 2 | 2.59 | 3 |  | 15.54
|  | 1 | 2 | 2.5 | 3 |  | 15
| door deduction | -1 | 1 | 1.05 | 2.1 |  | -2.21
| Doccumentation Room-1 | 1 | 2 | 3.03 | 3 |  | 18.18
|  | 1 | 2 | 5.8 | 3 |  | 34.8
| door deduction | -1 | 1 | 1.2 | 2.1 |  | -2.52
| door deduction | -1 | 2 | 1.5 | 0.9 |  | -2.7
| Gents Toilet | 1 | 2 | 3 | 3 |  | 18
|  | 1 | 2 | 3.42 | 3 |  | 20.52
| door deduction | -1 | 1 | 1 | 2.1 |  | -2.1
| ladies Toilet | 1 | 2 | 3 | 3 |  | 18
|  | 1 | 2 | 3.42 | 3 |  | 20.52
| door deduction | -1 | 1 | 1 | 2.1 |  | -2.1
| Doccumentation Room-2 | 1 | 2 | 6.16 | 3 |  | 36.96
|  | 1 | 2 | 3.44 | 3 |  | 20.64
| door deduction | -1 | 1 | 1.2 | 2.1 |  | -2.52
| window deduction | -1 | 1 | 0.9 | 0.9 |  | -0.81
| Hot Zone Room | 1 | 2 | 6.16 | 3 |  | 36.96
|  | 1 | 2 | 4.95 | 3 |  | 29.7
| door deduction | -1 | 1 | 1.2 | 2.1 |  | -2.52
| window deduction | -1 | 2 | 1.5 | 0.9 |  | -2.7
| window deduction | -1 | 1 | 1.8 | 0.9 |  | -1.62
| Staff Dining Room | 1 | 2 | 6.16 | 3 |  | 36.96
|  | 1 | 2 | 2.42 | 3 |  | 14.52
| door deduction | -1 | 1 | 1.2 | 2.1 |  | -2.52
| window deduction | -1 | 1 | 1.5 | 0.9 |  | -1.35
| window deduction | -1 | 1 | 0.9 | 0.9 |  | -0.81
| Dissolution Room-2 | 1 | 2 | 6.16 | 3 |  | 36.96
|  | 1 | 2 | 2.78 | 3 |  | 16.68
| door deduction | -1 | 1 | 1.2 | 2.1 |  | -2.52
| Wet Analysis Lab-2 | 1 | 2 | 8.71 | 3 |  | 52.26
|  | 1 | 2 | 5.75 | 3 |  | 34.5
| door deduction | -1 | 4 | 1.05 | 2.1 |  | -8.82
| door deduction | -1 | 1 | 1.2 | 2.1 |  | -2.52
| window deduction | -1 | 2 | 1.8 | 0.9 |  | -3.24
| Water Purification Room-2 | 1 | 2 | 3.05 | 3 |  | 18.3
|  | 1 | 2 | 3.19 | 3 |  | 19.14
| door deduction | -1 | 1 | 1.05 | 2.1 |  | -2.21
| window deduction | -1 | 1 | 1.2 | 0.9 |  | -1.08
| Wash Area-2 | 1 | 2 | 3.05 | 3 |  | 18.3
|  | 1 | 2 | 2.46 | 3 |  | 14.76
| door deduction | -1 | 1 | 1.05 | 2.1 |  | -2.21
| window deduction | -1 | 1 | 1.2 | 0.9 |  | -1.08
| Balance Room-2 | 1 | 2 | 2.83 | 3 |  | 16.98
|  | 1 | 2 | 5.75 | 3 |  | 34.5
| door deduction | -1 | 2 | 1.05 | 2.1 |  | -4.41
| window deduction | -1 | 1 | 1.2 | 0.9 |  | -1.08
| Instrumentation Room-2 | 1 | 2 | 6.79 | 3 |  | 40.74
|  | 1 | 2 | 5.75 | 3 |  | 34.5
| door deduction | -1 | 1 | 1.05 | 2.1 |  | -2.21
| door deduction | -1 | 1 | 1.2 | 2.1 |  | -2.52
| window deduction | -1 | 2 | 1.2 | 0.9 |  | -2.16
| window deduction | -1 | 1 | 1.8 | 0.9 |  | -1.62
| window deduction | -1 | 1 | 2.4 | 0.9 |  | -2.16
| Officer Room-1 | 1 | 2 | 4.4 | 3 |  | 26.4
|  | 1 | 2 | 3.12 | 3 |  | 18.72
| door deduction | -1 | 2 | 1 | 2.1 |  | -4.2
| window deduction | -1 | 1 | 1.2 | 0.9 |  | -1.08
| Toilet @officer rooms | 1 | 2 | 1.5 | 3 |  | 9
|  | 1 | 2 | 1.43 | 3 |  | 8.58
| door deduction | -1 | 1 | 0.8 | 2.1 |  | -1.68
| Officer Room-2 | 1 | 2 | 4.4 | 3 |  | 26.4
|  | 1 | 2 | 3.12 | 3 |  | 18.72
| door deduction | -1 | 2 | 1 | 2.1 |  | -4.2
| window deduction | -1 | 1 | 1.2 | 0.9 |  | -1.08
| Toilet @officer rooms | 1 | 2 | 1.5 | 3 |  | 9
|  | 1 | 2 | 1.43 | 3 |  | 8.58
| door deduction | -1 | 1 | 0.8 | 2.1 |  | -1.68
| Corridor-1 (Officer Rooms) | 1 | 2 | 18.58 | 3.4 |  | 126.34
| door deduction | -1 | 4 | 1 | 2.1 |  | -8.4
| window deduction | -1 | 1 | 1.2 | 0.9 |  | -1.08
| staircase deduction | -1 | 1 | 2.46 | 3.4 |  | -8.36
| Corridor-2 (Wet Analysis Lab-1) | 1 | 2 | 17.42 | 3.4 |  | 118.46
|  | 1 | 2 | 1.8 | 3.4 |  | 12.24
| door deduction | -1 | 3 | 1.2 | 2.1 |  | -7.56
| corridor deduction | -1 | 2 | 1.8 | 3.4 |  | -12.24
| Corridor-3 (Hot Zone Room) | 1 | 2 | 18.58 | 3.4 |  | 126.34
| door deduction | -1 | 3 | 1.2 | 2.1 |  | -7.56
| window deduction | -1 | 1 | 1.8 | 0.9 |  | -1.62
| corridor deduction | -1 | 1 | 1.8 | 3.4 |  | -6.12
| Corridor-4 (Wet Analysis Lab-2) | 1 | 2 | 11 | 3.4 |  | 74.8
|  | 1 | 2 | 1.8 | 3.4 |  | 12.24
| door deduction | -1 | 3 | 1.2 | 2.1 |  | -7.56
| door deduction | -1 | 1 | 1 | 2.1 |  | -2.1
| corridor deduction | -1 | 2 | 1.8 | 3.4 |  | -12.24
| Emergency exit corridor | 1 | 2 | 7 | 3.4 |  | 47.6
| Corridor-1 (Officer Rooms) | 1 | 1 | 18.58 | 1.8 |  | 33.44
| Corridor-2 (Wet Analysis Lab-1) | 1 | 1 | 17.42 | 1.8 |  | 31.36
| Corridor-3 (Hot Zone Room) | 1 | 1 | 18.58 | 1.8 |  | 33.44
| Corridor-4 (Wet Analysis Lab-2) | 1 | 1 | 11 | 1.8 |  | 19.8
| Emergency exit corridor | 1 | 1 | 7 | 1.8 |  | 12.6
[7 empty] | 1617.52 | Sqm | 202 | 326739
26 | Providing and applying Wall putty of White Cement or Polymer or Cement based of average 1 to 2 mm thickness over plastered surface to prepare the surface even and smooth after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, applying emery paper, Sand the surface, clean and wipe off loose dust, applying knifing paste filler by putty knife / muslin pad, air dry for 2 - 3 hrs, sand with 180 and 320 No., emery paper for the surface preparation including cost and conveyance of all materials to work site and all operational, incidental, labour charges, over heads and etc., complete for finished item of work in 5th floor Internal walls. at Gandhi Hospital
| Reference Standard Room | 1 | 2 | 4.4 | 3.4 |  | 29.92
|  | 1 | 2 | 2.7 | 3.4 |  | 18.36
| door deduction | -1 | 1 | 1.05 | 2.1 |  | -2.21
| window deduction | -1 | 1 | 1.2 | 0.9 |  | -1.08
| Instrumentation Room-1 | 1 | 2 | 4.4 | 3.4 |  | 29.92
|  | 1 | 2 | 11.3 | 3.4 |  | 76.84
| door deduction | -1 | 1 | 1.05 | 2.1 |  | -2.21
| window deduction | -1 | 2 | 0.9 | 0.9 |  | -1.62
|  | -1 | 2 | 1.2 | 0.9 |  | -2.16
| Balance Room-1 | 1 | 2 | 3.04 | 3.4 |  | 20.67
|  | 1 | 2 | 3.24 | 3.4 |  | 22.03
| door deduction | -1 | 1 | 1 | 2.1 |  | -2.1
| window deduction | -1 | 1 | 1.2 | 0.9 |  | -1.08
| Wet Analysis Lab-1 | 1 | 2 | 10.61 | 3.4 |  | 72.15
|  | 1 | 2 | 5.8 | 3.4 |  | 39.44
| door deduction | -1 | 3 | 1.05 | 2.1 |  | -6.62
| door deduction | -1 | 1 | 1.2 | 2.1 |  | -2.52
| window deduction | -1 | 1 | 2.4 | 0.9 |  | -2.16
| window deduction | -1 | 2 | 1.2 | 0.9 |  | -2.16
| Dissolution Room-1 | 1 | 2 | 2.64 | 3.4 |  | 17.95
|  | 1 | 2 | 5.8 | 3.4 |  | 39.44
| door deduction | -1 | 1 | 1.05 | 2.1 |  | -2.21
| window deduction | -1 | 2 | 1.2 | 0.9 |  | -2.16
| Water Purification Room-1 | 1 | 2 | 2.59 | 3.4 |  | 17.61
|  | 1 | 2 | 3.18 | 3.4 |  | 21.62
| door deduction | -1 | 1 | 1.05 | 2.1 |  | -2.21
| window deduction | -1 | 1 | 1.2 | 0.9 |  | -1.08
| Wash Area-1 | 1 | 2 | 2.59 | 3.4 |  | 17.61
|  | 1 | 2 | 2.5 | 3.4 |  | 17
| door deduction | -1 | 1 | 1.05 | 2.1 |  | -2.21
| Doccumentation Room-1 | 1 | 2 | 3.03 | 3.4 |  | 20.6
|  | 1 | 2 | 5.8 | 3.4 |  | 39.44
| door deduction | -1 | 1 | 1.2 | 2.1 |  | -2.52
| door deduction | -1 | 2 | 1.5 | 0.9 |  | -2.7
| Gents Toilet | 1 | 2 | 3 | 3.4 |  | 20.4
|  | 1 | 2 | 3.42 | 3.4 |  | 23.26
| door deduction | -1 | 1 | 1 | 2.1 |  | -2.1
| ladies Toilet | 1 | 2 | 3 | 3.4 |  | 20.4
|  | 1 | 2 | 3.42 | 3.4 |  | 23.26
| door deduction | -1 | 1 | 1 | 2.1 |  | -2.1
| Doccumentation Room-2 | 1 | 2 | 6.16 | 3.4 |  | 41.89
|  | 1 | 2 | 3.44 | 3.4 |  | 23.39
| door deduction | -1 | 1 | 1.2 | 2.1 |  | -2.52
| window deduction | -1 | 1 | 0.9 | 0.9 |  | -0.81
| Hot Zone Room | 1 | 2 | 6.16 | 3.4 |  | 41.89
|  | 1 | 2 | 4.95 | 3.4 |  | 33.66
| door deduction | -1 | 1 | 1.2 | 2.1 |  | -2.52
| window deduction | -1 | 2 | 1.5 | 0.9 |  | -2.7
| window deduction | -1 | 1 | 1.8 | 0.9 |  | -1.62
| Staff Dining Room | 1 | 2 | 6.16 | 3.4 |  | 41.89
|  | 1 | 2 | 2.42 | 3.4 |  | 16.46
| door deduction | -1 | 1 | 1.2 | 2.1 |  | -2.52
| window deduction | -1 | 1 | 1.5 | 0.9 |  | -1.35
| window deduction | -1 | 1 | 0.9 | 0.9 |  | -0.81
| Dissolution Room-2 | 1 | 2 | 6.16 | 3.4 |  | 41.89
|  | 1 | 2 | 2.78 | 3.4 |  | 18.9
| door deduction | -1 | 1 | 1.2 | 2.1 |  | -2.52
| Wet Analysis Lab-2 | 1 | 2 | 8.71 | 3.4 |  | 59.23
|  | 1 | 2 | 5.75 | 3.4 |  | 39.1
| door deduction | -1 | 4 | 1.05 | 2.1 |  | -8.82
| door deduction | -1 | 1 | 1.2 | 2.1 |  | -2.52
| window deduction | -1 | 2 | 1.8 | 0.9 |  | -3.24
| Water Purification Room-2 | 1 | 2 | 3.05 | 3.4 |  | 20.74
|  | 1 | 2 | 3.19 | 3.4 |  | 21.69
| door deduction | -1 | 1 | 1.05 | 2.1 |  | -2.21
| window deduction | -1 | 1 | 1.2 | 0.9 |  | -1.08
| Wash Area-2 | 1 | 2 | 3.05 | 3.4 |  | 20.74
|  | 1 | 2 | 2.46 | 3.4 |  | 16.73
| door deduction | -1 | 1 | 1.05 | 2.1 |  | -2.21
| window deduction | -1 | 1 | 1.2 | 0.9 |  | -1.08
| Balance Room-2 | 1 | 2 | 2.83 | 3.4 |  | 19.24
|  | 1 | 2 | 5.75 | 3.4 |  | 39.1
| door deduction | -1 | 2 | 1.05 | 2.1 |  | -4.41
| window deduction | -1 | 1 | 1.2 | 0.9 |  | -1.08
| Instrumentation Room-2 | 1 | 2 | 6.79 | 3.4 |  | 46.17
|  | 1 | 2 | 5.75 | 3.4 |  | 39.1
| door deduction | -1 | 1 | 1.05 | 2.1 |  | -2.21
| door deduction | -1 | 1 | 1.2 | 2.1 |  | -2.52
| window deduction | -1 | 2 | 1.2 | 0.9 |  | -2.16
| window deduction | -1 | 1 | 1.8 | 0.9 |  | -1.62
| window deduction | -1 | 1 | 2.4 | 0.9 |  | -2.16
| Officer Room-1 | 1 | 2 | 4.4 | 3.4 |  | 29.92
|  | 1 | 2 | 3.12 | 3.4 |  | 21.22
| door deduction | -1 | 2 | 1 | 2.1 |  | -4.2
| window deduction | -1 | 1 | 1.2 | 0.9 |  | -1.08
| Toilet @officer rooms | 1 | 2 | 1.5 | 3.4 |  | 10.2
|  | 1 | 2 | 1.43 | 3.4 |  | 9.72
| door deduction | -1 | 1 | 0.8 | 2.1 |  | -1.68
| Officer Room-2 | 1 | 2 | 4.4 | 3.4 |  | 29.92
|  | 1 | 2 | 3.12 | 3.4 |  | 21.22
| door deduction | -1 | 2 | 1 | 2.1 |  | -4.2
| window deduction | -1 | 1 | 1.2 | 0.9 |  | -1.08
| Toilet @officer rooms | 1 | 2 | 1.5 | 3.4 |  | 10.2
|  | 1 | 2 | 1.43 | 3.4 |  | 9.72
| door deduction | -1 | 1 | 0.8 | 2.1 |  | -1.68
| Corridor-1 (Officer Rooms) | 1 | 2 | 18.58 | 3.4 |  | 126.34
| door deduction | -1 | 4 | 1 | 2.1 |  | -8.4
| window deduction | -1 | 1 | 1.2 | 0.9 |  | -1.08
| staircase deduction | -1 | 1 | 2.46 | 3.4 |  | -8.36
| Corridor-2 (Wet Analysis Lab-1) | 1 | 2 | 17.42 | 3.4 |  | 118.46
|  | 1 | 2 | 1.8 | 3.4 |  | 12.24
| door deduction | -1 | 3 | 1.2 | 2.1 |  | -7.56
| corridor deduction | -1 | 2 | 1.8 | 3.4 |  | -12.24
| Corridor-3 (Hot Zone Room) | 1 | 2 | 18.58 | 3.4 |  | 126.34
| door deduction | -1 | 3 | 1.2 | 2.1 |  | -7.56
| window deduction | -1 | 1 | 1.8 | 0.9 |  | -1.62
| corridor deduction | -1 | 1 | 1.8 | 3.4 |  | -6.12
| Corridor-4 (Wet Analysis Lab-2) | 1 | 2 | 11 | 3.4 |  | 74.8
|  | 1 | 2 | 1.8 | 3.4 |  | 12.24
| door deduction | -1 | 3 | 1.2 | 2.1 |  | -7.56
| door deduction | -1 | 1 | 1 | 2.1 |  | -2.1
| corridor deduction | -1 | 2 | 1.8 | 3.4 |  | -12.24
| Emergency exit corridor | 1 | 2 | 7 | 3.4 |  | 47.6
| Corridor-1 (Officer Rooms) | 1 | 1 | 18.58 | 1.8 |  | 33.44
| Corridor-2 (Wet Analysis Lab-1) | 1 | 1 | 17.42 | 1.8 |  | 31.36
| Corridor-3 (Hot Zone Room) | 1 | 1 | 18.58 | 1.8 |  | 33.44
| Corridor-4 (Wet Analysis Lab-2) | 1 | 1 | 11 | 1.8 |  | 19.8
| Emergency exit corridor | 1 | 1 | 7 | 1.8 |  | 12.6
[7 empty] | 1771.85 | Sqm | 242 | 428788
27 | Supplying and fixing of 30mm thick Wood Plastic Composite (WPC) Door shutter, comprising of 70% virgin polymer, 15% wood powder (fiber), and the remaining 15% additives, the door shutter shall be water resistant, fire resistant and termite resistant, with Tensile Strength not less than 170 Kgf/cm2 and the door shutters surface finished deco paint etc., complete excluding cost of hinges, latches, aldrops etc., and including ISI marked Stainless Steel fixtures 3 Nos. butt hinges (IS:205) of 75mm long, 1 No. aldrop (IS:15834) 200 mm long, 1 No. tower bolt (IS:15833) of 100 mm x 10mm dia, 1 No. 105mm long handles (IS:208), including labour charges for fixing the frame in position, fixing the shutter to the frame etc., including overheads & contractors profit complete for finished item of work as per APSS 1001 & 1002. (The vertical frame of door shall be embedded in flooring for deth of not less than 10mm) (1000mm x 2100mm) (Toilets)
| Toilet @officer rooms | 1 | 2 | 0.8 | 2.1 |  | 3.36
| Gents Toilet | 1 | 1 | 1 | 2.1 |  | 2.1
| ladies Toilet | 1 | 1 | 1 | 2.1 |  | 2.1
[7 empty] | 7.56 | Sqm |  | 0
28 | Providing and fixing factory made solid Wood Polymer Composite (WPC) single extruded Door Frame section of 100*65 MM with encapsulation of 6 MM rigid layer on all external surfaces. The door frame will have a rebate of 32MM/ 37 MM. The two Vertical members are to be joined together with the horizontal member using 8x75MM long MS Star full thread screws to be used with reverse forward speed control hand rilling machine. The ready/assembled door frame is fixed to wall using Z Hand fast 300 MM long hold fast. (For Toilets)
| Toilet @officer rooms | 1 | 2 | 5 | 2.1 |  | 21
| Gents Toilet | 1 | 1 | 5.2 | 2.1 |  | 10.92
| ladies Toilet | 1 | 1 | 5.2 | 2.1 |  | 10.92
[7 empty] | 42.84 | Rmtt |  | 0
29 | Supply and fixing of Aluminium Frame work with supporting Aluminium sections of size 40×25mm of 2mm thick for outer frame & verticals ,of size 40x20mm of 2mm thick High Pressure Laminated (HPL) Cubicals including fixing the required number of screws bolts,ss butt hinges ss tower bolt ,ss handles and also silicon jell and nut including labour charges for fixing the frame in position using High Pressure Laminated Boards Sheet, including cost and conveyance of all materials etc., complete as directed as approved by Engineer-in-charge during execution including overheads & contractors profit etc., complete for finished item of work. (For Toilets)
| Gents Toilet | 1 | 2 | 1.5 | 2.1 |  | 6.3
|  | 1 | 2 | 1.15 | 2.1 |  | 4.83
| urinals | 1 | 2 | 1 | 0.6 |  | 1.2
| ladies Toilet | 1 | 2 | 1.5 | 2.1 |  | 6.3
|  | 1 | 2 | 1 | 2.1 |  | 4.2
|  | 1 | 1 | 1.5 | 2.1 |  | 3.15
[7 empty] | 25.98 | Sqm |  | 0

## Sheet1
DATA
Sl. No. |  | Description | Quantity |  | Rate (in Rs.) | Per Unit |  | Amount (in Rs.)
1 |  | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete.
| a) | Brick masonry
(BLD-CSTN-14-9/299)
|  | Mazdoor(unskilled) | 0.409 | Nos. | 545 | 1 | Each | 222.905
|  | Add for MA @ 40% | 0.4 |  | 222.905 |  |  | 89.162
|  | Rate per 1 cum | [5 empty] | 312.067
|  | Overheads & Contractors Profit @ 13.615% | 0 |  | 312.067 |  |  | 0
|  | Rate per 1 cum |  |  |  |  | Total Rs. | 312.067
|  | Rate per 1 cum |  |  |  |  | Or Say | 312
| c) | Kadapa slabs or shahabad stone slabs on sand bed
|  | Rate as per SSR TBSC-U.I-11 | 10 | sqm | 12 | 1 | sqm | 120
|  | Add for MA @ 40% | 0.4 |  | 120 |  |  | 48
|  | Rate per 10 sqm | [5 empty] | 168
|  | Rate per 1 sqm | [5 empty] | 16.8
|  | Overheads & Contractors Profit @ 13.615% | 0 |  | 16.8 |  |  | 0
|  | Rate per 1 sqm |  |  |  |  | Total Rs. | 16.8
[7 empty] | Or Say | 17
| b) | Reinforced cement concrete
(BLD-CSTN-14-8/298)
|  | Mazdoor(unskilled) | 4.32 | Nos. | 545 | 1 | Each | 2354.4
|  | Add for MA @ 40% | 0.4 |  | 2354.4 |  |  | 941.76
for cutting steel bars (BLD-CSTN-14-10/300)
|  | Blacksmith 2nd class | 0.5 | Nos. | 580 | 1 | Each | 290
|  | Mazdoor(Male) | 0.5 | Nos. | 545 | 1 | Each | 272.5
|  | Add for MA @ 40% | 0.4 |  | 562.5 |  |  | 225
|  | Rate per 1 cum | [5 empty] | 4083.66
|  | Overheads & Contractors Profit @ 13.615% | 0 |  | 4083.66 |  |  | 0
|  | Rate per 1 cum |  |  |  |  | Total Rs. | 4083.66
[7 empty] | Or Say | 4084
2 |  | Dismantling doors, windows and clear storey windows, Ventilators etc., (wood or steel) shutters including Chowkhats, architraves,hold fasts and other attachments etc., and stacking them within 100m lead including labour charge etc., and overheads & contractors profit complete for finished item of work.
(BLD-CSTN-14-11)
| a) | Not exceeding 3 sqm in area :
Details of cost per each :
|  | 2nd class mason | 0.1 | Nos. | 580 | 1 | No. | 58
|  | Mazdoor(Male) | 0.2 | Nos. | 545 | 1 | No. | 109
|  | 2nd class Blacksmith | 0.05 | Nos. | 580 | 1 | No. | 29
|  | Add for MA @ 40% | 0.4 |  | 196 |  |  | 78.4
274.4
|  | Overheads & Contractors Profit @ 13.615% | 0 |  | 274.4 |  |  | 0
|  | Cost per each |  |  |  |  | Total Rs. | 274.4
[7 empty] | Say | 274
b) |  | Exceeding 3 sqm in area :
Details of cost per each :
|  | 2nd class mason | 0.13 | Nos. | 580 | 1 | No. | 75.4
|  | Mazdoor(Male) | 0.27 | Nos. | 545 | 1 | No. | 147.15
|  | 2nd class Blacksmith | 0.07 | Nos. | 580 | 1 | No. | 40.6
|  | Add for MA @ 40% | 0.4 |  | 263.15 |  |  | 105.26
368.41
|  | Overheads & Contractors Profit @ 13.615% | 0 |  | 368.41 |  |  | 0
|  | Cost per each |  |  |  |  | Total Rs. | 368.41
[7 empty] | Or Say | 368
21 |  | Masonry work 100 mm thick in CM (1:4) prop (cement: Screened sand) in super structure with Aerated (Cellular) Autoclaved Concrete Blocks conforming to IS:2185 (Part-3) - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600x 200 x 100 mm from approved source having minimum crushing strength of 3 N/Sq.m including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, including sales & other taxes on all materials, all operational, incidental and labour charges such as mixing cement mortar, constructing masonry, scaffolding charges, lift charges, curing, etc., complete but excluding seigniorage charges for finished item of work. (APSS No. 501 & 504).
Unit - 10sqm
|  | A.MATERIALS : | [7 empty] | 1.008
|  | Flyash lime solid blocks | 84 | Nos. | 47 | 1 | Nos. | 3948
|  | Cement | 36 | Kgs | 5000 | 1000 | Kgs | 180
|  | Fine aggregate ( Sand ) | 0.1 | cu.m. | 2531.2 | 1 | cu.m. | 253.12
B.LABOUR :
|  | 1st class mason | 0.42 | Nos. | 610 | 1 | Each | 256.2
|  | 2nd class mason | 0.92 | Nos. | 580 | 1 | Each | 533.6
|  | Mazdoor (Unskilled) | 2.8 | Nos. | 545 | 1 | Each | 1526
|  | Add for MA @ 40% | 0.4 |  | 2315.8 |  |  | 926.32
|  | water charges @ 1% | 0.01 |  | 7623.24 |  |  | 76.2324
|  | Rate per 10 sqm | [5 empty] | 7699.4724
|  | Rate per 1 sqm | [5 empty] | 769.95
Internal walls :
|  | Rate for other Floors | FF (G.F) | SF | TF | 4 F | 5 F | 6 F | 7F | 8F | 9F
|  | Rate as worked out above | 769.95 | 769.95 | 769.95 | 769.95 | 769.95 | 769.95 | 769.95 | 769.95 | 769.95
|  | Hire charges for Access Scaffolding | 12.17 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17 | 12.17
|  | Labour charges for scaffolding | 98.93 | 142.32 | 185.7 | 229.08 | 272.47 | 315.85 | 359.23 | 402.62 | 446
|  | Add for MA @ 40% | 39.572 | 56.928 | 74.28 | 91.632 | 108.988 | 126.34 | 143.692 | 161.048 | 178.4
|  | Lift charges ( Page 131 of Std. Data ) | 0 | 23.16 | 46.32 | 69.47 | 92.63 | 115.79 | 138.95 | 162.11 | 185.26
|  | Add for MA @ 40% | 0 | 9.264 | 18.528 | 27.788 | 37.052 | 46.316 | 55.58 | 64.844 | 74.104
|  | Rate per 1 sqm | 920.622 | 1013.792 | 1106.948 | 1200.09 | 1293.26 | 1386.416 | 1479.572 | 1572.742 | 1665.884
|  | Overheads & Contractors Profit @ 13.615% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Rate per 1 sqm | 920.622 | 1013.792 | 1106.948 | 1200.09 | 1293.26 | 1386.416 | 1479.572 | 1572.742 | 1665.884
|  | Or Say | 921 | 1014 | 1107 | 1200 | 1293 | 1386 | 1480 | 1573 | 1666
20 |  | Masonry work in CM (1:6) prop (cement: Screened sand) in super structure with Aerated (Cellular) Autoclaved Concrete Blocks conforming to IS:2185 (Part-3) - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600x 230 x 200 mm from approved source having minimum crushing strength of 3 N/Sq.m including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, including sales & other taxes on all materials, all operational, incidental and labour charges such as mixing cement mortar, constructing masonry, scaffolding charges, lift charges, curing, etc., complete but excluding seigniorage charges for finished item of work. (APSS No. 501 & 504).
Unit = 1 Cum
A.MATERIALS
|  | No of blocks required for 1 Cum of Masonry | 37 | Nos | 106 | 1 | Nos | 3922
|  | Cement | 24 | Kgs | 5000 | 1000 | Kgs | 120
|  | Fine aggregate ( Sand ) | 0.1 | Cum | 2531.2 | 1 | Cum | 253.12
B .LABOUR
|  | Mason 1st class | 0.42 | Nos. | 610 | 1 | Each | 256.2
|  | Mason 2nd class | 0.92 | Nos. | 580 | 1 | Each | 533.6
|  | Man Mazdoor | 0.7 | Nos. | 545 | 1 | Each | 381.5
|  | Women Mazdoor | 2.1 | Nos. | 545 | 1 | Each | 1144.5
|  | Add for MA @ 40% | 0.4 |  | 2315.8 |  |  | 926.32
|  | water charges @ 1% | 0.01 |  | 7537.24 |  |  | 75.3724
|  | Rate per 1 cum | [5 empty] | 7612.6124
| a) | Rate for Foundation , Basement , Compound wall
|  | Rate as above | 1 | cum | 7612.6124 | 1 | cum | 7612.6124
|  | Overheads & Contractors Profit @ 13.615% | 0 |  | 7612.6124 |  |  | 0
|  | Rate per 1 cum | [5 empty] | 7612.6124
[7 empty] | Or Say | 7613
| b) | Superstructure :
|  | Rate for other Floors | FF (G.F) | SF | TF | 4 F | 5 F | 6 F | 7F | 8F | 9F
|  | Rate as worked out above | 7612.6124 | 7612.6124 | 7612.6124 | 7612.6124 | 7612.6124 | 7612.6124 | 7612.6124 | 7612.6124 | 7612.6124
|  | Hire charges for Access Scaffolding | 52.913 | 52.913 | 52.913 | 52.913 | 52.913 | 52.913 | 52.913 | 52.913 | 52.913
|  | Labour charges for scaffolding | 430.13 | 618.78 | 807.39 | 996 | 1184.65 | 1373.26 | 1561.87 | 1750.52 | 1939.13
|  | Add for MA @ 40% | 172.052 | 247.512 | 322.956 | 398.4 | 473.86 | 549.304 | 624.748 | 700.208 | 775.652
|  | Lift charges ( Page 131 of Std. Data ) | 0 | 231.58 | 463.16 | 694.74 | 926.32 | 1157.9 | 1389.48 | 1621.06 | 1852.64
|  | Add for MA @ 40% | 0 | 92.632 | 185.264 | 277.896 | 370.528 | 463.16 | 555.792 | 648.424 | 741.056
|  |  | 8267.7074 | 8856.0294 | 9444.2954 | 10032.5614 | 10620.8834 | 11209.1494 | 11797.4154 | 12385.7374 | 12974.0034
|  | Overheads & Contractors Profit @ 13.615% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Rate per 1 cum | 8267.7074 | 8856.0294 | 9444.2954 | 10032.5614 | 10620.8834 | 11209.1494 | 11797.4154 | 12385.7374 | 12974.0034
|  | Or Say | 8268 | 8856 | 9444 | 10033 | 10621 | 11209 | 11797 | 12386 | 12974
12 |  | Supply and placing of the Design Mix Concrete M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Concrete Batching Plant with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials, centering using Casurina Ballies, Bamboos, Wooden Reapers, Runners, Wood Posts, Steel Plates etc., including all operational, incidental and labour charges such as weigh batching, machine mixing, lifting of concrete manually, laying concrete, curing, overheads & contractors profit etc., complete but excluding cost of steel and its fabrication charges for finished item of work (APSS No. 402).
| a) | LINTELS : | FF (G.F) | SF | TF | 4F | 5F | 6F
| (i) | Lifting by Manual means
Rate for other Floors
|  | Rate as above | 10430.2596 | 10430.2596 | 10430.2596 | 10430.2596 | 10430.2596 | 10430.2596
|  | Hire charges of centering and scaffolding | 920 | 920 | 920 | 920 | 920 | 920
|  | Labour charges | 1558 | 1714 | 1870 | 2025 | 2181 | 2337
|  | Add for MA @ 40% | 623.2 | 685.6 | 748 | 810 | 872.4 | 934.8
|  | Lift charges of materials (Manual) | 0 | 325.073 | 650.146 | 975.219 | 1300.292 | 1625.365
|  | Add for MA @ 40% | 0 | 130.03 | 260.06 | 390.09 | 520.12 | 650.15
|  | Rate per 1 cum | 13531.4596 | 14204.9626 | 14878.4656 | 15550.5686 | 16224.0716 | 16897.5746
|  | Overheads & Contractors Profit @ 13.615% | 0 | 0 | 0 | 0 | 0 | 0
|  | Rate per 1 cum | 13531.4596 | 14204.9626 | 14878.4656 | 15550.5686 | 16224.0716 | 16897.5746
|  | Or Say | 13531 | 14205 | 14878 | 15551 | 16224 | 16898
28 |  | Plastering 12mm thick in two coats using screened sand with base coat of 8mm thick in CM (1:6) and top coat of 4mm thick in CM (1:4) with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales & other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and overheads & contractors profit complete for finished item of work. (SS 901,903 & 904).
( BLD-CSTN-8-10)
Unit : 10 sqm
A.MATERIALS :
Base coat in CM(1:6) , 8mm thick
|  | Cement | 26.4 | Kgs | 5000 | 1000 | Kgs | 132
|  | Fine aggregate (Sand) | 0.11 | Cum | 2531.2 | 1 | Cum | 278.432
Top coat in CM(1:4) , 4mm thick
|  | Cement | 14.4 | Kgs | 5000 | 1000 | Kgs | 72
|  | Fine aggregate (Sand) | 0.04 | Cum | 2531.2 | 1 | Cum | 101.248
B.LABOUR :
|  | 1st Class Mason | 0.63 | Nos. | 610 | 1 | Each | 384.3
|  | 2nd Class Mason | 1.47 | Nos. | 580 | 1 | Each | 852.6
|  | Mazdoor (Unskilled) | 3.9 | Nos. | 545 | 1 | Each | 2125.5
|  | Add for MA @ 40% | 0.4 |  | 3362.4 |  |  | 1344.96
|  | water charges @ 1% | 0.01 |  | 5291.04 |  |  | 52.9104
|  | Rate per 10 Sqm | [5 empty] | 5343.9504
|  | Rate per 1 Sqm | [5 empty] | 534.4
Walls in superstructure :
|  | Rate for other Floors | FF (G.F) | SF | TF | 4 F | 5 F | 6 F
|  | Rate as worked out above | 534.4 | 534.4 | 534.4 | 534.4 | 534.4 | 534.4
|  | Hire charges for Access Scaffolding | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22
|  | Labour charges for scaffolding | 9.89 | 14.23 | 18.57 | 22.91 | 27.25 | 31.58
|  | Add for MA @ 40% | 3.96 | 5.69 | 7.43 | 9.16 | 10.9 | 12.63
|  | Lift charges (Page 131 of Std. Data) | 0 | 33.62 | 67.25 | 100.87 | 134.5 | 168.12
|  | Add for MA @ 40% | 0 | 13.448 | 26.9 | 40.348 | 53.8 | 67.248
|  | Rate per 1 Sqm | 549.47 | 602.608 | 655.77 | 708.908 | 762.07 | 815.198
|  | Overheads & Contractors Profit @ 13.615% | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 549.47 | 602.608 | 655.77 | 708.908 | 762.07 | 815.198
|  | Or Say | 549 | 603 | 656 | 709 | 762 | 815
30 |  | Plastering 20mm thick in two coats using screened sand with base coat of 16mm thick in CM(1:6) and top coat of 4mm thick in CM(1:4) with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales & other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and overheads & contractors profit complete for finished item of work .(SS 901,903 & 904).
(BLD-CSTN-8-9)
Unit : 10 sqm
A.MATERIALS :
Base coat in CM(1:6) , 16mm thick
|  | Cement | 43.2 | Kgs | 5000 | 1000 | Kgs | 216
|  | Fine aggregate (Sand) | 0.18 | Cum | 2531.2 | 1 | Cum | 455.616
Top coat in CM(1:4), 4mm thick
|  | Cement | 14.4 | Kgs | 5000 | 1000 | Kgs | 72
|  | Fine aggregate (Sand) | 0.04 | Cum | 2531.2 | 1 | Cum | 101.248
B.LABOUR :
|  | 1st Class Mason | 0.63 | Nos. | 610 | 1 | Each | 384.3
|  | 2nd Class Mason | 1.47 | Nos. | 580 | 1 | Each | 852.6
|  | Mazdoor (Unskilled) | 3.9 | Nos. | 545 | 1 | Each | 2125.5
|  | Add for MA @ 40% | 0.4 |  | 3362.4 |  |  | 1344.96
|  | water charges @ 1% | 0.01 |  | 5552.224 |  |  | 55.5222
|  | Rate per 10 Sqm | [5 empty] | 5607.7462
|  | Rate per 1 Sqm | [5 empty] | 560.77
Walls in superstructure :
|  | Rate for other Floors | FF (G.F) | SF | TF | 4 F | 5 F | 6 F
|  | Rate as worked out above | 560.77 | 560.77 | 560.77 | 560.77 | 560.77 | 560.77
|  | Hire charges for Access Scaffolding | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22
|  | Labour charges for scaffolding | 9.89 | 14.23 | 18.57 | 22.91 | 27.25 | 31.58
|  | Add for MA @ 40% | 3.96 | 5.69 | 7.43 | 9.16 | 10.9 | 12.63
|  | Lift charges ( Page 131 of Std. Data ) | 0 | 33.62 | 67.25 | 100.87 | 134.5 | 168.12
|  | Add for MA @ 40% | 0 | 13.448 | 26.9 | 40.348 | 53.8 | 67.248
|  |  | 575.84 | 628.978 | 682.14 | 735.278 | 788.44 | 841.568
|  | Overheads & Contractors Profit @ 13.615% | 0 | 0 | 0 | 0 | 0 | 0
|  | Rate per 1 Sqm | 575.84 | 628.978 | 682.14 | 735.278 | 788.44 | 841.568
|  | Or Say | 576 | 629 | 682 | 735 | 788 | 842
35 |  | Flooring with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM (1:8) prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab , including neat cement slurry of honey like consistancy spread @ 3.3 kgs per Sqm. and jointed neately with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site (excluding cost of C.C. bed) including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in-charge etc.,and overheads & contractors profit complete for finished item of work. (APSS No.701 & 707).
(BLD-CSTN-9-5)
Unit = 10 sqm.
A. MATERIALS:
|  | Cost of Double charged vitrified tiles TBSC-C.II-05 | 10.5 | sqm | 578 | 1 | Sqm | 6069
|  | Cement for CM(1:8)proportion for base coat | 21.6 | Kgs | 5000 | 1000 | Kgs | 108
|  | Cement for slurry | 33 | Kgs | 5000 | 1000 | Kgs | 165
|  | White Cement | 6 | Kgs | 36 | 1 | Kg | 216
|  | Sand for CM(1:8) | 0.12 | Cum | 2531.2 | 1 | Cum | 303.744
B .LABOUR
|  | Mason 1st class | 0.96 | Nos | 610 | 1 | Each | 585.6
|  | Mason 2nd class | 2.24 | Nos | 580 | 1 | Each | 1299.2
|  | Mazdoor(un skilled) | 3.3 | Nos | 545 | 1 | Each | 1798.5
|  | Add for MA @ 40% | 0.4 |  | 3683.3 |  |  | 1473.32
|  | Add water charges 1% | 0.01 |  | 12018.364 |  |  | 120.1836
|  | Rate for 10sqm | [5 empty] | 12138.5476
|  | Rate for other Floors | FF (G.F) | SF | TF | 4 F | 5 F | 6 F
|  | Rate as worked out above | 12138.5476 | 12138.5476 | 12138.5476 | 12138.5476 | 12138.5476 | 12138.5476
|  | Lift charges ( Page 131 of Std. Data ) | 0 | 368.33 | 736.66 | 1104.99 | 1473.32 | 1841.65
|  | Gravel | 0 | 147.332 | 294.664 | 441.996 | 589.328 | 736.66
|  |  | 12138.5476 | 12654.2096 | 13169.8716 | 13685.5336 | 14201.1956 | 14716.8576
|  | Overheads & Contractors Profit @ 13.615% | 0 | 0 | 0 | 0 | 0 | 0
|  | Rate per 10 Sqm | 12138.5476 | 12654.2096 | 13169.8716 | 13685.5336 | 14201.1956 | 14716.8576
|  | Rate per 1 Sqm | 1213.8548 | 1265.421 | 1316.9872 | 1368.5534 | 1420.1196 | 1471.6858
|  | Or Say | 1214 | 1265 | 1317 | 1369 | 1420 | 1472
45 |  | Providing skirting to internal walls to 10 cm height with soluble salt porcelain vitrified tiles screen printed and polished of thickness between 8 to 10mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630(Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707)
(BLD-CSTN-9-20)
Unit = 10 sqm
|  | Cost of vitrified tiles 8-10mm thick | 10.5 | sqm | 443 | 1 | sqm | 4651.5
|  | Sand for CM(1:5) base coat | 0.12 | cum | 2531.2 | 1 | cum | 303.744
|  | Cement for CM(1:5) base coat | 34.56 | Kgs | 5000 | 1000 | Kgs | 172.8
|  | Cement for slurry | 33 | Kgs | 5000 | 1000 | Kgs | 165
|  | White cement for jointing & pointing | 2 | Kgs | 36 | 1 | Kg | 72
B.LABOUR
|  | Mason 1st class | 0.96 | Nos. | 610 | 1 | Each | 585.6
|  | Mason 2nd class | 2.24 | Nos. | 580 | 1 | Each | 1299.2
|  | Mazdoor(unskilled) | 3.3 | Nos. | 545 | 1 | Each | 1798.5
|  | Add for MA @ 40% | 0.4 |  | 3683.3 |  |  | 1473.32
|  | Add water charges 1% | 0.01 |  | 10521.664 |  |  | 105.2166
|  | Rate for 10 sqm | [5 empty] | 10626.8806
|  | Rate for other Floors | FF (G.F) | SF | TF | 4 F | 5 F | 6 F
|  | Rate as worked out above | 10626.8806 | 10626.8806 | 10626.8806 | 10626.8806 | 10626.8806 | 10626.8806
|  | Lift charges ( Page 131 of Std. Data ) | 0 | 368.33 | 736.66 | 1104.99 | 1473.32 | 1841.65
|  | Add for MA @ 40% | 0 | 147.332 | 294.664 | 441.996 | 589.328 | 736.66
|  |  | 10626.8806 | 11142.5426 | 11658.2046 | 12173.8666 | 12689.5286 | 13205.1906
|  | Overheads & Contractors Profit @ 13.615% | 0 | 0 | 0 | 0 | 0 | 0
|  | Rate per 10 Sqm | 10626.8806 | 11142.5426 | 11658.2046 | 12173.8666 | 12689.5286 | 13205.1906
|  | Rate per 1 RM | 106.2688 | 111.4254 | 116.582 | 121.7387 | 126.8953 | 132.0519
|  | Or Say | 106 | 111 | 117 | 122 | 127 | 132
34 |  | Flooring with non-skid full body ceramic floor tiles of size 300mm x 300mm and thickness between 7 - 8mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630(Part 1 to 15) of any colour and finish in all shades and designs as approved by Engineer-in-charge, set over base coat of cement mortar (1:8), 12mm thick using screened sandover CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread @ 3.3 Kgs per Sqm & jointed epoxy emulsion grout/ synthetic /resin adhesive in width of 3-5 mm with Nylonspacers excluding cost of tiles neatly with to full depth mixed with pigment of matching shade, including cost of all materials like cement, screened sand , water and tiles etc., and overheads & contractors profit complete for finished item of work. (In toilets) (APSS No.701 & 707) .
(BLD-CSTN-9-6)
Unit = 10 sqm.
A. MATERIALS:
|  | Ceramic tiles 7 to 8mm thick (300mm x 300mm) | 10.5 | Sqm | 315 | 1 | Sqm | 3307.5
|  | Cement for CM(1:8) proportion for base coat | 21.6 | Kgs | 5000 | 1000 | Kgs | 108
|  | Cement for slurry | 33 | Kgs | 5000 | 1000 | Kgs | 165
|  | Providing and fixing flooring with full depth jointing and pointing to the Vitrified/ CeramicTile flooring in specified thick for tiles of any sizes with epoxy emulsion grout/ synthetic /resin adhesive in width of 3-5 mm with Nylonspacers excluding cost of tiles. | 10.5 | SQM | 340 | 1 | Sqm | 3570
|  | Sand for CM(1:8) | 0.12 | Cum | 2531.2 | 1 | Cum | 303.744
B .LABOUR
|  | Mason 1st class | 0.96 | Nos | 610 | 1 | Each | 585.6
|  | Mason 2nd class | 2.24 | Nos | 580 | 1 | Each | 1299.2
|  | Mazdoor(un skilled) | 3.3 | Nos | 545 | 1 | Each | 1798.5
|  | Add for MA @ 40% | 0.4 |  | 3683.3 |  |  | 1473.32
|  | Add water charges 1% | 0.01 |  | 12610.864 |  |  | 126.1086
|  | Rate for 10sqm | [5 empty] | 12736.9726
|  | Rate for other Floors | FF (G.F) | SF | TF | 4 F | 5 F | 6 F
|  | Rate as worked out above | 12736.9726 | 12736.9726 | 12736.9726 | 12736.9726 | 12736.9726 | 12736.9726
|  | Lift charges ( Page 131 of Std. Data ) | 0 | 368.33 | 736.66 | 1104.99 | 1473.32 | 1841.65
|  | Add for MA @ 40% | 0 | 147.332 | 294.664 | 441.996 | 589.328 | 736.66
|  |  | 12736.9726 | 13252.6346 | 13768.2966 | 14283.9586 | 14799.6206 | 15315.2826
|  | Overheads & Contractors Profit @ 13.615% | 0 | 0 | 0 | 0 | 0 | 0
|  | Rate per 10 Sqm | 12736.9726 | 13252.6346 | 13768.2966 | 14283.9586 | 14799.6206 | 15315.2826
|  | Rate per 1 Sqm | 1273.6973 | 1325.2635 | 1376.8297 | 1428.3959 | 1479.9621 | 1531.5283
|  | Or Say | 1274 | 1325 | 1377 | 1428 | 1480 | 1532
30 |  | Providing impervious coat to exposed RCC roof slab surfaces to required slopes with CM (1:3) prop. using screened sand 20mm thick (average) mixed with integral cement water proofing liquid confirming to IS: 2645-2003 manufactured by reputed manufacturers as approved by Engineer-in-charge at 1 Kg per one bag of cement, laid over roof slab when it is green, finished smooth with a floating coat of neat cement and thread lining at regular intervals of 45cmx45cm including cost and conveyance of all materials like cement, sand, water proofing compound, water etc., to site, including sales & other taxes on all materials and operational, incidental, and labour charges for mixing mortar, laying, lift charges, rendering smooth and thread lining, curing including rounding off junctions of wall and slab etc., and overheads & contractors profit complete for finished item of work. (APSS No. 901 & 903).
(BLD-CSTN-10-25)
Unit : 10 sqm
A.MATERIALS :
|  | Cement | 100.8 | Kgs | 5000 | 1000 | Kgs | 504
|  | Fine aggregate (Sand) | 0.21 | Cum | 2531.2 | 1 | Cum | 531.552
|  | Integral cement waterproofing liquid | 0.4 | Ltrs | 223 | 1 | Ltrs | 89.2
B.LABOUR :
|  | 1st Class Mason | 0.66 | Nos. | 610 | 1 | Each | 402.6
|  | 2nd Class Mason | 1.54 | Nos. | 580 | 1 | Each | 893.2
|  | Mazdoor (Unskilled) | 3.7 | Nos. | 545 | 1 | Each | 2016.5
|  | Add for MA @ 40% | 0.4 |  | 3312.3 |  |  | 1324.92
|  | water charges @ 1% | 0.01 |  | 5761.972 |  |  | 57.6197
|  | Rate per 10 Sqm | [5 empty] | 5819.5917
|  | Rate for other Floors | FF (G.F) | SF | TF | 4 F | 5 F | 6 F
|  | Rate as worked out above | 5819.5917 | 5819.5917 | 5819.5917 | 5819.5917 | 5819.5917 | 5819.5917
|  | Lift charges ( Page 131 of Std. Data ) | 0 | 331.23 | 662.46 | 993.69 | 1324.92 | 1656.15
|  | Add for MA @ 40% | 0 | 132.492 | 264.984 | 397.476 | 529.968 | 662.46
|  |  | 5819.5917 | 6283.3137 | 6747.0357 | 7210.7577 | 7674.4797 | 8138.2017
|  | Overheads & Contractors Profit @ 13.615% | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 5819.5917 | 6283.3137 | 6747.0357 | 7210.7577 | 7674.4797 | 8138.2017
|  | Rate per 1 Sqm | 581.9592 | 628.3314 | 674.7036 | 721.0758 | 767.448 | 813.8202
|  | Or Say | 582 | 628 | 675 | 721 | 767 | 814
47 |  | Filling with light weight concrete in Cement Concrete (1:5:10) proportion using brick jelly for low roofs including cost and conveyance of all materials like cement, sand, brick bats etc., to site including cost of all labour charges for laying concrete, ramming, curing, overheads & contractors profit etc., complete for finished item of work. (APSS. No. 402)
(BLD-CSTN-3-7)
Unit: 1 Cum
A. Materials :-
|  | Cement | 129.6 | Kgs | 5000 | 1000 | Kgs | 648
|  | Cost of brick jelly 20mm size(1/3rd rate) | 460 | Nos. | 9325.38 | 1000 | Nos. | 1429.8916
|  | Fine aggregate ( Sand ) | 0.45 | Cum | 2321.2 | 1 | Cum | 1044.54
|  | Water (including curing) | 1.2 | kl | 109 | 1 | kl | 130.8
B.MACHINERY :
|  | Concrete Mixer 10 / 7 cft (0.2 / 0.8 cum) capacity | 1 | hour | 194.7 | 1 | hour | 194.7
|  | Crew Charges | 1 | hour | 318.5 | 1 | hour | 318.5
|  | Add MA on crew charges | 0.4 |  | 318.5 |  |  | 127.4
C.LABOUR :
|  | 1st class mason | 0.1 | Nos. | 610 | 1 | Each | 61
|  | Mazdoor (unskilled) | 1.39 | Nos. | 545 | 1 | Each | 757.55
|  | Add for MA @ 40% | 0.4 |  | 818.55 |  |  | 327.42
5039.8016
|  | Rate for other Floors | FF (G.F) | SF | TF | 4 F | 5 F | 6 F
|  | Rate as above | 5039.8016 | 5039.8016 | 5039.8016 | 5039.8016 | 5039.8016 | 5039.8016
|  | Lift charges ( Page 131 of Std. Data ) | 0 | 81.86 | 163.71 | 245.57 | 327.42 | 409.28
|  | Add for MA @ 40% | 0 | 32.744 | 65.484 | 98.228 | 130.968 | 163.712
|  | Rate per 1 cum | 5039.8016 | 5154.4056 | 5268.9956 | 5383.5996 | 5498.1896 | 5612.7936
|  | Overheads & Contractors Profit @ 13.615% | 0 | 0 | 0 | 0 | 0 | 0
|  | Rate per 1 cum | 5039.8016 | 5154.4056 | 5268.9956 | 5383.5996 | 5498.1896 | 5612.7936
|  | Or Say | 5040 | 5154 | 5269 | 5384 | 5498 | 5613
44 |  | Providing dadooing to walls with glazed full body porcelain wall tiles of size 300 x 600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete overheads & contractors profit complete for finished item of work.
(BLD-CSTN-9-18)
Unit = 10 sqm
A.MATERIALS :
|  | cost of glazed full body porcelain wall tiles of size 300 x 600 mm | 10.5 | sqm | 750 | 1 | sqm | 7875
|  | Sand for CM(1:5) base coat | 0.12 | cum | 2531.2 | 1 | cum | 303.744
|  | Cement for CM(1:5) base coat | 34.56 | Kgs | 5000 | 1000 | Kgs | 172.8
|  | Cement for slurry | 33 | Kgs | 5000 | 1000 | Kgs | 165
|  | White cement for jointing & pointing | 6 | Kgs | 36 | 1 | Kg | 216
B.LABOUR
|  | Mason 1st class | 0.77 | Nos. | 610 | 1 | Each | 469.7
|  | Mazdoor(unskilled) | 0.8 | Nos. | 545 | 1 | Each | 436
|  | Add for MA @ 40% | 0.4 |  | 905.7 |  |  | 362.28
|  | Add water charges 1% | 0.01 |  | 10000.524 |  |  | 100.0052
|  | Rate for 10 sqm | [5 empty] | 10100.5292
|  | Rate for other Floors | FF (G.F) | SF | TF | 4 F | 5 F | 6 F
|  | Rate as worked out above | 10100.5292 | 10100.5292 | 10100.5292 | 10100.5292 | 10100.5292 | 10100.5292
|  | Lift charges ( Page 131 of Std. Data ) | 0 | 90.57 | 181.14 | 271.71 | 362.28 | 452.85
|  | Add for MA @ 40% | 0 | 36.228 | 72.456 | 108.684 | 144.912 | 181.14
|  |  | 10100.5292 | 10227.3272 | 10354.1252 | 10480.9232 | 10607.7212 | 10734.5192
|  | Overheads & Contractors Profit @ 13.615% | 0 | 0 | 0 | 0 | 0 | 0
|  | Rate per 10 Sqm | 10100.5292 | 10227.3272 | 10354.1252 | 10480.9232 | 10607.7212 | 10734.5192
|  | Rate per 1 Sqm | 1010.0529 | 1022.7327 | 1035.4125 | 1048.0923 | 1060.7721 | 1073.4519
|  | Or Say | 1010 | 1023 | 1035 | 1048 | 1061 | 1073
69 |  | Providing and fixing in true horizontal level 14 mm - Mineral Fiber sheet 595 x 595 (Square / Tegular) Fissura fine model edge tiles with a Humidity Resistance of 90% RH,Average NRC 0.50, Light Reflectance >80%, Thermal Conductivity λ= 0.052 to 0.057 w/mk, Fire Performance Class 0/Class 1 using hot dipped Galvanized Steel section exposed surface with pre-coated capping, main Tee of size 24 x 32 mm at every 1200 mm c/c maximum and rotary stitched cross tee of size 24 x 27 mm at every 600 mm c/c and sub-cross tee of size 24 mm x 25 mm at 1200 mm c/c and wall angle of size 19 x 19 mm fixed to periphery of the wall and the above grid is suspended at every 1200 mm c/c in both directions using 2.0 mm thick pre-straightened GI Wire including cost and conveyance of all materials and labour charges such as cutting , fixing of standing of frame work exposing roof making, overheads & contractor profit etc., complete for finished item of work in all floor in all floors.
(BLD-CSTN-10-33 & vide Page No. 391 of SoR 2011-12)
Unit 1 Sqm
A) Material requirement
|  | 14mm Mineral Fiber sheet 600 x 600 TBSC-K.I-05 | 1 | sqm | 621 | 1 | sqm | 621
|  | Hotdipped GI Angle - Precoated - Grid - 19mmx19mmX0.7mm TBSC-K.II-08 | 0.4 | RM | 44 | 1 | RM | 17.6
|  | Polyster painted GI - T section - 1200mm - 24x32mm and 24x25mm (sub-cross Tee) TBSC-K.II-09&10 | 1.6 | RM | 51.5 | 1 | RM | 82.4
|  | Polyster painted GI-T Section - 300mm - 24mm x 27mm TBSC-K.II-11 | 1.6 | RM | 50 | 1 | RM | 80
|  | GI Rod - prestraightened - 2.0mm dia -Connecting Rod TBSC-K.II-24 | 1.28 | RM | 13 | 1 | RM | 16.64
|  | 6mm Nylon Rawl Plug TBSC-K.II-15 | 1.28 | Nos. | 6 | 1 | No. | 7.68
B) Labour charges
|  | 1st Class Carpenter | 0.12 | Nos. | 720 | 1 | No. | 86.4
|  | 2nd Class Carpenter | 0.12 | Nos. | 580 | 1 | No. | 69.6
|  | 1st Class Painter | 0.024 | Nos. | 700 | 1 | No. | 16.8
|  | 2nd Class Painter | 0.024 | Nos. | 580 | 1 | No. | 13.92
|  | Power Saw cutter - Hand Operated - Operator | 0.012 | Nos. | 710 | 1 | No. | 8.52
|  | Power Drill - Hand Operated - Operator | 0.012 | Nos. | 710 | 1 | No. | 8.52
|  | Unskilled Mazdoor | 0.072 | Nos. | 545 | 1 | No. | 39.24
|  | Add for MA @ 40% | 0.4 |  | 243 |  |  | 97.2
C) Machinery
|  | Power Saw cutter - Hand Operated - Hire Charges TBSC-S.I-02 | 0.32 | Hours | 152 | 1 | No. | 48.64
|  | Power Drill - Hand Operated - Hire Charges TBSC-S.I-03 | 0.32 | Hours | 142 | 1 | No. | 45.44
1259.6
|  | Scaffolding charges 1% | 0.01 |  | 1259.6 |  |  | 12.596
|  | Basic Cost per 1 sqm | [5 empty] | 1272.196
|  | Overheads & Contractors Profit @ 13.615% | 0 |  | 1272.196 |  |  | 0
|  | Rate per 1 sqm | [5 empty] | 1272.196
[7 empty] | Say | 1272
55 |  | Supply & application of one coat water based cement primer of interior grade I and two coats of acrylic emulsion paint having VOC (Volatile Organic Compound) content less than 50 grams/litre for internal walls including cost and conveyance of all materials to site, sales & other taxes, incidental, operational and all labour charges etc., and overheads & contractors profit complete for finished item of work in all floors.
(BLD-CSTN-12-2& Amendment in SoR 2011-12)
Unit 10 Sqm.
A. Materials:-
|  | Cost of cement primer interior grade I TBSC-G.I-01 | 1 | Kg | 173 | 1 | Kg | 173
|  | Painter 1st class | 0.21 | Nos. | 700 | 1 | Each | 147
|  | Painter 2nd class | 0.49 | Nos. | 580 | 1 | Each | 284.2
|  | Acrylic emulsion paint TBSC-G.III-04 | 0.8 | Ltrs | 263 | 1 | Ltrs | 210.4
|  | Painter 1st class | 0.36 | Nos. | 700 | 1 | Each | 252
|  | Painter 2nd class | 0.84 | Nos. | 580 | 1 | Each | 487.2
|  | Add for MA @ 40% | 0.4 |  | 1170.4 |  |  | 468.16
|  | Sundries including brushes, ladders etc., @ 1% | 0.01 |  | 2021.96
2021.96
|  | Overheads & Contractors Profit @ 13.615% | 0 |  | 2021.96 |  |  | 0
|  | Rate per 10 sqm | [5 empty] | 2021.96
|  | Rate per 1 sqm | [5 empty] | 202.196
[7 empty] | Say | 202
53 |  | Providing and applying Wall putty of White Cement or Polymer or Cement based of average 1 to 2 mm thickness over plastered surface to prepare the surface even and smooth after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, applying emery paper, Sand the surface, clean & wipe off loose dust, applying knifing paste filler by putty knife / muslin pad, air dry for 2 - 3 hrs, sand with 180 and 320 No., emery paper for the surface preparation including cost and conveyance of all materials to work site and all operational, incidental, labour charges, over heads and contractors profit etc., complete for finished item of work in all floors for Internal walls.
(As per Amendment in SoR 2011-12)
Unit = 10 Sqm
|  | Wall putty TBSC-G.I-03 | 23 | Kgs | 41 | 1 | Kg | 943
|  | Painter 1st class | 0.273 | Nos. | 700 | 1 | Each | 191.1
|  | Painter 2nd class | 0.637 | Nos. | 580 | 1 | Each | 369.46
|  | Mazdoor | 0.91 | Nos. | 545 | 1 | Each | 495.95
|  | Add for MA @ 40% | 0.4 |  | 1056.51 |  |  | 422.604
|  | Sundries for emery papers, fillers, knife etc., @ 1% | 0.01 |  | 2422.114
2422.114
|  | Overheads & Contractors Profit @ 13.615% | 0 |  | 2422.114 |  |  | 0
|  | Rate per 10 sqm | [5 empty] | 2422.114
|  | Rate per 1 sqm | [5 empty] | 242.2114
[7 empty] | Say | 242