## Ele Abstract
ABSTRACT - ELECTRICAL WORKS (SSR 2024-25)
NAME OF THE WORK : PROPOSED GANDHI MEDICAL COLLEGE & HOSPITAL COMPLEX MUSHEERABAD, SECUNDERABAD
S.No | Description of Works | Amount
1 | GIRLS HOSTEL | 5860754
2 | BOYS HOSTEL | 10289728.75
3 | SR. RESIDENTS HOSTEL | 7517385.75
| Grand Total : | 16150482.75

## EST-GH
ELECTRICAL ESTIMATE
Sl. No. | Description of Work | Quantity | Unit | Rate | Amount
1 | Supply and Laying of ISI 25mm outer dia heavy grade with IS:9537 part 3 rigid PVC pipe concealed in Roof Slabs with all required PVC / Metallic Deep Boxes including masonary work and labour charges etc., complete. Makes : Sudhakar / Finolex / Modi / VIP / Precision / Universal / Million Plast / Gold / Polycab / DEC | 450 | ONE RM | 102 | 45900
2 | Supply and laying of ISI 25mm outer dia medium grade, with IS:9537 part 3 rigid PVC concealed in wall with all required PVC / Metallic Junction Boxes including masonary work and labour charges etc., Makes:- Sudhakar / Finolex / Modi / VIP / Precision / Universal / Million Plast / Gold / Polycab / DEC. | 3400 | ONE RM | 107 | 363800
3 | Supply and erecting PVC / GI / MS Galvanished fan hook box with hook in RCC slab including all Labour charges etc., complete. | 60 | EACH | 158 | 9480
WIRING
4 | Wiring with run of 2 of 1.5 Sqmm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specification for Copper cable. in existing PVC conduit pipe including Supply and fixing of Jumbo Ceiling rose and 6A/10A ISI Mark 1way Modular switch with required modular box and cover frame in existing Surface or Concealed pipe wiring including cost and conveyance of all material and all labour charges etc., complete for light, Fan, Exhaust fan and bell points in R.B. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | 300 | EACH POINT | 935 | 280500
5 | Supply and fixing of 10A 3/2 Pin 2 Module Modular Socket with shutter with 6 / 10A 1 Way 1 Module Modular Switch, 3 Module box with cover frame in Common switch board including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B. Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | 70 | Each | 716 | 50120
6 | Supply and fixing of 6 / 10A 1 Way 1 Module Modular Switches - 2 Nos and 10A 3/2 Pin 2 Module Modular Socket with shutter - 2 Nos Modular type with cover plate and GI switch box fixing on separate board including all labour charges etc., complete. Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. |  | Each | 1301 | 0
7 | Supply and fixing of 16A / 6A 2 Module Combi Socket Modular Socket with shutter with 16A/20A 1 Way 1 Module Modular Switch fixed on suitable size Modular box with required cover frame including with connections, cost and conveyance of all material and all labour charges etc., complete Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. |  | Each | 846 | 0
8 | Supply and fixing of following switches and sockets modular type on suitable size Modular deep box with cover frame including cost and coveyance of all material and all labour charges etc., complete with following configurations 1) 16A / 6A 2 Module Combi Socket Modular Socket with shutter - 1 No 2) 16A/20A 1 Way 1 Module Modular Switch. - 1 No 3) 10A 3/2 Pin 2 Module Modular Socket with shutter - 1 Nos. 4) 6 / 10A 1 Way 1 Module Modular Switch – 1 Nos. including cost and coveyance of all material and all labour charges etc., complete for Computer, LAB and OTs Use Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. |  | Each | 1432 | 0
9 | Supply and fixing of following switches and sockets modular type on suitable size Modular deep box with cover frame including cost and coveyance of all material and all labour charges etc., complete with following configurations. 1) 16A / 6A 2 Module Combi Socket Modular Socket with shutter - 2 Nos 2) 16A/20A 1 Way 1 Module Modular Switch. - 2 Nos 3) 10A 3/2 Pin 2 Module Modular Socket with shutter - 2 Nos. 4) 6 / 10A 1 Way 1 Module Modular Switch - 2 Nos. including cost and coveyance of all material and all labour charges etc., complete for LAB,ICU's and OTs Use Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. |  | Each | 2846 | 0
RUN of MAINS
10 | Supply and Run of 1 of 1.5 sq.mm (Earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specification for Copper cable. specifications for Copper cable in the existing conduict pipe for earth continuity inlcuding all labour charges etc., complete. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | 1700 | One RM | 37 | 62900
11 | Supply and Run of 3 of 2.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable of in existing conduit pipe for individual lighting circuits including labour charges etc., complete as required for switch boards. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | 2600 | One RM | 166 | 431600
12 | Supply and Run of 3 of 4.0 sq mm (phase neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable of in existing pipe for power points and AC Sockets inlcuding all labour charges etc., complete. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | 2100 | One RM | 239 | 501900
13 | Supply and Run of 3 of 6.0 sq mm (phase neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable of in existing pipe for SPNDB's incoming inlcuding all labour charges etc., complete. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | 600 | One RM | 336 | 201600
14 | Supply and Run of 5 of 6.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable in the existing conduict pipe for run of mains from VTPN / Panel Board to TPN DB"s with pin type lugs and connections etc., complete. [for LDBs & 4P MCB's ] Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | 550 | One RM | 568 | 312400
15 | Supply and Run of 5 of 10.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable in the existing conduict pipe for run of mains from VTPN / Panel Board to TPN DB"s with pin type lugs and connections etc., complete. [for PDBs] Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | 550 | One RM | 907 | 498850
DISTRIBUTION BOARDS
16 | Supply and fixing of 20A SP Plug and Socket with 20A SP MCB with SS enclosure including connections for Flush Mounting etc.,complete for AC's. Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. | 10 | Each | 2669 | 26690
17 | Supply and fixing of FP Metal Enclosure with IP 20 Protection DB Make with 1 No 63A, 10 KA DP MCB including internal connection and labour charges for Flush Mounting etc.,complete. Makes of Enclousure : Legrand / Schneider / Siemens / L&T / Crabtree Xpro / ABB / C&S MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. | 10 | Each | 4896 | 48960
18 | Supply and fixing of 4 Way (8+12) TPN DB Horizontal with IP 43 Protection as per IS:13032 with 1 No., of 32A FP MCB 10KA, C/D Curve ISI Mark as incomer and 12 Nos 6-32 A 10KA SP MCBs 10KA, C/D Curve ISI Mark as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. (For Lighting DBs) DB Makes : Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro / ABB / C&S MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. | 8 | Each | 14372 | 114976
19 | Supply and fixing of 4 Way (8+12) TPN DB Horizontal with IP 43 Protection as per IS:13032 with 1 No., of 63A FP MCB 10KA, C/D Curve ISI Mark as incomer and 12 Nos 6-32 A 10 KA SP MCBs 10KA, C/D Curve ISI Mark as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. (For Power DBs& UPS DB's) DB Makes :Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro / ABB / C&S MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. | 8 | Each | 15243 | 121944
20 | Supply and fixing of 8 Way VTPN DB with IP 43 Protection as per IS:13032 with 1 No., of 125A 4P MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted as incomer with 8 Nos of 63A TP MCBs 10KA, C/D Curve ISI Mark as Out goings including internal connections and labour charges for FLUSH Mounting etc., complete. DB Makes :Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. MCCB Makes : L&T- D sine / Schneider-NS NSX / Legrand -DP X3 / Siemens-3V / Hager-h3 / C&S -Winbreak. | 4 | Each | 62982 | 251928
20 | Supply and fixing of cable adopteres box with cover for DBs including, massanory work etc., complete., Makes : Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro | 20 | Each | 600 | 12000
21 | Supply and Installation of 63A 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 KA with thermal magnetic release with suitable SS Enclosure and angle iron frame work on wall / floor including all Labours charges massonry work etc complete with connections. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3VL / Hager-h3/C&S -Winbreak. | 2 | Each | 16538 | 33076
22 | Supply and Installation of 125 Amps 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release with suitable SS Enclosure and angle iron frame work on wall / floor including all Labours charges massonry work etc complete with connections. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3VL / Hager-h3/C&S -Winbreak. | 4 | Each | 25775 | 103100
Earthings
23 | Providing independent earthing for Important equipment with 40mm dia 'B' class 2.5m long G.I pipe and 19mm dia 'B' class G.I pipe of 0.3mtr. long connected with reducer providing G.I funnel with mesh enclosed in C.C/ brick massonry chamber of 450m x 450m x 400mm withR.C.C. Slab cover duly providing staggered holes filling with 20Kg Salt and 40Kg Charcoal or 40Kg bentonite powder from the bottom of the pipe giving earth connection from electrode through G.I strip of 40 x 6mm x 200mm length with all accessories and labour charges complete, as per IS specifications 732/1982 (Part II) | 2 | Each | 6635 | 13270
24 | Providing independent earthing by exacavating a pit to a depth of 2.25Mtr in all soils as per size specified in the data for Sophisticated Electronic equipment with 600mm x 600mm x 3.15mm thick copper plate rigidly fixed to 19mm dia 'B' Class G.I Pipe of 2.5Mtr lengthwith funnel as per National Electric Code and earth connection from electrode GI strip of 40mm x 5mm x 200mm length to be bolted with nut bolts to G.I.pipe including 25mm x 3mm copper strip of 6Mtrs length connected from plate to GI strip including filling with 20Kg Salt and 40Kg Charcoal or 40Kg bentonite powder from the bottom of the pipe and providing CC / Brick massonry chamber 450mmX450mmX400mm and covered with R.C.C. Slab including all accessories and labour charges etc complete as per IS specification 732/1982 (Part II). | 4 | Each | 18940 | 75760
25 | Supply and Run of 25mm x 6mm G.I Strip including cost of all accessories and labour charges etc., complete. | 120 | One RM | 160 | 19200
26 | Supply and Run of 25mm x 3mm copper strip (Cuurrent Carrying Capacity 270A) including cost of all accessories and labour charges etc., complete. | 60 | One RM | 883 | 52980
FIXTURES
27 | Supply, transportation and fixing of 22W +/ 10% , >/ 2300 lumens, 1200mm length LED light housing made with alluminium anodised body, wide operating voltage with PF≥0.9, Surge protection: > 2KV, THD<10%, with inbuilt driver and frosted cover CCT: 3000K - 6500K as desired by the department as per IS, minimum CRI≥80 etc., complete with 5 years warranty with BIS Certification with BIS Certification LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Goldmedal.. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. Make & Model will be Approved by the Head Office / Engineer-in-charge. | 20 | Each | 882 | 17640 | 20
28 | Supply, transportation and fixing 32-36W (>=3240 Lumens) 2' x2' (600mm x 600mm) slim panel Recessed / Surface LED luminaire Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >90 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% with non integrated driver etc., complete with 2 years warranty with BIS Certification. LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Goldmedal.. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. Make & Model will be Approved by the Head Office / Engineer-in-charge. | 80 | Each | 3374 | 269920 | 120
29 | Supply, transportation and fixing of 18 W +/-10% (>= 1800 Lumens) LED Down Light Recessed / Surface mounting round / square with housing made of Powder coated Pressure die cast aluminium housing with extended heat sink, with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor > 0.9, Surge protection: > 2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI >80, and THD is less than 15% etc., complete with 5 years warranty with BIS Certification. LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Goldmedal.. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. Make & Model will be Approved by the Head Office / Engineer-in-charge. | 80 | Each | 1848 | 147840 | 40
30 | Supply, Transportation of energy efficient fan, 1200 mm sweep, aluminium body, consuming 28 W, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) motor, class of insulation: B, 3 no's blades, 30 cm long down rod, 2 no's canopies, shackle'kit, safety rope, copper winding, Power Factor greater than 0.90, Service Value (CMMAV) greater than 8.5, Air delivery minimum 235 CMM, 350 RPM( tolerance as per IS:374-2019), THD less than 10%. with remote or compatible to electronic step type regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise = 75 degree C(max), insulation resistance more than 2 mega ohm, suitable for 230V, 50 HZ, single phase AC supply, earthing etc., including all standard accessories etc., complete. Makes : Atomberg (Efficio ) / Havells / Orient / Halonix | 60 | Each | 3505 | 210300 | 50
31 | Supply and fixing of Modular type Stepped electronic regulator for sweep AC ceiling fans of 1200mm / 1400mm complete with connections. Makes : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Crabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T Englaze. | 60 | Each | 773 | 46380
32 | Labour charges for Fixing of Ceiling fan including giving connections with twin core wire etc., complete. | 60 | Each | 207 | 12420
33 | Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete. | 60 | Each | 175 | 10500
34 | Supply,Transportation of 12" (300mm) ISI, 900 RPM Heavy duty exhaust fan with metallic blades wiremesh with all accessories etc complete. Makes : Crompton / Almounard / Havells Turbo Force. | 10 | Each | 3952 | 39520
35 | Labour charges for fixing of Exhaust fan in wall with necessary connections and masonary work including material of making hole, finishing etc., complete. | 10 | Each | 849 | 8490
36 | Supply and fixing of GI louver shutter including GI mesh to avoid birds entry with necessary materials suitable for 300mm(12 inches) Exhaust fan. | 10 | Each | 205 | 2050
Telephone System
37 | Supply and fixing of Modular telephone Jack with connector on modular box with cover frame in existing consealed pipe wiring including cost and coveyance of all material and all labour charges etc., complete. Makes : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze | 40 | Each | 384 | 15360
38 | Supply, Transportation and Run of 1 of 2 Pair 0.5mm telephone copper cable in the existing conduit pipe and labour charges etc., complete. Makes : Finolex / Delton / Surabi / Polycab. | 1800 | One RM | 28 | 50400
39 | Supply, Transportation and Run of 1 of 20 Pair telephone copper cable in the existing cable tray/ conduit pipe and labour charges etc., complete. Makes :Finolex / Delton / Surabi / Polycab | 250 | One RM | 122 | 30500
40 | Supply, Transportation and Fixing of 100 pair Telephone distribution box with back mount frame, krone connector, powder coated metal body with lock and key arrangement including all accessories and labour charges etc., complete. | 1 | Each | 5507 | 5507
41 | Supply, Installation, Testing and Commissioning of IP Based digtal Telephone (EPABX) system--complied with following specifications: > IP @ Core, PCM/TDM switching, Non blocking, > Must Support PRI, E1, Analog Junctions > Must Support PC Console, > Must support Mobile SIP (Android and I O.S) > Must support Voice Mail > Must support Card based GSM > Inbuilt Call Details Software with search engine software > 8 Analog Trunks > 8 Digital Extensions > 96 Analog Extensions > 1 Digital Key Phone with minimum 16 Keys (Must work only on 2 wires) > Expandable to 220 Ports wired or more at extra cost Approved Brands: NEC/ Alcatel/ Karel / Unify |  | Each | 454460 | 0
LAN
42 | Supply, Transportation and Run of Cat - 6 UTP cable for LAN in the existing conduit pipe and labour charges etc., complete. Makes : D Link / AMP / Molex / Legrand / Krone. | 3400 | One RM | 50 | 170000
43 | Supply, Transportation and Fixing of Cat 6 RJ-45 information outlets including duel face plate with all accessories and labour charges etc., complete. Makes : D Link / AMP / Molex / Legrand / Krone. | 70 | Each | 593 | 41510
44 | Supply, Transportation and Fixing of 24 Port 10 / 100 / 1000 Gigabit Ethernet switches including all accessories and labour charges etc., complete. Makes : Digisol / TP Link / D link. | 4 | Each | 10660 | 42640
45 | Supply, Transportation and Fixing of 24 port patch panels including all accessories and labour charges etc., complete. Makes : D Link / AMP / Molex / Legrand / Krone | 4 | Each | 8123 | 32492
46 | Supply, Transportation and Fixing of 19" 6U Wall mounting net work rack with power spike including all accessories and labour charges etc., complete. Makes : HCL / VAL / Rittal / APW | 1 | Each | 8526 | 8526
CABLE TRAYS PERFORATED
47 | Supply and Installation of 150mm x 50mm x 2mm thick GI perforated cable tray with out cover along with required angle supports, with coupler plates, Anchor bolts and nuts etc complete and the tray should be fitted on the wall / Ceiling etc. complete. Makes: DEC/MNR/ H FAB or equivalent | 50 | ONE MTR | 886 | 44300
48 | Supply and Installation of 300mm x 50mm x 2mm thick GI perforated cable tray with out cover along with required angle supports, with coupler plates, Anchor bolts and nuts etc complete and the tray should be fitted on the wall / Ceiling etc. complete. Makes: DEC/MNR/ H FAB or equivalent | 100 | ONE MTR | 1227 | 122700
#REF! | Supply , fabrication and transportation of MS channel iron/ angle iron /flats including two coats of aluminium paint and one coat of red oxide paint including all labour charges etc complete. | 150 | 1KG | 142 | 21300
Lighting Panel
#REF! | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor Type MV panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Alluminium busbar ( with rating of 0.8A/ Sqmm)supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, flexibiltioy to accept the up four out going cables and necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges. | 1 | Each | 282182 | 282182
Incomer: Supply of 160A 4-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 kA with thermal magnetic release Panel Mounted-1 No Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH
Outgoing: Supply of 125 A 3-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 kA with thermal magnetic release Panel Mounted-6 Nos Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH
Supply of 63 A 3-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 kA with thermal magnetic release Panel Mounted-4 Nos Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH
0-415V volt Digital meter of size 96x96mm on exisiting box / panel board including connections etc., complete of CONZERVE / ELMEASURE / MECO / HPL MAKE. - 1 No.
0-100 / 200 / 400 / 600 /1000 - 5A CT Digital Ammeter of size 96x96mm on existing box / panel board including connections etc., complete of CONZERVE / ELMEASURE / MECO / HPL MAKE. - 1 No.
Analog selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete. L&T / C&S / SALZAR / HPL MAKE. - 2 Nos
Analog LED indicator lamps on the existing box / panel board.L&T / C&S / SALZAR / HPL MAKE. - 3 Nos.
32A fuse bases with 2A control fuses. Makes : C&S / GM / Million / Gold Medal-3 Nos
Analog LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete. KAPPA MAKE. - 3 Nos.
Labour charges etc complete with connections for Finished item of work.
Power Panel
#REF! | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor Type MV panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Alluminium busbar ( with rating of 0.8A/ Sqmm)supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, flexibiltioy to accept the up four out going cables and necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges. | 1 | Each | 374911 | 374911
Incomer: Supply of 250A 4-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 36 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH
Outgoings: Supply of 160A 3-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH -4 Nos
Supply of 125 A 3-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH- 4Nos
63A / 60A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 KA with thermal magnetic release Panel Mounted.- 6 Nos. Makes : L&T- D shine / Schneider-NS NSX / Legrand -DP X3 / Siemens-3VL / Hagerh3 / C&S -Winbreak - 6 Nos
0-415V volt Digital meter of size 96x96mm on exisiting box / panel board including connections etc., complete of CONZERVE / ELMEASURE / MECO / HPL MAKE. - 1 No.
0-100 / 200 / 400 / 600 /1000 - 5A CT Digital Ammeter of size 96x96mm on existing box / panel board including connections etc., complete of CONZERVE / ELMEASURE / MECO / HPL MAKE. - 1 No.
Analog selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete. L&T / C&S / SALZAR / HPL MAKE. - 2 Nos
Analog LED indicator lamps on the existing box / panel board.L&T / C&S / SALZAR / HPL MAKE. - 3 Nos.
32A fuse bases with 2A control fuses. Makes : C&S / GM / Million / Gold Medal-3 Nos
Analog LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete. KAPPA MAKE. - 3 Nos.
Labour charges etc complete with connections for Finished item of work.
UG Cable
#REF! | Supply of the Following XLPE insulated, 1100V grade armoured alluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) Makes : Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / RR kable / Finecab / RPG.
c | 50 Sqmm 3.5 Core | 125 | One RM | 648 | 81000
d | 70 Sqmm 3.5 Core | 125 | One RM | 830 | 103750
LT Cable laying
#REF! | Earth work excavation of Trench in hard ground soil and Sand filling shall be provided at the bottom of trench before laying the cable and laying of U.G cables from 95 Sqmm up to 400 sqmm covering the cable with bricks and back filling of Trench duly providing route indicator at every 8 Mtrs distance embedded in C.C including cost and conveyance of materials and labour charges etc., complete. | 10 | One RM | 378 | 3780
#REF! | Laying of PVC armoured under ground cable up to 70 Sqmm fixing on chromium plated metallic base saddles on wall / Cable tray as per IS 1255 and as directed by the department including cost and conveyance of all materials and labour charges etc., complete. | 390 | One RM | 55 | 21450
LT Cable terminations
#REF! | Providing Termination for UG cables for following XLPE insulated armoured cable with fixing of heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket, with required lugs etc complete. Makes: SMI / Commet / Dowels.
c | 50 Sqmm 3.5 Core | 4 | Each | 1071 | 4284
d | 70 Sqmm 3.5 Core | 4 | Each | 1542 | 6168
| Electrical Total : |  |  |  | 5860754

## EST-BH
ELECTRICAL ESTIMATE
NAME OF THE WORK : CONSTRUCTION OF BOYS HOSTEL & FEMALE INTERNS HOSTEL AT OSMANIA MEDICAL COLLEGE
SUB ESTIMATE : PROPOSED BOYS HOSTEL 200 CAPACITY OVER CENTRAL LIBRARY BUILDING (G+4)
Sl. No. | Description of Work | Quantity | Unit | Rate (in Rs.) | Amount (in Rs.)
1 | Supply and Laying of ISI 25mm outer dia heavy grade with IS:9537 part 3 rigid PVC pipe concealed in Roof Slabs with all required PVC / Metallic Deep Boxes including masonary work and labour charges etc., complete. Makes : Sudhakar / Finolex / Modi / VIP / Precision / Universal / Million Plast / Gold / Polycab / DEC | 9677.25 | ONE RM | 102 | 987079.5
2 | Supply and laying of ISI 25mm outer dia medium grade, with IS:9537 part 3 rigid PVC concealed in wall with all required PVC / Metallic Junction Boxes including masonary work and labour charges etc., Makes:- Sudhakar / Finolex / Modi / VIP / Precision / Universal / Million Plast / Gold / Polycab / DEC. | 6451.5 | ONE RM | 107 | 690310.5
3 | Supply and erecting PVC / GI / MS Galvanished fan hook box with hook in RCC slab including all Labour charges etc., complete. | 215 | EACH | 158 | 33970
WIRING
4 | Wiring with run of 2 of 1.5 Sqmm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specification for Copper cable. in existing PVC conduit pipe including Supply and fixing of Jumbo Ceiling rose and 6A/10A ISI Mark 1way Modular switch with required modular box and cover frame in existing Surface or Concealed pipe wiring including cost and conveyance of all material and all labour charges etc., complete for light, Fan, Exhaust fan and bell points in R.B. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | 805 | EACH POINT | 935 | 752675
5 | Wiring with run of 2 of 1.5 Sqmm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specification for Copper cable. in existing PVC conduit pipe including Supply and fixing of Jumbo Ceiling rose and 6A/10A ISI Mark 1way Modular switch with required modular box and cover frame in existing Surface or Concealed pipe wiring including cost and conveyance of all material and all labour charges etc., complete for staircase light points in N.R.B. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | 18 | EACH POINT | 1403 | 25254
6 | Supply and fixing of 10A 3/2 Pin 2 Module Modular Socket with shutter with 6 / 10A 1 Way 1 Module Modular Switch, 3 Module box with cover frame in Common switch board including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B. Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | 110 | Each | 716 | 78760
7 | Supply and fixing of 6 / 10A 1 Way 1 Module Modular Switches - 2 Nos and 10A 3/2 Pin 2 Module Modular Socket with shutter - 2 Nos Modular type with cover plate and GI switch box fixing on separate board including all labour charges etc., complete. Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | 15 | Each | 1301 | 19515
8 | Supply and fixing of 16A / 6A 2 Module Combi Socket Modular Socket with shutter with 16A/20A 1 Way 1 Module Modular Switch fixed on suitable size Modular box with required cover frame including with connections, cost and conveyance of all material and all labour charges etc., complete Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | 20 | Each | 846 | 16920
9 | Supply and fixing of following switches and sockets modular type on suitable size Modular deep box with cover frame including cost and coveyance of all material and all labour charges etc., complete with following configurations 1) 16A / 6A 2 Module Combi Socket Modular Socket with shutter - 1 No 2) 16A/20A 1 Way 1 Module Modular Switch. - 1 No 3) 10A 3/2 Pin 2 Module Modular Socket with shutter - 1 Nos. 4) 6 / 10A 1 Way 1 Module Modular Switch – 1 Nos. including cost and coveyance of all material and all labour charges etc., complete for Computer, LAB and OTs Use Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | 0 | Each | 1432 | 0
10 | Supply and fixing of following switches and sockets modular type on suitable size Modular deep box with cover frame including cost and coveyance of all material and all labour charges etc., complete with following configurations. 1) 16A / 6A 2 Module Combi Socket Modular Socket with shutter - 2 Nos 2) 16A/20A 1 Way 1 Module Modular Switch. - 2 Nos 3) 10A 3/2 Pin 2 Module Modular Socket with shutter - 2 Nos. 4) 6 / 10A 1 Way 1 Module Modular Switch - 2 Nos. including cost and coveyance of all material and all labour charges etc., complete for LAB,ICU's and OTs Use Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | 0 | Each | 2846 | 0
RUN of MAINS
11 | Supply and Run of 1 of 1.5 sq.mm (Earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specification for Copper cable. specifications for Copper cable in the existing conduict pipe for earth continuity inlcuding all labour charges etc., complete. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | 780 | One RM | 37 | 28860
12 | Supply and Run of 3 of 2.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable of in existing conduit pipe for individual lighting circuits including labour charges etc., complete as required for switch boards. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | 5590.625 | One RM | 166 | 928043.75
13 | Supply and Run of 3 of 4.0 sq mm (phase neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable of in existing pipe for power points and AC Sockets inlcuding all labour charges etc., complete. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | 300 | One RM | 239 | 71700
14 | Supply and Run of 3 of 6.0 sq mm (phase neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable of in existing pipe for SPNDB's incoming inlcuding all labour charges etc., complete. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | 125 | One RM | 336 | 42000
15 | Supply and Run of 5 of 6.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable in the existing conduict pipe for run of mains from VTPN / Panel Board to TPN DB"s with pin type lugs and connections etc., complete. [for LDBs & 4P MCB's ] Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | 450 | One RM | 568 | 255600
16 | Supply and Run of 5 of 10.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable in the existing conduict pipe for run of mains from VTPN / Panel Board to TPN DB"s with pin type lugs and connections etc., complete. [for PDBs] Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | 300 | One RM | 907 | 272100
DISTRIBUTION BOARDS
17 | Supply and fixing of 20A SP Plug and Socket with 20A SP MCB with SS enclosure including connections for Flush Mounting etc.,complete for AC's. Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. | 5 | Each | 2669 | 13345
18 | Supply and fixing of FP Metal Enclosure with IP 20 Protection DB Make with 1 No 63A, 10 KA DP MCB including internal connection and labour charges for Flush Mounting etc.,complete. Makes of Enclousure : Legrand / Schneider / Siemens / L&T / Crabtree Xpro / ABB / C&S MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. | 5 | Each | 4896 | 24480
19 | Supply and fixing of 8 Way SPN DB with IP 43 Protection as per IS:13032 with 1 No 40A DP MCB as Incommer, and 6 Nos of 20A SP MCB 10KA, C/D Curve ISI Mark as out goings, concealing in wall etc complete. DB Makes : Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro / ABB / C&S MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. | 3 | Each | 8487 | 25461
20 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 with 1 No., of 32A FP MCB 10KA, C/D Curve ISI Mark as incomer and 12 Nos 6-32 A 10KA SP MCBs 10KA, C/D Curve ISI Mark as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. (For Lighting DBs) DB Makes : Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro / ABB / C&S MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. | 10 | Each | 14372 | 143720
21 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 with 1 No., of 63A FP MCB 10KA, C/D Curve ISI Mark as incomer and 12 Nos 6-32 A 10 KA SP MCBs 10KA, C/D Curve ISI Mark as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. (For Power DBs& UPS DB's) DB Makes :Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro / ABB / C&S MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. | 10 | Each | 15243 | 152430
22 | Supply and fixing of 4 Way VTPN DB with IP 43 Protection as per IS:13032 with 1 No., of 125A 4P MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted as incomer with 8 Nos of 63A TP MCBs 10KA, C/D Curve ISI Mark as Out goings including internal connections and labour charges for FLUSH Mounting etc., complete. DB Makes :Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. MCCB Makes : L&T- D sine / Schneider-NS NSX / Legrand -DP X3 / Siemens-3V / Hager-h3 / C&S -Winbreak. | 8 | Each | 47564 | 380512
23 | Supply and fixing of 8 Way VTPN DB with IP 43 Protection as per IS:13032 with 1 No., of 125A 4P MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted as incomer with 8 Nos of 63A TP MCBs 10KA, C/D Curve ISI Mark as Out goings including internal connections and labour charges for FLUSH Mounting etc., complete. DB Makes :Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. MCCB Makes : L&T- D sine / Schneider-NS NSX / Legrand -DP X3 / Siemens-3V / Hager-h3 / C&S -Winbreak. | 2 | Each | 62982 | 125964
23 | Supply and fixing of cable adopteres box with cover for DBs including, massanory work etc., complete., Makes : Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro | 31 | Each | 600 | 18600
24 | Supply and Installation of 63A 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 KA with thermal magnetic release with suitable SS Enclosure and angle iron frame work on wall / floor including all Labours charges massonry work etc complete with connections. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3VL / Hager-h3/C&S -Winbreak. | 0 | Each | 16538 | 0
25 | Supply and Installation of 125 Amps 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release with suitable SS Enclosure and angle iron frame work on wall / floor including all Labours charges massonry work etc complete with connections. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3VL / Hager-h3/C&S -Winbreak. | 0 | Each | 25775 | 0
26 | Supply and Installation of 250 Amps 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release with suitable SS Enclosure and angle iron frame work on wall / floor including all Labours charges massonry work etc complete with connections. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3VL / Hager-h3/C&S -Winbreak. | 0 | Each | 52546 | 0
Earthings
27 | Providing independent earthing for Important equipment with 40mm dia 'B' class 2.5m long G.I pipe and 19mm dia 'B' class G.I pipe of 0.3mtr. long connected with reducer providing G.I funnel with mesh enclosed in C.C/ brick massonry chamber of 450m x 450m x 400mm withR.C.C. Slab cover duly providing staggered holes filling with 20Kg Salt and 40Kg Charcoal or 40Kg bentonite powder from the bottom of the pipe giving earth connection from electrode through G.I strip of 40 x 6mm x 200mm length with all accessories and labour charges complete, as per IS specifications 732/1982 (Part II) | 4 | Each | 6635 | 26540
28 | Providing independent earthing by exacavating a pit to a depth of 2.25Mtr in all soils as per size specified in the data for Sophisticated Electronic equipment with 600mm x 600mm x 3.15mm thick copper plate rigidly fixed to 19mm dia 'B' Class G.I Pipe of 2.5Mtr lengthwith funnel as per National Electric Code and earth connection from electrode GI strip of 40mm x 5mm x 200mm length to be bolted with nut bolts to G.I.pipe including 25mm x 3mm copper strip of 6Mtrs length connected from plate to GI strip including filling with 20Kg Salt and 40Kg Charcoal or 40Kg bentonite powder from the bottom of the pipe and providing CC / Brick massonry chamber 450mmX450mmX400mm and covered with R.C.C. Slab including all accessories and labour charges etc complete as per IS specification 732/1982 (Part II). | 4 | Each | 18940 | 75760
29 | Supply and Run of 25mm x 6mm G.I Strip including cost of all accessories and labour charges etc., complete. | 150 | One RM | 160 | 24000
30 | Supply and Run of 50mm x 6mm G.I Strip including cost of all accessories and labour charges etc., complete. | 150 | One RM | 322 | 48300
31 | Supply and Run of 25mm x 3mm copper strip (Cuurrent Carrying Capacity 270A) including cost of all accessories and labour charges etc., complete. | 150 | One RM | 883 | 132450
32 | Supply and run of No. 8SWG GI wire including cost of all accessories and labour charges etc complete. | 250 | One RM | 27 | 6750
FIXTURES
33 | Supply, transportation and fixing of 22W +/ 10% , >/ 2300 lumens, 1200mm length LED light housing made with alluminium anodised body, wide operating voltage with PF≥0.9, Surge protection: > 2KV, THD<10%, with inbuilt driver and frosted cover CCT: 3000K - 6500K as desired by the department as per IS, minimum CRI≥80 etc., complete with 5 years warranty with BIS Certification with BIS Certification LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Goldmedal.. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. Make & Model will be Approved by the Head Office / Engineer-in-charge. | 410 | Each | 882 | 361620
34 | Supply, transportation and fixing 32-36W (>=3240 Lumens) 2' x2' (600mm x 600mm) slim panel Recessed / Surface LED luminaire Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >90 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% with non integrated driver etc., complete with 2 years warranty with BIS Certification. LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Goldmedal.. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. Make & Model will be Approved by the Head Office / Engineer-in-charge. | 0 | Each | 3374 | 0
35 | Supply, transportation and fixing of 18 W +/-10% (>= 1800 Lumens) LED Down Light Recessed / Surface mounting round / square with housing made of Powder coated Pressure die cast aluminium housing with extended heat sink, with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor > 0.9, Surge protection: > 2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI >80, and THD is less than 15% etc., complete with 5 years warranty with BIS Certification. LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Goldmedal.. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. Make & Model will be Approved by the Head Office / Engineer-in-charge. | 0 | Each | 1848 | 0
36 | Supply, Transportation and fixing of 60 W +/-10% (>6000 Lumens) LED HIgh Bay Luminaire with high power COB LED made of pressure diecast alluminium housing with powder coated,Supply Input voltage 120 - 270 V AC, P.F > 0.90, high power LED's, System efficacy >100 lm / W and junction temprature < 70°C, with Ingrees protection IP65, IK05, Driver surge protection 4KV, external Surge protection ≥ 5KV with wide/ Narrow beam optics, THD<10% at 110 Volts AC, driver efficiency >90%, CCT: 3000K - 5700K, minimum CRI>70, etc., with required wiring complete with BIS certification with warranty 5 years warranty. The contractor has to furnish the manufacturer warranty letter, LM 79 and LM 80 certificates. LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Goldmedal.. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. | 10 | Each | 8712 | 87120
37 | Supply, transportation and fixing ISI mark batten holder / slanting holder Makes : Anchor / Gold Medal Olive / Million Zoom in lieu of ceiling rose of light point complete with all connections and all labour charges with 5W LED Lamp. LED Lamp MAKES: Phillips / OSRAM / Crompton / Eveready / Bajaj / Havells / Halonix / Jaquar / C&S / GM / / Gold Medal / Million. | 100 | Each | 150 | 15000
38 | Supply, Transportation of energy efficient fan, 1200 mm sweep, aluminium body, consuming 28 W, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) motor, class of insulation: B, 3 no's blades, 30 cm long down rod, 2 no's canopies, shackle'kit, safety rope, copper winding, Power Factor greater than 0.90, Service Value (CMMAV) greater than 8.5, Air delivery minimum 235 CMM, 350 RPM( tolerance as per IS:374-2019), THD less than 10%. with remote or compatible to electronic step type regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise = 75 degree C(max), insulation resistance more than 2 mega ohm, suitable for 230V, 50 HZ, single phase AC supply, earthing etc., including all standard accessories etc., complete. Makes : Atomberg (Efficio ) / Havells / Orient / Halonix | 215 | Each | 3505 | 753575
39 | Supply and fixing of Modular type Stepped electronic regulator for sweep AC ceiling fans of 1200mm / 1400mm complete with connections. Makes : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Crabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T Englaze. | 215 | Each | 773 | 166195
40 | Labour charges for Fixing of Ceiling fan including giving connections with twin core wire etc., complete. | 215 | Each | 207 | 44505
41 | Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete. | 215 | Each | 175 | 37625
42 | Supply,Transportation of light duty exhaust fan 12"(300 mm) size 900 rpm with metal blades wiremesh with all accessories etc complete. Makes : Crompton / Havells Ventil Air-DB / Orient hill air. | 20 | Each | 2005 | 40100
43 | Supply,Transportation of 12" (300mm) ISI, 900 RPM Heavy duty exhaust fan with metallic blades wiremesh with all accessories etc complete. Makes : Crompton / Almounard / Havells Turbo Force. | 25 | Each | 3952 | 98800
44 | Labour charges for fixing of Exhaust fan in wall with necessary connections and masonary work including material of making hole, finishing etc., complete. | 45 | Each | 849 | 38205
45 | Supply and fixing of GI louver shutter including GI mesh to avoid birds entry with necessary materials suitable for 300mm(12 inches) Exhaust fan. | 45 | Each | 205 | 9225
Telephone System
46 | Supply and fixing of Modular telephone Jack with connector on modular box with cover frame in existing consealed pipe wiring including cost and coveyance of all material and all labour charges etc., complete. Makes : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze | 2 | Each | 384 | 768
47 | Supply, Transportation and Run of 1 of 2 Pair 0.5mm telephone copper cable in the existing conduit pipe and labour charges etc., complete. Makes : Finolex / Delton / Surabi / Polycab. | 70 | One RM | 28 | 1960
48 | Supply, Transportation and Run of 1 of 20 Pair telephone copper cable in the existing cable tray/ conduit pipe and labour charges etc., complete. Makes :Finolex / Delton / Surabi / Polycab | 35 | One RM | 122 | 4270
49 | Supply, Transportation and Fixing of 20 pair Telephone distribution box with back mount frame, krone connector, powder coated metal body with lock and key arrangement including all accessories and labour charges etc., complete. | 1 | Each | 1566 | 1566
50 | Supply, Transportation and Fixing of 100 pair Telephone distribution box with back mount frame, krone connector, powder coated metal body with lock and key arrangement including all accessories and labour charges etc., complete. | 0 | Each | 5507 | 0
51 | Supply, Installation, Testing and Commissioning of IP Based digtal Telephone (EPABX) system--complied with following specifications: > IP @ Core, PCM/TDM switching, Non blocking, > Must Support PRI, E1, Analog Junctions > Must Support PC Console, > Must support Mobile SIP (Android and I O.S) > Must support Voice Mail > Must support Card based GSM > Inbuilt Call Details Software with search engine software > 8 Analog Trunks > 8 Digital Extensions > 96 Analog Extensions > 1 Digital Key Phone with minimum 16 Keys (Must work only on 2 wires) > Expandable to 220 Ports wired or more at extra cost Approved Brands: NEC/ Alcatel/ Karel / Unify | 0 | Each | 454460 | 0
LAN
52 | Supply, Transportation and Run of Cat - 6 UTP cable for LAN in the existing conduit pipe and labour charges etc., complete. Makes : D Link / AMP / Molex / Legrand / Krone. | 70 | One RM | 50 | 3500
53 | Supply, Transportation and Fixing of Cat 6 RJ-45 information outlets including duel face plate with all accessories and labour charges etc., complete. Makes : D Link / AMP / Molex / Legrand / Krone. | 2 | Each | 593 | 1186
54 | Supply, Transportation and Fixing of 24 Port 10 / 100 / 1000 Gigabit Ethernet switches including all accessories and labour charges etc., complete. Makes : Digisol / TP Link / D link. | 1 | Each | 10660 | 10660
55 | Supply, Transportation and Fixing of 24 port patch panels including all accessories and labour charges etc., complete. Makes : D Link / AMP / Molex / Legrand / Krone | 1 | Each | 8123 | 8123
56 | Supply, Transportation and Fixing of 19" 6U Wall mounting net work rack with power spike including all accessories and labour charges etc., complete. Makes : HCL / VAL / Rittal / APW | 1 | Each | 8526 | 8526
Air Conditioners
57 | Supply, transportation and installation of split AC unit with high wall mounted 100% copper indoor unit and outdoor condencing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.0 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord (Voltage range 160- 264 volts) and cordless remote control with 5 years warranty compressor and comprehensive maintenance for 2 years.
a) | 1.5 TR 3 Star capable of delivering 18000 BTU/hr Makes: Carrier / Daikin / Blue Star / Hitachi. | 2 | Each | 44878 | 89756
b) | 2.0 / 1.8 TR 3 Star capable of delivering 21600 BTU/hr and above Makes: Daikin / Thoshiba / O General / Carrier / Blue Star / Hitachi | 2 | Each | 55308 | 110616
58 | Supply and erecting fully automatic line voltage stabilizer for operation on input voltage 200 to 250V. rated for 4 KVA maximum load and time delay model with Volt meter, selector switch, 6A / 16A flush type, 5 pin socket for out put and with 3 core flexible chord and 3 pin 6/16A plug top suitable for AC for continuous operation including cost and conveyance of all mateials and all labour charges etc., complete. Makes : V-Guard / Real Guard / Uni Stab / ITL. | 2 | Each | 3665 | 7330
59 | Supply and erecting fully automatic line voltage stabilizer for operation on input voltage 200 to 250V. rated for 5 KVA maximum load and time delay model with Volt meter, selector switch, 6A / 16A flush type, 5 pin socket for out put and with 3 core flexible chord and 3 pin 6/16A plug top suitable for AC for continuous operation including cost and conveyance of all mateials and all labour charges etc., complete. Makes : V-Guard / Real Guard / Uni Stab / ITL. | 2 | Each | 4372 | 8744
CABLE TRAYS PERFORATED
60 | Supply and Installation of 100mm x 25mm x 2mm thick GI perforated cable tray with out cover along with required angle supports, with coupler plates, Anchor bolts and nuts etc complete and the tray should be fitted on the wall / Ceiling etc. complete. Makes: DEC/MNR/ H FAB or equivalent | 0 | ONE MTR | 517 | 0
61 | Supply and Installation of 150mm x 50mm x 2mm thick GI perforated cable tray with out cover along with required angle supports, with coupler plates, Anchor bolts and nuts etc complete and the tray should be fitted on the wall / Ceiling etc. complete. Makes: DEC/MNR/ H FAB or equivalent | 50 | ONE MTR | 886 | 44300
62 | Supply and Installation of 300mm x 50mm x 2mm thick GI perforated cable tray with out cover along with required angle supports, with coupler plates, Anchor bolts and nuts etc complete and the tray should be fitted on the wall / Ceiling etc. complete. Makes: DEC/MNR/ H FAB or equivalent | 100 | ONE MTR | 1227 | 122700
63 | Supply and Installation of 450mm x 50mm x 2mm thick GI perforated cable tray with out cover along with required angle supports, with coupler plates, Anchor bolts and nuts etc complete and the tray should be fitted on the wall / Ceiling etc. complete. Makes: DEC/MNR/ H FAB or equivalent | 0 | ONE MTR | 1454 | 0
64 | Supply, Transportation and Installation of 600mm x 75mm x 2mm thick GI Ladder type cable tray along with required coupler plates, T's, Bends, Reducers, Anchor bolts, nuts, washers and slotted channels / Angle Iron Channels etc complete and the tray should be fitted on the wall / Ceiling etc. complete for finished item of work. Makes: DEC/MNR/ H FAB or | 0 | ONE MTR | 2227 | 0
65 | Supply , fabrication and transportation of MS channel iron/ angle iron /flats including two coats of aluminium paint and one coat of red oxide paint including all labour charges etc complete. | 200 | 1KG | 142 | 28400
Lighting Panel
66 | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor Type MV panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Alluminium busbar ( with rating of 0.8A/ Sqmm)supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, flexibiltioy to accept the up four out going cables and necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges. | 1 | Each | 282182 | 282182
Incomer: Supply of 160A 4-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 kA with thermal magnetic release Panel Mounted-1 No Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH
Outgoing: Supply of 125 A 3-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 kA with thermal magnetic release Panel Mounted-6 Nos Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH
Supply of 63 A 3-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 kA with thermal magnetic release Panel Mounted-4 Nos Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH
0-415V volt Digital meter of size 96x96mm on exisiting box / panel board including connections etc., complete of CONZERVE / ELMEASURE / MECO / HPL MAKE. - 1 No.
0-100 / 200 / 400 / 600 /1000 - 5A CT Digital Ammeter of size 96x96mm on existing box / panel board including connections etc., complete of CONZERVE / ELMEASURE / MECO / HPL MAKE. - 1 No.
Analog selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete. L&T / C&S / SALZAR / HPL MAKE. - 2 Nos
Analog LED indicator lamps on the existing box / panel board.L&T / C&S / SALZAR / HPL MAKE. - 3 Nos.
32A fuse bases with 2A control fuses. Makes : C&S / GM / Million / Gold Medal-3 Nos
Analog LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete. KAPPA MAKE. - 3 Nos.
Labour charges etc complete with connections for Finished item of work.
Power Panel
67 | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor Type MV panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Alluminium busbar ( with rating of 0.8A/ Sqmm)supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, flexibiltioy to accept the up four out going cables and necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges. | 1 | Each | 374911 | 374911
Incomer: Supply of 250A 4-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 36 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH
Outgoings: Supply of 160A 3-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH -4 Nos
Supply of 125 A 3-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH- 4Nos
63A / 60A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 KA with thermal magnetic release Panel Mounted.- 6 Nos. Makes : L&T- D shine / Schneider-NS NSX / Legrand -DP X3 / Siemens-3VL / Hagerh3 / C&S -Winbreak - 6 Nos
0-415V volt Digital meter of size 96x96mm on exisiting box / panel board including connections etc., complete of CONZERVE / ELMEASURE / MECO / HPL MAKE. - 1 No.
0-100 / 200 / 400 / 600 /1000 - 5A CT Digital Ammeter of size 96x96mm on existing box / panel board including connections etc., complete of CONZERVE / ELMEASURE / MECO / HPL MAKE. - 1 No.
Analog selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete. L&T / C&S / SALZAR / HPL MAKE. - 2 Nos
Analog LED indicator lamps on the existing box / panel board.L&T / C&S / SALZAR / HPL MAKE. - 3 Nos.
32A fuse bases with 2A control fuses. Makes : C&S / GM / Million / Gold Medal-3 Nos
Analog LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete. KAPPA MAKE. - 3 Nos.
Labour charges etc complete with connections for Finished item of work.
UG Cable
68 | Supply of the Following XLPE insulated, 1100V grade armoured alluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) Makes : Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / RR kable / Finecab / RPG.
a | 16 Sqmm 4 Core | 50 | One RM | 319 | 15950
b | 35 Sqmm 3.5 Core | 100 | One RM | 489 | 48900
c | 50 Sqmm 3.5 Core | 100 | One RM | 648 | 64800
d | 70 Sqmm 3.5 Core | 80 | One RM | 830 | 66400
e | 95 Sqmm 3.5 Core | 0 | One RM | 1080 | 0
f | 120 Sqmm 3.5 Core | 0 | One RM | 1330 | 0
g | 185 Sqmm 3.5 Core | 0 | One RM | 1841 | 0
h | 240 Sqmm 3.5 Core | 0 | One RM | 2341 | 0
i | 300 Sqmm 3.5 Core | 0 | One RM | 2852 | 0
LT Cable laying
69 | Earth work excavation of Trench in hard ground soil and Sand filling shall be provided at the bottom of trench before laying the cable and laying of U.G cables from 95 Sqmm up to 400 sqmm covering the cable with bricks and back filling of Trench duly providing route indicator at every 8 Mtrs distance embedded in C.C including cost and conveyance of materials and labour charges etc., complete. | 50 | One RM | 378 | 18900
70 | Earth work excavation of Trench in hard ground soil and Sand filling shall be provided at the bottom of trench before laying the cable and laying of U.G cables up to 70 sqmm covering the cable with back filling of Trench duly providing route indicator embedded in C.C including cost and conveyance of materials and labour charges etc., complete. | 50 | One RM | 365 | 18250
71 | Laying of PVC armoured under ground cable from 95 Sq.mm to 400 Sqmm fixing on chromium plated metallic base saddles on wall / cable tray as per IS 1255 and as directed by the department including cost and conveyance of all materials and labour charges etc., complete. | 50 | One RM | 66 | 3300
72 | Laying of PVC armoured under ground cable up to 70 Sqmm fixing on chromium plated metallic base saddles on wall / Cable tray as per IS 1255 and as directed by the department including cost and conveyance of all materials and labour charges etc., complete. | 50 | One RM | 55 | 2750
LT Cable terminations
73 | Providing Termination for UG cables for following XLPE insulated armoured cable with fixing of heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket, with required lugs etc complete. Makes: SMI / Commet / Dowels.
a | 16 Sqmm 4 Core | 12 | Each | 692 | 8304
b | 35 Sqmm 3.5 Core | 12 | Each | 861 | 10332
c | 50 Sqmm 3.5 Core | 12 | Each | 1071 | 12852
d | 70 Sqmm 3.5 Core | 10 | Each | 1542 | 15420
e | 95 Sqmm 3.5 Core | 0 | Each | 1637 | 0
f | 120 Sqmm 3.5 Core | 0 | Each | 2164 | 0
g | 185 Sqmm 3.5 Core | 0 | Each | 2889 | 0
h | 240 Sqmm 3.5 Core | 0 | Each | 3616 | 0
i | 300 Sqmm 3.5 Core | 0 | Each | 4287 | 0
Safety equipments
74 | Supply of Rubber hand gloves suitable for 11 KV. | 4 | Each Pair | 2272 | 9088
75 | Supply and fixing of PVC synthetic elastomer electrically insulated mat with Class B insulation conforming to IS: 15652-2006 having 2.5mm thickness upto 11KV. | 0 | One Sqmtr | 5643 | 0
76 | Providing & Fixing of Shock instrution chart in English / Hindi / Telugu duly framed with front glass. | 0 | Each | 654 | 0
77 | Providing & Fixing of Danger Notice Plates of size 250x200mm, shall comply with IS:2551-1982. | 0 | Each | 325 | 0
78 | Providing floor mounting stand for keeping 4No of fire bucket 1500mm length, 900mm height made out of 40x40x6mm angle iron welded with 4 hooks and duly painted with one coat of red lead and two coats of enamel paint. | 0 | Each | 1593 | 0
79 | Providing & Supply of round bottom G.I sheet bucket of 9 Ltrs. Capacity as per IS:2546 made out of 24 gauge GI sheet with extra handle at bottom duly painted inside and red out side with printed with FIRE Mark for stand and hook and filled with sand and arranged to existing stand or hook. | 2 | Each | 391 | 782
80 | First Aid box 18" x 12" x 8" containing material as prescribed by St. John Ambulance brigade OR Indian Red Cross complete as required. | 0 | Each | 1718 | 0
81 | Preparation of Drawings of existing or new installations and obtaining approval from the CEIG complete as per the requirement at site. | 0 | Each | 40000 | 0
82 | Supply, transportation, installation, testing and commissioning of 8 passenger Gearless & Machine Room less elevator with following specifications with connected minor civil works required for installation of Lift including all accessories, scoffolding, requried channels, loading and unloading of materials etc, including comprehensive maintenance of lifts during the defect liability period. Makes: Schindler / Kone / OTIS / Mitsubishi or equivalent. Make & Model will be Approved by the Head Office / Engineer-in-charge. | 1 | Each | 1831133 | 1831133
Specifications: a) Type: Machine room less b) Pit Depth: 1500 mm or as per NBC c) Minimum Floor to Floor Height (Required): As per Standard d) Travel height: 3.6 to 4.0mtrs e) Head room Height: 4.5mtrs f) Lintel Height (Required) : 2240mm from finished floor level +/- 10% g) Number of persons : 8 Persons
h) Rated Load: 544 Kgs i) Number of Stops: 5 stops j) Number of Access sides : 1 k) Floor Designations : G, 1, 2, 3,4.
l) Drive Sytem : Alternating current, Voltage Frequency Drive (ACVF). m) Type of Controller : Fully collective control - Simplex / Duplex as per the site condition. n) Speed of Travel : 1.0 Mtr / Sec o) Car size : As per Standard p) Door width : 800/ 900/1000mm or As per Standard q) Door Height : 2000 mm or as per standard r) Rated output motor : as per standard s) Car Design : Car walls finish in Stainless stell hairline finish LED spot in ceiling. t) Car Doors : stainless steel hairline finish. Granite Flooring finish in Black sea. Deco ceiling finish in stainless steel Hairline. Full Height mirror on rear car panel.
u) Car Operating Panel : Mechanical push button.Door open/close and alarm buttons / Touch panel or equivalent, Visual call confirmation, Car position Indicator, Preannouncing arrows for collective controls, 16 Segment display v) Landing Doors : Fully automatic landing doors with stainless steel hairline finish. Center Opening or Side Opening as per the site condition
w) Special Features : 1.Closed loop control system 2.Self Diagnostic control 3.Overload detection 4.Automatic evacuation to nearest floor(ARD) 5.Light curtain on car entrance 6.Alarm Horn 7.Fire Switch 8.Handrail in stainless steel finish on rear wall 9.Auto Fan off 10.Auto light off 11.Intercom-3way
| Electrical Total : |  |  |  | 10289728.75

## Sr.HST
ELECTRICAL ESTIMATE
NAME OF THE WORK : CONSTRUCTION OF BOYS HOSTEL & FEMALE INTERNS HOSTEL AT OSMANIA MEDICAL COLLEGE
SUB ESTIMATE : PROPOSED SR. RESIDENTS HOSTEL (G+9)
Sl. No. | Description of Work | Quantity | Unit | Rate (in Rs.) | Amount (in Rs.)
1 | Supply and Laying of ISI 25mm outer dia heavy grade with IS:9537 part 3 rigid PVC pipe concealed in Roof Slabs with all required PVC / Metallic Deep Boxes including masonary work and labour charges etc., complete. Makes : Sudhakar / Finolex / Modi / VIP / Precision / Universal / Million Plast / Gold / Polycab / DEC | 5933.25 | ONE RM | 102 | 605191.5
2 | Supply and laying of ISI 25mm outer dia medium grade, with IS:9537 part 3 rigid PVC concealed in wall with all required PVC / Metallic Junction Boxes including masonary work and labour charges etc., Makes:- Sudhakar / Finolex / Modi / VIP / Precision / Universal / Million Plast / Gold / Polycab / DEC. | 3955.5 | ONE RM | 107 | 423238.5
3 | Supply and erecting PVC / GI / MS Galvanished fan hook box with hook in RCC slab including all Labour charges etc., complete. | 90 | EACH | 158 | 14220
WIRING
4 | Wiring with run of 2 of 1.5 Sqmm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specification for Copper cable. in existing PVC conduit pipe including Supply and fixing of Jumbo Ceiling rose and 6A/10A ISI Mark 1way Modular switch with required modular box and cover frame in existing Surface or Concealed pipe wiring including cost and conveyance of all material and all labour charges etc., complete for light, Fan, Exhaust fan and bell points in R.B. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | 605 | EACH POINT | 935 | 565675
5 | Wiring with run of 2 of 1.5 Sqmm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specification for Copper cable. in existing PVC conduit pipe including Supply and fixing of Jumbo Ceiling rose and 6A/10A ISI Mark 1way Modular switch with required modular box and cover frame in existing Surface or Concealed pipe wiring including cost and conveyance of all material and all labour charges etc., complete for staircase light points in R.B. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | 18 | EACH POINT | 1403 | 25254
6 | Supply and fixing of 10A 3/2 Pin 2 Module Modular Socket with shutter with 6 / 10A 1 Way 1 Module Modular Switch, 3 Module box with cover frame in Common switch board including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B. Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | 100 | Each | 716 | 71600
7 | Supply and fixing of 6 / 10A 1 Way 1 Module Modular Switches - 2 Nos and 10A 3/2 Pin 2 Module Modular Socket with shutter - 2 Nos Modular type with cover plate and GI switch box fixing on separate board including all labour charges etc., complete. Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | 5 | Each | 1301 | 6505
8 | Supply and fixing of 16A / 6A 2 Module Combi Socket Modular Socket with shutter with 16A/20A 1 Way 1 Module Modular Switch fixed on suitable size Modular box with required cover frame including with connections, cost and conveyance of all material and all labour charges etc., complete Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | 5 | Each | 846 | 4230
9 | Supply and fixing of following switches and sockets modular type on suitable size Modular deep box with cover frame including cost and coveyance of all material and all labour charges etc., complete with following configurations 1) 16A / 6A 2 Module Combi Socket Modular Socket with shutter - 1 No 2) 16A/20A 1 Way 1 Module Modular Switch. - 1 No 3) 10A 3/2 Pin 2 Module Modular Socket with shutter - 1 Nos. 4) 6 / 10A 1 Way 1 Module Modular Switch – 1 Nos. including cost and coveyance of all material and all labour charges etc., complete for Computer, LAB and OTs Use Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | 0 | Each | 1432 | 0
10 | Supply and fixing of following switches and sockets modular type on suitable size Modular deep box with cover frame including cost and coveyance of all material and all labour charges etc., complete with following configurations. 1) 16A / 6A 2 Module Combi Socket Modular Socket with shutter - 2 Nos 2) 16A/20A 1 Way 1 Module Modular Switch. - 2 Nos 3) 10A 3/2 Pin 2 Module Modular Socket with shutter - 2 Nos. 4) 6 / 10A 1 Way 1 Module Modular Switch - 2 Nos. including cost and coveyance of all material and all labour charges etc., complete for LAB,ICU's and OTs Use Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze. | 0 | Each | 2846 | 0
RUN of MAINS
11 | Supply and Run of 1 of 1.5 sq.mm (Earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specification for Copper cable. specifications for Copper cable in the existing conduict pipe for earth continuity inlcuding all labour charges etc., complete. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | 540 | One RM | 37 | 19980
12 | Supply and Run of 3 of 2.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable of in existing conduit pipe for individual lighting circuits including labour charges etc., complete as required for switch boards. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | 3120.625 | One RM | 166 | 518023.75
13 | Supply and Run of 3 of 4.0 sq mm (phase neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable of in existing pipe for power points and AC Sockets inlcuding all labour charges etc., complete. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | 75 | One RM | 239 | 17925
14 | Supply and Run of 3 of 6.0 sq mm (phase neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable of in existing pipe for SPNDB's incoming inlcuding all labour charges etc., complete. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | 0 | One RM | 336 | 0
15 | Supply and Run of 5 of 6.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable in the existing conduict pipe for run of mains from VTPN / Panel Board to TPN DB"s with pin type lugs and connections etc., complete. [for LDBs & 4P MCB's ] Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | 330 | One RM | 568 | 187440
16 | Supply and Run of 5 of 10.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable in the existing conduict pipe for run of mains from VTPN / Panel Board to TPN DB"s with pin type lugs and connections etc., complete. [for PDBs] Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR). | 300 | One RM | 907 | 272100
DISTRIBUTION BOARDS
17 | Supply and fixing of 20A SP Plug and Socket with 20A SP MCB with SS enclosure including connections for Flush Mounting etc.,complete for AC's. Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. | 0 | Each | 2669 | 0
18 | Supply and fixing of FP Metal Enclosure with IP 20 Protection DB Make with 1 No 63A, 10 KA DP MCB including internal connection and labour charges for Flush Mounting etc.,complete. Makes of Enclousure : Legrand / Schneider / Siemens / L&T / Crabtree Xpro / ABB / C&S MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. | 0 | Each | 4896 | 0
19 | Supply and fixing of 8 Way SPN DB with IP 43 Protection as per IS:13032 with 1 No 40A DP MCB as Incommer, and 6 Nos of 20A SP MCB 10KA, C/D Curve ISI Mark as out goings, concealing in wall etc complete. DB Makes : Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro / ABB / C&S MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. | 0 | Each | 8487 | 0
20 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 with 1 No., of 32A FP MCB 10KA, C/D Curve ISI Mark as incomer and 12 Nos 6-32 A 10KA SP MCBs 10KA, C/D Curve ISI Mark as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. (For Lighting DBs) DB Makes : Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro / ABB / C&S MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. | 10 | Each | 14372 | 143720
21 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 with 1 No., of 63A FP MCB 10KA, C/D Curve ISI Mark as incomer and 12 Nos 6-32 A 10 KA SP MCBs 10KA, C/D Curve ISI Mark as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. (For Power DBs& UPS DB's) DB Makes :Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro / ABB / C&S MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. | 10 | Each | 15243 | 152430
22 | Supply and fixing of 4 Way VTPN DB with IP 43 Protection as per IS:13032 with 1 No., of 125A 4P MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted as incomer with 8 Nos of 63A TP MCBs 10KA, C/D Curve ISI Mark as Out goings including internal connections and labour charges for FLUSH Mounting etc., complete. DB Makes :Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. MCCB Makes : L&T- D sine / Schneider-NS NSX / Legrand -DP X3 / Siemens-3V / Hager-h3 / C&S -Winbreak. | 1 | Each | 47564 | 47564
23 | Supply and fixing of 8 Way VTPN DB with IP 43 Protection as per IS:13032 with 1 No., of 125A 4P MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted as incomer with 8 Nos of 63A TP MCBs 10KA, C/D Curve ISI Mark as Out goings including internal connections and labour charges for FLUSH Mounting etc., complete. DB Makes :Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. MCCB Makes : L&T- D sine / Schneider-NS NSX / Legrand -DP X3 / Siemens-3V / Hager-h3 / C&S -Winbreak. | 2 | Each | 62982 | 125964
23 | Supply and fixing of cable adopteres box with cover for DBs including, massanory work etc., complete., Makes : Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro | 21 | Each | 600 | 12600
24 | Supply and Installation of 63A 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 KA with thermal magnetic release with suitable SS Enclosure and angle iron frame work on wall / floor including all Labours charges massonry work etc complete with connections. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3VL / Hager-h3/C&S -Winbreak. | 0 | Each | 16538 | 0
25 | Supply and Installation of 125 Amps 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release with suitable SS Enclosure and angle iron frame work on wall / floor including all Labours charges massonry work etc complete with connections. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3VL / Hager-h3/C&S -Winbreak. | 0 | Each | 25775 | 0
26 | Supply and Installation of 250 Amps 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release with suitable SS Enclosure and angle iron frame work on wall / floor including all Labours charges massonry work etc complete with connections. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3VL / Hager-h3/C&S -Winbreak. | 0 | Each | 52546 | 0
Earthings
27 | Providing independent earthing for Important equipment with 40mm dia 'B' class 2.5m long G.I pipe and 19mm dia 'B' class G.I pipe of 0.3mtr. long connected with reducer providing G.I funnel with mesh enclosed in C.C/ brick massonry chamber of 450m x 450m x 400mm withR.C.C. Slab cover duly providing staggered holes filling with 20Kg Salt and 40Kg Charcoal or 40Kg bentonite powder from the bottom of the pipe giving earth connection from electrode through G.I strip of 40 x 6mm x 200mm length with all accessories and labour charges complete, as per IS specifications 732/1982 (Part II) | 6 | Each | 6635 | 39810
28 | Providing independent earthing by exacavating a pit to a depth of 2.25Mtr in all soils as per size specified in the data for Sophisticated Electronic equipment with 600mm x 600mm x 3.15mm thick copper plate rigidly fixed to 19mm dia 'B' Class G.I Pipe of 2.5Mtr lengthwith funnel as per National Electric Code and earth connection from electrode GI strip of 40mm x 5mm x 200mm length to be bolted with nut bolts to G.I.pipe including 25mm x 3mm copper strip of 6Mtrs length connected from plate to GI strip including filling with 20Kg Salt and 40Kg Charcoal or 40Kg bentonite powder from the bottom of the pipe and providing CC / Brick massonry chamber 450mmX450mmX400mm and covered with R.C.C. Slab including all accessories and labour charges etc complete as per IS specification 732/1982 (Part II). | 6 | Each | 18940 | 113640
29 | Supply and Run of 25mm x 6mm G.I Strip including cost of all accessories and labour charges etc., complete. | 100 | One RM | 160 | 16000
30 | Supply and Run of 50mm x 6mm G.I Strip including cost of all accessories and labour charges etc., complete. | 100 | One RM | 322 | 32200
31 | Supply and Run of 25mm x 3mm copper strip (Cuurrent Carrying Capacity 270A) including cost of all accessories and labour charges etc., complete. | 100 | One RM | 883 | 88300
32 | Supply and run of No. 8SWG GI wire including cost of all accessories and labour charges etc complete. | 150 | One RM | 27 | 4050
FIXTURES
33 | Supply, transportation and fixing of 22W +/ 10% , >/ 2300 lumens, 1200mm length LED light housing made with alluminium anodised body, wide operating voltage with PF≥0.9, Surge protection: > 2KV, THD<10%, with inbuilt driver and frosted cover CCT: 3000K - 6500K as desired by the department as per IS, minimum CRI≥80 etc., complete with 5 years warranty with BIS Certification with BIS Certification LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Goldmedal.. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. Make & Model will be Approved by the Head Office / Engineer-in-charge. | 200 | Each | 882 | 176400
34 | Supply, transportation and fixing 32-36W (>=3240 Lumens) 2' x2' (600mm x 600mm) slim panel Recessed / Surface LED luminaire Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >90 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% with non integrated driver etc., complete with 2 years warranty with BIS Certification. LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Goldmedal.. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. Make & Model will be Approved by the Head Office / Engineer-in-charge. | 0 | Each | 3374 | 0
35 | Supply, transportation and fixing of 18 W +/-10% (>= 1800 Lumens) LED Down Light Recessed / Surface mounting round / square with housing made of Powder coated Pressure die cast aluminium housing with extended heat sink, with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor > 0.9, Surge protection: > 2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI >80, and THD is less than 15% etc., complete with 5 years warranty with BIS Certification. LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Goldmedal.. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. Make & Model will be Approved by the Head Office / Engineer-in-charge. | 0 | Each | 1848 | 0
36 | Supply, Transportation and fixing of 60 W +/-10% (>6000 Lumens) LED HIgh Bay Luminaire with high power COB LED made of pressure diecast alluminium housing with powder coated,Supply Input voltage 120 - 270 V AC, P.F > 0.90, high power LED's, System efficacy >100 lm / W and junction temprature < 70°C, with Ingrees protection IP65, IK05, Driver surge protection 4KV, external Surge protection ≥ 5KV with wide/ Narrow beam optics, THD<10% at 110 Volts AC, driver efficiency >90%, CCT: 3000K - 5700K, minimum CRI>70, etc., with required wiring complete with BIS certification with warranty 5 years warranty. The contractor has to furnish the manufacturer warranty letter, LM 79 and LM 80 certificates. LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Goldmedal.. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs. | 4 | Each | 8712 | 34848
37 | Supply, transportation and fixing ISI mark batten holder / slanting holder Makes : Anchor / Gold Medal Olive / Million Zoom in lieu of ceiling rose of light point complete with all connections and all labour charges with 5W LED Lamp. LED Lamp MAKES: Phillips / OSRAM / Crompton / Eveready / Bajaj / Havells / Halonix / Jaquar / C&S / GM / / Gold Medal / Million. | 200 | Each | 150 | 30000
38 | Supply, Transportation of energy efficient fan, 1200 mm sweep, aluminium body, consuming 28 W, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) motor, class of insulation: B, 3 no's blades, 30 cm long down rod, 2 no's canopies, shackle'kit, safety rope, copper winding, Power Factor greater than 0.90, Service Value (CMMAV) greater than 8.5, Air delivery minimum 235 CMM, 350 RPM( tolerance as per IS:374-2019), THD less than 10%. with remote or compatible to electronic step type regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise = 75 degree C(max), insulation resistance more than 2 mega ohm, suitable for 230V, 50 HZ, single phase AC supply, earthing etc., including all standard accessories etc., complete. Makes : Atomberg (Efficio ) / Havells / Orient / Halonix | 90 | Each | 3505 | 315450
39 | Supply and fixing of Modular type Stepped electronic regulator for sweep AC ceiling fans of 1200mm / 1400mm complete with connections. Makes : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Crabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T Englaze. | 90 | Each | 773 | 69570
40 | Labour charges for Fixing of Ceiling fan including giving connections with twin core wire etc., complete. | 90 | Each | 207 | 18630
41 | Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete. | 90 | Each | 175 | 15750
42 | Supply,Transportation of light duty exhaust fan 12"(300 mm) size 900 rpm with metal blades wiremesh with all accessories etc complete. Makes : Crompton / Havells Ventil Air-DB / Orient hill air. | 90 | Each | 2005 | 180450
43 | Supply,Transportation of 12" (300mm) ISI, 900 RPM Heavy duty exhaust fan with metallic blades wiremesh with all accessories etc complete. Makes : Crompton / Almounard / Havells Turbo Force. | 0 | Each | 3952 | 0
44 | Labour charges for fixing of Exhaust fan in wall with necessary connections and masonary work including material of making hole, finishing etc., complete. | 90 | Each | 849 | 76410
45 | Supply and fixing of GI louver shutter including GI mesh to avoid birds entry with necessary materials suitable for 300mm(12 inches) Exhaust fan. | 90 | Each | 205 | 18450
Telephone System
46 | Supply and fixing of Modular telephone Jack with connector on modular box with cover frame in existing consealed pipe wiring including cost and coveyance of all material and all labour charges etc., complete. Makes : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze | 1 | Each | 384 | 384
47 | Supply, Transportation and Run of 1 of 2 Pair 0.5mm telephone copper cable in the existing conduit pipe and labour charges etc., complete. Makes : Finolex / Delton / Surabi / Polycab. | 35 | One RM | 28 | 980
48 | Supply, Transportation and Run of 1 of 20 Pair telephone copper cable in the existing cable tray/ conduit pipe and labour charges etc., complete. Makes :Finolex / Delton / Surabi / Polycab | 0 | One RM | 122 | 0
49 | Supply, Transportation and Fixing of 20 pair Telephone distribution box with back mount frame, krone connector, powder coated metal body with lock and key arrangement including all accessories and labour charges etc., complete. | 0 | Each | 1566 | 0
50 | Supply, Transportation and Fixing of 100 pair Telephone distribution box with back mount frame, krone connector, powder coated metal body with lock and key arrangement including all accessories and labour charges etc., complete. | 0 | Each | 5507 | 0
51 | Supply, Installation, Testing and Commissioning of IP Based digtal Telephone (EPABX) system--complied with following specifications: > IP @ Core, PCM/TDM switching, Non blocking, > Must Support PRI, E1, Analog Junctions > Must Support PC Console, > Must support Mobile SIP (Android and I O.S) > Must support Voice Mail > Must support Card based GSM > Inbuilt Call Details Software with search engine software > 8 Analog Trunks > 8 Digital Extensions > 96 Analog Extensions > 1 Digital Key Phone with minimum 16 Keys (Must work only on 2 wires) > Expandable to 220 Ports wired or more at extra cost Approved Brands: NEC/ Alcatel/ Karel / Unify | 0 | Each | 454460 | 0
LAN
52 | Supply, Transportation and Run of Cat - 6 UTP cable for LAN in the existing conduit pipe and labour charges etc., complete. Makes : D Link / AMP / Molex / Legrand / Krone. | 35 | One RM | 50 | 1750
53 | Supply, Transportation and Fixing of Cat 6 RJ-45 information outlets including duel face plate with all accessories and labour charges etc., complete. Makes : D Link / AMP / Molex / Legrand / Krone. | 1 | Each | 593 | 593
54 | Supply, Transportation and Fixing of 24 Port 10 / 100 / 1000 Gigabit Ethernet switches including all accessories and labour charges etc., complete. Makes : Digisol / TP Link / D link. | 0 | Each | 10660 | 0
55 | Supply, Transportation and Fixing of 24 port patch panels including all accessories and labour charges etc., complete. Makes : D Link / AMP / Molex / Legrand / Krone | 0 | Each | 8123 | 0
56 | Supply, Transportation and Fixing of 19" 6U Wall mounting net work rack with power spike including all accessories and labour charges etc., complete. Makes : HCL / VAL / Rittal / APW | 0 | Each | 8526 | 0
Air Conditioners
57 | Supply, transportation and installation of split AC unit with high wall mounted 100% copper indoor unit and outdoor condencing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.0 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord (Voltage range 160- 264 volts) and cordless remote control with 5 years warranty compressor and comprehensive maintenance for 2 years.
a) | 1.5 TR 3 Star capable of delivering 18000 BTU/hr Makes: Carrier / Daikin / Blue Star / Hitachi. | 0 | Each | 44878 | 0
b) | 2.0 / 1.8 TR 3 Star capable of delivering 21600 BTU/hr and above Makes: Daikin / Thoshiba / O General / Carrier / Blue Star / Hitachi | 0 | Each | 55308 | 0
58 | Supply and erecting fully automatic line voltage stabilizer for operation on input voltage 200 to 250V. rated for 4 KVA maximum load and time delay model with Volt meter, selector switch, 6A / 16A flush type, 5 pin socket for out put and with 3 core flexible chord and 3 pin 6/16A plug top suitable for AC for continuous operation including cost and conveyance of all mateials and all labour charges etc., complete. Makes : V-Guard / Real Guard / Uni Stab / ITL. | 0 | Each | 3665 | 0
59 | Supply and erecting fully automatic line voltage stabilizer for operation on input voltage 200 to 250V. rated for 5 KVA maximum load and time delay model with Volt meter, selector switch, 6A / 16A flush type, 5 pin socket for out put and with 3 core flexible chord and 3 pin 6/16A plug top suitable for AC for continuous operation including cost and conveyance of all mateials and all labour charges etc., complete. Makes : V-Guard / Real Guard / Uni Stab / ITL. | 0 | Each | 4372 | 0
CABLE TRAYS PERFORATED
60 | Supply and Installation of 100mm x 25mm x 2mm thick GI perforated cable tray with out cover along with required angle supports, with coupler plates, Anchor bolts and nuts etc complete and the tray should be fitted on the wall / Ceiling etc. complete. Makes: DEC/MNR/ H FAB or equivalent | 0 | ONE MTR | 517 | 0
61 | Supply and Installation of 150mm x 50mm x 2mm thick GI perforated cable tray with out cover along with required angle supports, with coupler plates, Anchor bolts and nuts etc complete and the tray should be fitted on the wall / Ceiling etc. complete. Makes: DEC/MNR/ H FAB or equivalent | 100 | ONE MTR | 886 | 88600
62 | Supply and Installation of 300mm x 50mm x 2mm thick GI perforated cable tray with out cover along with required angle supports, with coupler plates, Anchor bolts and nuts etc complete and the tray should be fitted on the wall / Ceiling etc. complete. Makes: DEC/MNR/ H FAB or equivalent | 50 | ONE MTR | 1227 | 61350
63 | Supply and Installation of 450mm x 50mm x 2mm thick GI perforated cable tray with out cover along with required angle supports, with coupler plates, Anchor bolts and nuts etc complete and the tray should be fitted on the wall / Ceiling etc. complete. Makes: DEC/MNR/ H FAB or equivalent | 0 | ONE MTR | 1454 | 0
64 | Supply, Transportation and Installation of 600mm x 75mm x 2mm thick GI Ladder type cable tray along with required coupler plates, T's, Bends, Reducers, Anchor bolts, nuts, washers and slotted channels / Angle Iron Channels etc complete and the tray should be fitted on the wall / Ceiling etc. complete for finished item of work. Makes: DEC/MNR/ H FAB or | 0 | ONE MTR | 2227 | 0
65 | Supply , fabrication and transportation of MS channel iron/ angle iron /flats including two coats of aluminium paint and one coat of red oxide paint including all labour charges etc complete. | 100 | 1KG | 142 | 14200
Sub Power Panel
66 | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor Type MV panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Alluminium busbar ( with rating of 0.8A/ Sqmm)supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, flexibiltioy to accept the up four out going cables and necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges. | 0 | Each | 282182 | 0
Incomer : 160 A 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 36/35 KA with thermal magnetic release Panel Mounted as incomer.Makes : L&T- D shine / Schneider-NS NSX / Legrand -DP X3 / Siemens-3VL / Hagerh3 / C&S -Winbreak - 1 No.
Out goings : 125A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted - 5 Nos Makes : L&T- D shine / Schneider-NS NSX / Legrand -DP X3 / Siemens-3VL / Hagerh3 / C&S -Winbreak
63A / 60A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 KA with thermal magnetic release Panel Mounted.- 4 Nos. Makes : L&T- D shine / Schneider-NS NSX / Legrand -DP X3 / Siemens-3VL / Hagerh3 / C&S -Winbreak
0-415V volt Digital meter of size 96x96mm on exisiting box / panel board including connections etc., complete of CONZERVE / ELMEASURE / MECO / HPL MAKE. - 1 No.
0-100 / 200 / 400 / 600 /1000 - 5A CT Digital Ammeter of size 96x96mm on existing box / panel board including connections etc., complete of CONZERVE / ELMEASURE / MECO / HPL MAKE. - 1 No.
Analog selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete. L&T / C&S / SALZAR / HPL MAKE. - 2 Nos
Analog LED indicator lamps on the existing box / panel board.L&T / C&S / SALZAR / HPL MAKE. - 3 Nos.
Analog LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete. KAPPA MAKE. - 3 Nos.
Labour charges etc complete with connections for Finished item of work.
Sub Lighting Panel
67 | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor Type MV panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Alluminium busbar ( with rating of 0.8A/ Sqmm)supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, flexibiltioy to accept the up four out going cables and necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges. | 0 | Each | 374911 | 0
Incomer : 125 A 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted as incomer.Makes : L&T- D shine / Schneider-NS NSX / Legrand -DP X3 / Siemens-3VL / Hagerh3 / C&S -Winbreak - 1 No.
63A / 60A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 KA with thermal magnetic release Panel Mounted.- 6 Nos. Makes : L&T- D shine / Schneider-NS NSX / Legrand -DP X3 / Siemens-3VL / Hagerh3 / C&S -Winbreak
0-415V volt Digital meter of size 96x96mm on exisiting box / panel board including connections etc., complete of CONZERVE / ELMEASURE / MECO / HPL MAKE. - 1 No.
0-100 / 200 / 400 / 600 /1000 - 5A CT Digital Ammeter of size 96x96mm on existing box / panel board including connections etc., complete of CONZERVE / ELMEASURE / MECO / HPL MAKE. - 1 No.
Analog selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete. L&T / C&S / SALZAR / HPL MAKE. - 2 Nos
Analog LED indicator lamps on the existing box / panel board.L&T / C&S / SALZAR / HPL MAKE. - 3 Nos.
Analog LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete. KAPPA MAKE. - 3 Nos.
Labour charges etc complete with connections for Finished item of work.
UG Cable
68 | Supply of the Following XLPE insulated, 1100V grade armoured alluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) Makes : Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / RR kable / Finecab / RPG.
a | 16 Sqmm 4 Core | 50 | One RM | 319 | 15950
b | 35 Sqmm 3.5 Core | 50 | One RM | 489 | 24450
c | 50 Sqmm 3.5 Core | 100 | One RM | 648 | 64800
d | 70 Sqmm 3.5 Core | 100 | One RM | 830 | 83000
e | 95 Sqmm 3.5 Core | 50 | One RM | 1080 | 54000
f | 120 Sqmm 3.5 Core | 0 | One RM | 1330 | 0
g | 185 Sqmm 3.5 Core | 0 | One RM | 1841 | 0
h | 240 Sqmm 3.5 Core | 0 | One RM | 2341 | 0
i | 300 Sqmm 3.5 Core | 0 | One RM | 2852 | 0
LT Cable laying
69 | Earth work excavation of Trench in hard ground soil and Sand filling shall be provided at the bottom of trench before laying the cable and laying of U.G cables from 95 Sqmm up to 400 sqmm covering the cable with bricks and back filling of Trench duly providing route indicator at every 8 Mtrs distance embedded in C.C including cost and conveyance of materials and labour charges etc., complete. | 100 | One RM | 378 | 37800
70 | Earth work excavation of Trench in hard ground soil and Sand filling shall be provided at the bottom of trench before laying the cable and laying of U.G cables up to 70 sqmm covering the cable with back filling of Trench duly providing route indicator embedded in C.C including cost and conveyance of materials and labour charges etc., complete. | 100 | One RM | 365 | 36500
71 | Laying of PVC armoured under ground cable from 95 Sq.mm to 400 Sqmm fixing on chromium plated metallic base saddles on wall / cable tray as per IS 1255 and as directed by the department including cost and conveyance of all materials and labour charges etc., complete. | 150 | One RM | 66 | 9900
72 | Laying of PVC armoured under ground cable up to 70 Sqmm fixing on chromium plated metallic base saddles on wall / Cable tray as per IS 1255 and as directed by the department including cost and conveyance of all materials and labour charges etc., complete. | 150 | One RM | 55 | 8250
LT Cable terminations
73 | Providing Termination for UG cables for following XLPE insulated armoured cable with fixing of heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket, with required lugs etc complete. Makes: SMI / Commet / Dowels.
a | 16 Sqmm 4 Core | 8 | Each | 692 | 5536
b | 35 Sqmm 3.5 Core | 8 | Each | 861 | 6888
c | 50 Sqmm 3.5 Core | 8 | Each | 1071 | 8568
d | 70 Sqmm 3.5 Core | 8 | Each | 1542 | 12336
e | 95 Sqmm 3.5 Core | 0 | Each | 1637 | 0
f | 120 Sqmm 3.5 Core | 0 | Each | 2164 | 0
g | 185 Sqmm 3.5 Core | 0 | Each | 2889 | 0
h | 240 Sqmm 3.5 Core | 0 | Each | 3616 | 0
i | 300 Sqmm 3.5 Core | 0 | Each | 4287 | 0
Safety equipments
74 | Supply of Rubber hand gloves suitable for 11 KV. | 0 | Each Pair | 2272 | 0
75 | Supply and fixing of PVC synthetic elastomer electrically insulated mat with Class B insulation conforming to IS: 15652-2006 having 2.5mm thickness upto 11KV. | 0 | One Sqmtr | 5643 | 0
76 | Providing & Fixing of Shock instrution chart in English / Hindi / Telugu duly framed with front glass. | 0 | Each | 654 | 0
77 | Providing & Fixing of Danger Notice Plates of size 250x200mm, shall comply with IS:2551-1982. | 0 | Each | 325 | 0
78 | Providing floor mounting stand for keeping 4No of fire bucket 1500mm length, 900mm height made out of 40x40x6mm angle iron welded with 4 hooks and duly painted with one coat of red lead and two coats of enamel paint. | 0 | Each | 1593 | 0
79 | Providing & Supply of round bottom G.I sheet bucket of 9 Ltrs. Capacity as per IS:2546 made out of 24 gauge GI sheet with extra handle at bottom duly painted inside and red out side with printed with FIRE Mark for stand and hook and filled with sand and arranged to existing stand or hook. | 0 | Each | 391 | 0
80 | First Aid box 18" x 12" x 8" containing material as prescribed by St. John Ambulance brigade OR Indian Red Cross complete as required. | 0 | Each | 1718 | 0
81 | Preparation of Drawings of existing or new installations and obtaining approval from the CEIG complete as per the requirement at site. | 0 | Each | 40000 | 0
82 | Supply, transportation, installation, testing and commissioning of 8 passenger Gearless & Machine Room less elevator with following specifications with connected minor civil works required for installation of Lift including all accessories, scoffolding, requried channels, loading and unloading of materials etc, including comprehensive maintenance of lifts during the defect liability period. Makes: Schindler / Kone / OTIS / Mitsubishi or equivalent. Make & Model will be Approved by the Head Office / Engineer-in-charge. | 1 | Each | 2537932 | 2537932
Specifications: a) Type: Machine room less b) Pit Depth: 1500 mm or as per NBC c) Minimum Floor to Floor Height (Required): As per Standard d) Travel height: 3.6 to 4.0mtrs e) Head room Height: 4.5mtrs f) Lintel Height (Required) : 2240mm from finished floor level +/- 10% g) Number of persons : 8 Persons
h) Rated Load: 544 Kgs i) Number of Stops: 10 stops j) Number of Access sides : 1 k) Floor Designations : G, 1, 2, 3,4,5,6,7,8,9.
l) Drive Sytem : Alternating current, Voltage Frequency Drive (ACVF). m) Type of Controller : Fully collective control - Simplex / Duplex as per the site condition. n) Speed of Travel : 1.5 - 1.75 Mtr / Sec o) Car size : As per Standard p) Door width : 800/ 900/1000mm or As per Standard q) Door Height : 2000 mm or as per standard r) Rated output motor : as per standard s) Car Design : Car walls finish in Stainless stell hairline finish LED spot in ceiling. t) Car Doors : stainless steel hairline finish. Granite Flooring finish in Black sea. Deco ceiling finish in stainless steel Hairline. Full Height mirror on rear car panel.
u) Car Operating Panel : Mechanical push button.Door open/close and alarm buttons / Touch panel or equivalent, Visual call confirmation, Car position Indicator, Preannouncing arrows for collective controls, 16 Segment display v) Landing Doors : Fully automatic landing doors with stainless steel hairline finish. Center Opening or Side Opening as per the site condition
w) Special Features : 1.Closed loop control system 2.Self Diagnostic control 3.Overload detection 4.Automatic evacuation to nearest floor(ARD) 5.Light curtain on car entrance 6.Alarm Horn 7.Fire Switch 8.Handrail in stainless steel finish on rear wall 9.Auto Fan off 10.Auto light off 11.Intercom-3way
| Electrical Total : |  |  |  | 7517385.75

## E-Data 24-25
| 1 |  | Skilled Electrician. |  |  | 735
| 2 |  | Lineman Electric / Telephone |  |  | 615
| 3 |  | Helper (Electrical). |  |  | 615
| 4 |  | Mason Cl- I / Brick layer Cl- I |  |  | 645
| 5 |  | Man Mazdoor |  |  | 575
| 7 |  | Contractor Profit | 0.13615
Electrical Datas
(SSR Based on SSR 2022-23)
Electrical Datas 2024-25
S.No | SSR Item No | Item Code | Description | Qty |  | Unit |  | Rate | Amount
I |  |  | CONDUIT PIPE
1 |  |  | Supply and Laying of ISI 25mm outer dia heavy grade with IS:9537 part 3 rigid PVC pipe concealed in Roof Slabs with all required PVC / Metallic Deep Boxes including masonary work and labour carges etc., complete. Makes : Sudhakar / Finolex / Modi / VIP / Precision / Universal / Million Plast / Gold / Polycab / DEC
a) Labour charges :
| 1 |  | Skilled Electrician. | 2 | day | 1 | day | 735 | 1470
| 2 |  | Lineman Electric / Telephone | 2 | day | 1 | day | 615 | 1230
| 3 |  | Helper (Electrical). | 2 | day | 1 | day | 615 | 1230
|  |  | Labour Rate Per 100 Rm | [5 empty] | 3930
|  |  | Labour Rate for 1 Mtr | [5 empty] | 39.3
b) Material
| 1.2.7 | b | Supply of PVC Junction Boxes Deep size 25mm. | 12 | Nos | 1 | Nos | 35 | 420
| 1.2.8 | b | Supply of 25mm dia 1.5mm thick PVC Bends. | 12 | Nos | 1 | Nos | 12 | 144
| 1.2.1 | b | Supply of ISI 25mm outer dia heavy grade FRLS with IS:9537 part 3 regid PVC pipe. | 100 | Mtr | 1 | Mtr | 45 | 4500
|  |  | Material Rate for 100 Mtrs | [5 empty] | 5064
|  |  | Material Rate for 1 Mtr | [5 empty] | 50.64
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 89.9
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 12.2399
102.1399
|  |  | Rate per Meter | [5 empty] | 102
2 |  |  | Supply and laying of ISI 25mm outer dia medium grade, with IS:9537 part 3 rigid PVC concealed in wall with all required PVC / Metallic Junction Boxes including masonary work and labour charges etc., Makes:- Sudhakar / Finolex / Modi / VIP / Precision / Universal / Million Plast / Gold / Polycab / DEC.
a) Labour charges :
| 1 |  | Skilled Electrician. | 2 | day | 1 | day | 735 | 1470
| 2 |  | Lineman Electric / Telephone | 2 | day | 1 | day | 615 | 1230
| 3 |  | Helper (Electrical). | 2 | day | 1 | day | 615 | 1230
|  |  | Labour Rate Per 100 Rm | [5 empty] | 3930
|  |  | Labour Rate for 1 Mtr | [5 empty] | 39.3
b) Material
| 10.4.10 |  | Cement. | 50 | kg | 1 | Kg | 9 | 450
| 10.1.4 |  | U Nails. | 200 | Nos | 100 | Nos | 44 | 88
| 1.2.6 | b | Supply of 25mm PVC Junction Boxes Normal. | 12 | Nos | 1 | Nos | 28 | 336
| 1.2.8 | b | Supply of 25mm dia 1.5mm thick PVC Bends. | 12 | Nos | 1 | Nos | 12 | 144
| 1.2.2 | b | Supply of ISI 25mm outer dia medium grade FRLS with IS:9537 part 3 regid PVC pipe. | 100 | Mtr | 1 | Mtr | 45 | 4500
|  |  | Material Rate for 100 Mtrs | [5 empty] | 5518
|  |  | Material Rate for 1 Mtr | [5 empty] | 55.18
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 94.4
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 12.8526
107.2526
|  |  | Rate per Meter | [5 empty] | 107
Supply and Fixing of ISI 25mm outer dia medium grade, with IS:9537 part 3 rigid PVC with all accessories fixing on chromium plated metallic base saddles including all labour charges etc., complete for run of mains. Makes:- Sudhakar / Finolex / Modi / VIP / Precision / Universal / Million Plast / Gold / Polycab / DEC.
a) Labour charges :
| 1 |  | Skilled Electrician. | 2 | day | 1 | day | 695 | 1390
| 2 |  | Lineman Electric / Telephone | 2 | day | 1 | day | 580 | 1160
| 3 |  | Helper (Electrical). | 2 | day | 1 | day | 580 | 1160
| 4 |  | Mason Cl- I / Brick layer Cl- I |  | day | 1 | day | 610 | 0
|  |  | Labour Rate Per 100 Rm | [5 empty] | 3710
|  |  | Labour Rate for 1 Mtr | [5 empty] | 37.1
b) Material
| 9.4.11 |  | Cement. | 25 | kg | 1 | Kg | 9 | 225
| 9.1.2 |  | Rawl Plugs | 200 | Nos | 100 | Nos | 45 | 90
| 1.4.4 | d | 35mm Screws | 200 | Nos | 100 | Nos | 128 | 256
| 1.1.11 | b | Chromium Plated saddles with base | 200 | Nos | 100 | Nos | 279 | 558
| 1.2.6 | b | Supply of 25mm PVC Junction Boxes Normal. | 12 | Nos | 1 | Nos | 26 | 312
| 1.2.8 | b | Supply of 25mm dia 1.5mm thick PVC Bends. | 12 | Nos | 1 | Nos | 10 | 120
| 1.2.2 | b | Supply of ISI 25mm outer dia medium grade FRLS with IS:9537 part 3 regid PVC pipe. | 100 | Mtr | 1 | Mtr | 31 | 3100
|  |  | Material Rate for 100 Mtrs | [5 empty] | 4661
|  |  | Material Rate for 1 Mtr | [5 empty] | 46.61
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 83.7
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 11.3958
95.0958
|  |  | Rate per Meter | [5 empty] | 95
3 |  |  | Supply and erecting PVC / GI / MS Galvanished fan hook box with hook in RCC slab including all Labour charges etc., complete.
a) Labour charges :
| 1 |  | Skilled Electrician. | 0.03 | day | 1 | day | 735 | 22.05
| 2 |  | Helper (Electrical). | 0.03 | day | 1 | day | 615 | 18.45
|  |  | Labour Rate for 1 Mtr | [5 empty] | 40.5
a) Material
| 10.1.23 |  | PVC/ MS with hook in RCC Fan hook | each | 1 | 1 | Nos | 138 | 138
| 1.2.7 | b | Deduct Supply of PVC Junction Boxes Deep size 25mm. | each | -1 | 1 | Nos | 35 | -35
|  |  | Rate | [5 empty] | 103
143.5
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 14.0234
157.5234
|  |  | Rate per Each | [5 empty] | 158
Wiring
Point wiring in Residential Building
4 |  |  | Wiring with run of 2 of 1.5 Sqmm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specification for Copper cable. in existing PVC conduit pipe including Supply and fixing of Jumbo Ceiling rose and 6A/10A ISI Mark 1way Modular switch with required modular box and cover frame in existing Surface or Concealed pipe wiring including cost and conveyance of all material and all labour charges etc., complete for light, Fan, Exhaust fan and bell points in R.B. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR)./ DEC (HFFR). Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze.
a) Labour charges :
| 1 |  | Skilled Electrician. | 0.7 | day | 1 | day | 735 | 514.5
| 2 |  | Lineman Electric / Telephone | 1.4 | day | 1 | day | 615 | 861
| 3 |  | Helper (Electrical). | 0.7 | day | 1 | day | 615 | 430.5
|  |  | Labour for 6 Points | [5 empty] | 1806
|  |  | Labour for 1 Point | [5 empty] | 258
b) Material
| ELEC-1.3.1 | b | Supply of 3 Module box. | 1 | Nos | 1 | No | 110 | 110
| ELEC-1.3.1 | c | Supply of 4 Module box. | 1 | Nos | 1 | No | 130 | 130
| ELEC-1.3.3 | b | Supply of 3 Modular Cover Frame. | 1 | Nos | 1 | No | 105 | 105
| ELEC-1.3.3 | c | Supply of 4 Modular Cover Frame. | 1 | Nos | 1 | No | 120 | 120
| ELEC-1.9.1 | a | Supply of 6A/ 10A 1 Way 1 Module Modular Switch. | 7 | Nos | 1 | No | 130 | 910
| ELEC-1.7.1 | m | Supply of 3 Plate Jumbo Ceiling Rose. | 7 | Nos | 1 | No | 25 | 175
| ELEC-1.5.1 | a | Supply of 22/0.3mm (1.5 Sqmm) FRLS / HFFR PVC insulated 1100V grade as perIS:694/1990 specification for Copper cable. | 100 | Mtrs | 100 | Mtrs | 2410 | 2410
|  |  | Cost of Material for 7 Points | [5 empty] | 3960
|  |  | Cost of Material Rate per 1 Point | [5 empty] | 565.7143
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 823
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 112.0514
935.0514
|  |  | Rate per Each | [5 empty] | 935
Stair case point wiring Point wiring in Residential Building
5 |  |  | Wiring with run of 2 of 1.5 Sqmm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specification for Copper cable. in existing PVC conduit pipe including Supply and fixing of Jumbo Ceiling rose and 6A/10A ISI Mark 1way Modular switch with required modular box and cover frame in existing Surface or Concealed pipe wiring including cost and conveyance of all material and all labour charges etc., complete for staircase light points in R.B. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR)./ DEC (HFFR). Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze.
|  |  | 1.5 times of normal (Total Cost of Material + Labour Charges) of Item number 4 = 935x1.5 | 935 | Nos | 1 | No | 1.5 | 1402.5
|  |  | Rate per Each | [5 empty] | 1403
Point wiring in Residential Building
Wiring with run of 2 of 1.5 Sqmm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specification for Copper cable. in existing PVC conduit pipe including Supply and fixing of Jumbo Ceiling rose and 6A/10A ISI Mark 1way Modular switch with required modular box and cover frame in existing Surface or Concealed pipe wiring including cost and conveyance of all material and all labour charges etc., complete for light, Fan, Exhaust fan and bell points in R.B. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR)./ DEC (HFFR). Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze.
a) Labour charges :
| 1 |  | Skilled Electrician. | 0.7 | day | 1 | day | 660 | 462
| 2 |  | Lineman Electric / Telephone | 1.4 | day | 1 | day | 550 | 770
| 3 |  | Helper (Electrical). | 0.7 | day | 1 | day | 550 | 385
|  |  | Labour for 6 Points | [5 empty] | 1617
|  |  | Labour for 1 Point | [5 empty] | 231
b) Material
| ELEC-1.3.1 | b | Supply of 3 Module box. | 1 | Nos | 1 | No | 101 | 101
| ELEC-1.3.1 | c | Supply of 4 Module box. | 1 | Nos | 1 | No | 120 | 120
| ELEC-1.3.2 | b | Supply of 3 Modular Cover Frame. | 1 | Nos | 1 | No | 97 | 97
| ELEC-1.3.2 | c | Supply of 4 Modular Cover Frame. | 1 | Nos | 1 | No | 112 | 112
| ELEC-1.9.1 | a | Supply of 6A/ 10A 1 Way 1 Module Modular Switch. | 7 | Nos | 1 | No | 116 | 812
| ELEC-1.7.1 | m | Supply of 3 Plate Jumbo Ceiling Rose. | 7 | Nos | 1 | No | 23 | 161
| ELEC-1.5.1 | a | Supply of 22/0.3mm (1.5 Sqmm) FRLS / HFFR PVC insulated 1100V grade as perIS:694/1990 specification for Copper cable. | 100 | Mtrs | 100 | Mtrs | 2187 | 2187
|  |  | Cost of Material for 7 Points | [5 empty] | 3590
|  |  | Cost of Material Rate per 1 Point | [5 empty] | 512.8571
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 743
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 101.1594
844.1594
|  |  | Rate per Each | [5 empty] | 844
Stair case point wiring Point wiring in Residential Building
Wiring with run of 2 of 1.5 Sqmm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specification for Copper cable. in existing PVC conduit pipe including Supply and fixing of Jumbo Ceiling rose and 6A/10A ISI Mark 1way Modular switch with required modular box and cover frame in existing Surface or Concealed pipe wiring including cost and conveyance of all material and all labour charges etc., complete for staircase light points in R.B. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR)./ DEC (HFFR). Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze.
|  |  | 1.5 times of normal (Total Cost of Material + Labour Charges) of Item number 4 = 844x1.5 | 844 | Nos | 1 | No | 1.5 | 1266
|  |  | Rate per Each | [5 empty] | 1266
Common Socket
6 |  |  | Supply and fixing of 10A 3/2 Pin 2 Module Modular Socket with shutter with 6 / 10A 1 Way 1 Module Modular Switch, 3 Module box with cover frame in Common switch board including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B. Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze.
a) Labour charges :
| 1 |  | Skilled Electrician. | 0.067 | day | 1 | day | 735 | 49.245
| 2 |  | Helper (Electrical). | 0.067 | day | 1 | day | 615 | 41.205
|  |  | Labour for 1 Point | [5 empty] | 90.45
b) Material
| 1.3.1 | b | Supply of 3 Module box. | 1 | No | 1 | No | 110 | 110
| 1.3.2 | b | Supply of 3 Modular Cover Frame. | 1 | No | 1 | No | 105 | 105
| 1.9.1 | a | 6 / 10A 1 Way 1 Module Modular Switch | 1 | No | 1 | No | 130 | 130
| 1.9.1 | d | 10A 3/2 Pin 2 Module Modular Socket with shutter | 1 | No | 1 | No | 195 | 195
|  |  | Cost of Material Rate per 1 Point | [5 empty] | 540
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 630
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 85.7745
715.7745
|  |  | Rate per Each | [5 empty] | 716
6A Switches - 2 Nos & 6A Sockets - 2 Nos
7 |  |  | Supply and fixing of 6 / 10A 1 Way 1 Module Modular Switches - 2 Nos and 10A 3/2 Pin 2 Module Modular Socket with shutter - 2 Nos Modular type with cover plate and GI switch box fixing on separate board including all labour charges etc., complete. Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze.
a) Labour charges :
| 1 |  | Skilled Electrician. | 0.1 | day | 1 | day | 735 | 73.5
| 2 |  | Helper (Electrical). | 0.1 | day | 1 | day | 615 | 61.5
|  |  | Labour for 1 No | [5 empty] | 135
b) Material
| 1.3.1 | d | Supply of 6 Module box | 1 | No | 1 | No | 180 | 180
| 1.3.2 | d | Supply of 6 Modular Cover Frame. | 1 | Nos | 1 | No | 180 | 180
| 1.9.1 | a | 6 / 10A 1 Way 1 Module Modular Switch | 2 | Nos | 1 | No | 130 | 260
| 1.9.1 | d | 10A 3/2 Pin 2 Module Modular Socket with shutter | 2 | Nos | 1 | No | 195 | 390
|  |  | Cost of Material for 1 No | [5 empty] | 1010
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 1145
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 155.8918
1300.8918
|  |  | Rate per Each | [5 empty] | 1301
6A Sockets - 3 Nos & 6A Switches - 2 Nos
Supply and fixing of 6 / 10A 1 Way 1 Module Modular Switch - 2 Nos and 10A 3/2 Pin 2 Module Modular Socket with shutter - 3 Nos Modular type with cover plate and GI switch box fixing on separate board including all labour charges with connections etc., complete. Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze.
a) Labour charges :
| 1 |  | Skilled Electrician. | 0.2 | day | 1 | day | 695 | 139
| 2 |  | Helper (Electrical). | 0.2 | day | 1 | day | 580 | 116
|  |  | Labour for 1 No | [5 empty] | 255
b) Material
| ELEC-1.3.1 | e | Supply of 8 Module box | 1 | No | 1 | No | 213 | 213
| ELEC-1.3.2 | e | Supply of 8 Modular Cover Frame. | 1 | Nos | 1 | No | 213 | 213
| ELEC-1.9.1 | a | 6 / 10A 1 Way 1 Module Modular Switch | 2 | Nos | 1 | No | 116 | 232
| ELEC-1.9.1 | d | 10A 3/2 Pin 2 Module Modular Socket with shutter | 3 | Nos | 1 | No | 178 | 534
|  |  | Cost of Material for 1 No | [5 empty] | 1192
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 1447
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 197.0091
1644.0091
|  |  | Rate per Each | [5 empty] | 1644
6A Switches - 4 Nos & 6A Sockets - 4 Nos
Supply and fixing of 6 / 10A 1 Way 1 Module Modular Switches - 4 Nos and 10A 3/2 Pin 2 Module Modular Socket with shutter - 4 Nos Modular type with cover plate and GI switch box fixing on separate board including all labour charges etc., complete. Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze.
a) Labour charges :
| 1 |  | Skilled Electrician. | 0.2 | day | 1 | day | 695 | 139
| 2 |  | Helper (Electrical). | 0.2 | day | 1 | day | 580 | 116
|  |  | Labour for 1 No | [5 empty] | 255
b) Material
| ELEC-1.3.1 | f | Supply of 12 Module box | 1 | No | 1 | No | 258 | 258
| ELEC-1.3.2 | f | Supply of 12 Modular Cover Frame. | 1 | Nos | 1 | No | 263 | 263
| ELEC-1.9.1 | a | 6 / 10A 1 Way 1 Module Modular Switch | 4 | Nos | 1 | No | 116 | 464
| ELEC-1.9.1 | d | 10A 3/2 Pin 2 Module Modular Socket with shutter | 4 | Nos | 1 | No | 178 | 712
|  |  | Cost of Material for 1 No | [5 empty] | 1697
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 1952
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 265.7648
2217.7648
|  |  | Rate per Each | [5 empty] | 2218
16 A Socket
8 |  |  | Supply and fixing of 16A / 6A 2 Module Combi Socket Modular Socket with shutter with 16A/20A 1 Way 1 Module Modular Switch fixed on suitable size Modular box with required cover frame including with connections, cost and conveyance of all material and all labour charges etc., complete in N.R.B. / R.B. Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze.
a) Labour charges :
| 1 |  | Skilled Electrician. | 0.067 | day | 1 | day | 735 | 49.245
| 2 |  | Helper (Electrical). | 0.067 | day | 1 | day | 615 | 41.205
|  |  | Labour for 1 No | [5 empty] | 90.45
b) Material
| ELEC-1.3.1 | b | Supply of 3 Module box. | 1 | No | 1 | No | 110 | 110
| ELEC-1.3.2 | b | Supply of 3 Modular Cover Frame. | 1 | No | 1 | No | 105 | 105
| ELEC-1.9.1 | h | Supply of 16A/20A 1 Way 1 Module Modular Switch. | 1 | No | 1 | No | 170 | 170
| ELEC-1.9.1 | L | Supply of 16A / 6A 2 Module Combi Socket Modular Socket with shutter | 1 | No | 1 | No | 270 | 270
|  |  | Cost of Material for 1 No | [5 empty] | 655
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 745
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 101.4317
846.4317
|  |  | Rate per Each | [5 empty] | 846
9 |  |  | Supply and fixing of following switches and sockets modular type on suitable size Modular deep box with cover frame including cost and coveyance of all material and all labour charges etc., complete with following configurations 1) 16A / 6A 2 Module Combi Socket Modular Socket with shutter - 1 No 2) 16A/20A 1 Way 1 Module Modular Switch. - 1 No 3) 10A 3/2 Pin 2 Module Modular Socket with shutter - 1 Nos. 4) 6 / 10A 1 Way 1 Module Modular Switch – 1 Nos. including cost and coveyance of all material and all labour charges etc., complete for Computer, LAB and OTs Use Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze.
a) Labour charges :
| 1 |  | Skilled Electrician. | 0.1 | day | 1 | day | 735 | 73.5
| 2 |  | Helper (Electrical). | 0.1 | day | 1 | day | 615 | 61.5
|  |  | Labour for 1 No | [5 empty] | 135
b) Material
| ELEC-1.9.1 | a | 6 / 10A 1 Way 1 Module Modular Switch | 1 | each | 1 | each | 130 | 130
| ELEC-1.9.1 | d | 10A 3/2 Pin 2 Module Modular Socket with shutter | 1 | each | 1 | each | 195 | 195
| ELEC-1.9.1 | h | Supply of 16A/20A 1 Way 1 Module Modular Switch. | 1 | each | 1 | each | 170 | 170
| ELEC-1.9.1 | L | Supply of 16A / 6A 2 Module Combi Socket Modular Socket with shutter | 1 | each | 1 | each | 270 | 270
| 1.3.2 | d | 6 Module cover frame | 1 | each | 1 | each | 180 | 180
| 1.3.1 | d | 6 Module box | 1 | each | 1 | each | 180 | 180
|  |  | Cost of Material for 1 No | [5 empty] | 1125
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 1260
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 171.549
1431.549
|  |  | Rate per Each | [5 empty] | 1432
10 |  |  | Supply and fixing of following switches and sockets modular type on suitable size Modular deep box with cover frame including cost and coveyance of all material and all labour charges etc., complete with following configurations. 1) 16A / 6A 2 Module Combi Socket Modular Socket with shutter - 2 Nos 2) 16A/20A 1 Way 1 Module Modular Switch. - 2 Nos 3) 10A 3/2 Pin 2 Module Modular Socket with shutter - 2 Nos. 4) 6 / 10A 1 Way 1 Module Modular Switch - 2 Nos. including cost and coveyance of all material and all labour charges etc., complete for LAB,ICU's and OTs Use Makes of switches : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze.
Taking Output = 15 Points
a) Labour charges :
| 1 |  | Skilled Electrician | 0.3 | day | 1 | day | 735 | 220.5
| 2 |  | Helpers | 0.3 | day | 1 | day | 615 | 184.5
|  |  | Labour for 1 No | [5 empty] | 405
b) Material
| ELEC-1.9.1 | a | 6 / 10A 1 Way 1 Module Modular Switch | 2 | each | 1 | each | 130 | 260
| ELEC-1.9.1 | d | 10A 3/2 Pin 2 Module Modular Socket with shutter | 2 | each | 1 | each | 195 | 390
| ELEC-1.9.1 | h | Supply of 16A/20A 1 Way 1 Module Modular Switch. | 2 | each | 1 | each | 170 | 340
| ELEC-1.9.1 | L | Supply of 16A / 6A 2 Module Combi Socket Modular Socket with shutter | 2 | each | 1 | each | 270 | 540
| 1.3.2 | f | 12 Module cover frame | 1 | each | 1 | each | 285 | 285
| 1.3.1 | f | 12 Module box | 1 | each | 1 | each | 285 | 285
|  |  | Cost of Material for 1 No | [5 empty] | 2100
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 2505
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 341.0557
2846.0557
|  |  | Rate per Each | [5 empty] | 2846
III |  |  | Run of Mains
11 |  |  | Supply and Run of 1 of 1.5 sq.mm (Earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specification for Copper cable. specifications for Copper cable in the existing conduict pipe for earth continuity inlcuding all labour charges etc., complete. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR).
a) Labour charges :
| 1 |  | Skilled Electrician. | 0.34 | day | 1 | day | 735 | 249.9
| 2 |  | Lineman Electric / Telephone | 0.7 | day | 1 | day | 615 | 430.5
| 3 |  | Helper (Electrical). | 0.34 | day | 1 | day | 615 | 209.1
|  |  | Labour for 100 Mtr | [5 empty] | 889.5
|  |  | Labour for 1 Mtr | [5 empty] | 8.895
b) Material
| ELEC-1.5.1 | a | Supply of 22/0.3mm (1.5 Sqmm) FRLS / HFFR PVC insulated 1100V grade as perIS:694/1990 specification for Copper cable. | 100 | Mtrs | 100 | Mtrs | 2410 | 2410
|  |  | Cost of Material for 100 Metres | [5 empty] | 2410
|  |  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 24.1
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 32.9
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 4.4793
37.3793
|  |  | Rate per Meter | [5 empty] | 37
Supply and Run of 3 of 1.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable of in existing pipe. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR)/ DEC (HFFR).
a) Labour charges :
| 1 |  | Skilled Electrician. | 1 | day | 1 | day | 660 | 660
| 2 |  | Lineman Electric / Telephone | 2.5 | day | 1 | day | 550 | 1375
| 3 |  | Helper (Electrical). | 1 | day | 1 | day | 550 | 550
|  |  | Labour for 100 Mtr | [5 empty] | 2585
|  |  | Labour for 1 Mtr | [5 empty] | 25.85
b) Material
| ELEC-1.5.1 | a | Supply of 22/0.3mm (1.5 Sqmm) FRLS / HFFR PVC insulated 1100V grade as perIS:694/1990 specification for Copper cable. | 300 | Mtrs | 100 | Mtrs | 2187 | 6561
|  |  | Cost of Material for 100 Metres | [5 empty] | 6561
|  |  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 65.61
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 91.4
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 12.4441
103.8441
|  |  | Rate per Meter | [5 empty] | 104
12 |  |  | Supply and Run of 3 of 2.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable of in existing pipe. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR).
a) Labour charges :
| 1 |  | Skilled Electrician. | 1 | day | 1 | day | 735 | 735
| 2 |  | Lineman Electric / Telephone | 2.5 | day | 1 | day | 615 | 1537.5
| 3 |  | Helper (Electrical). | 1 | day | 1 | day | 615 | 615
|  |  | Labour for 100 Mtr | [5 empty] | 2887.5
|  |  | Labour for 1 Mtr | [5 empty] | 28.875
b) Material
| ELEC-1.5.1 | b | Supply of 36/0.3mm (2.5 Sqmm) FRLS / HFFR PVC insulated 1100V grade as perIS:694/1990 specification for Copper cable. | 300 | Mtrs | 100 | Mtrs | 3900 | 11700
|  |  | Cost of Material for 100 Metres | [5 empty] | 11700
|  |  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 117
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 145.8
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 19.8507
165.6507
|  |  | Rate per Meter | [5 empty] | 166
13 |  |  | Supply and Run of 3 of 4.0 sq mm (phase neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable of in existing pipe for power points and AC Sockets inlcuding all labour charges etc., complete. Makes of wires :Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR).
a) Labour charges :
| 1 |  | Skilled Electrician. | 1 | day | 1 | day | 735 | 735
| 2 |  | Lineman Electric / Telephone | 3 | day | 1 | day | 615 | 1845
| 3 |  | Helper (Electrical). | 1 | day | 1 | day | 615 | 615
|  |  | Labour for 100 Mtr | [5 empty] | 3195
|  |  | Labour for 1 Mtr | [5 empty] | 31.95
b) Material
| ELEC-1.5.1 | c | Supply of 56/0.3mm (4.0 Sqmm) FRLS / HFFR PVC insulated 1100V grade as perIS:694/1990 specification for Copper cable. | 300 | Mtrs | 100 | Mtrs | 5950 | 17850
|  |  | Cost of Material for 100 Metres | [5 empty] | 17850
|  |  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 178.5
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 210.4
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 28.646
239.046
|  |  | Rate per Meter | [5 empty] | 239
14 |  |  | Supply and Run of 3 of 6.0 sq mm (phase neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable of in existing pipe for SPNDB's incoming inlcuding all labour charges etc., complete. Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR).
a) Labour charges :
| 1 |  | Skilled Electrician. | 1 | day | 1 | day | 735 | 735
| 2 |  | Lineman Electric / Telephone | 3 | day | 1 | day | 615 | 1845
| 3 |  | Helper (Electrical). | 1 | day | 1 | day | 615 | 615
|  |  | Labour for 100 Mtr | [5 empty] | 3195
|  |  | Labour for 1 Mtr | [5 empty] | 31.95
b) Material
| ELEC-1.5.1 | d | Supply of 84/0.3mm (6.0 Sqmm) FRLS / HFFR PVC insulated 1100V grade as perIS:694/1990 specification for Copper cable. | 300 | Mtrs | 100 | Mtrs | 8790 | 26370
|  |  | Cost of Material for 100 Metres | [5 empty] | 26370
|  |  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 263.7
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 295.6
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 40.2459
335.8459
|  |  | Rate per Meter | [5 empty] | 336
15 |  |  | Supply and Run of 5 of 6.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable in the existing conduict pipe for run of mains from VTPN / Panel Board to TPN DB"s with pin type lugs and connections etc., complete. [for LDBs] Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR).
a) Labour charges :
| 1 |  | Skilled Electrician. | 2 | day | 1 | day | 735 | 1470
| 2 |  | Lineman Electric / Telephone | 5.5 | day | 1 | day | 615 | 3382.5
| 3 |  | Helper (Electrical). | 2 | day | 1 | day | 615 | 1230
|  |  | Labour for 100 Mtr | [5 empty] | 6082.5
|  |  | Labour for 1 Mtr | [5 empty] | 60.825
b) Material
| ELEC-1.5.1 | d | Supply of 84/0.3mm (6.0 Sqmm) FRLS / HFFR PVC insulated 1100V grade as perIS:694/1990 specification for Copper cable. | 500 | Mtrs | 100 | Mtrs | 8790 | 43950
|  |  | Cost of Material for 100 Metres | [5 empty] | 43950
|  |  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 439.5
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 500.3
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 68.1158
568.4158
|  |  | Rate per Meter | [5 empty] | 568
16 |  |  | Supply and Run of 5 of 10.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable in the existing conduict pipe for run of mains from VTPN / Panel Board to TPN DB"s with pin type lugs and connections etc., complete. [for PDBs] Makes of wires : Finolex / RR kabel / Havells / Polycab / Finecab Gold (HFFR) / GM(HFFR) / Gold Medal(HFFR) / Million (HFFR) / KEI (HFFR) / V-Guard (HFFR) / DEC (FRLS / HFFR) / Avocab (HFFR) / Fortune Arrt (HFFR) / Nakoda (HFFR) / HPL (HFFR).
a) Labour charges :
| 1 |  | Skilled Electrician. | 2.34 | day | 1 | day | 735 | 1719.9
| 2 |  | Lineman Electric / Telephone | 6.5 | day | 1 | day | 615 | 3997.5
| 3 |  | Helper (Electrical). | 2.34 | day | 1 | day | 615 | 1439.1
|  |  | Labour for 100 Mtr | [5 empty] | 7156.5
|  |  | Labour for 1 Mtr | [5 empty] | 71.565
b) Material
| ELEC-1.5.1 | e | Supply of 140/0.3mm (10.0 Sqmm) PVC FRLS / HFFR insulated flexible Copper cable. | 500 | Mtrs | 100 | Mtrs | 14535 | 72675
|  |  | Cost of Material for 100 Metres | [5 empty] | 72675
|  |  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 726.75
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 798.3
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 108.6885
906.9885
|  |  | Rate per Meter | [5 empty] | 907
IV |  |  | Distribution Boards
17 |  |  | Supply and fixing of 20A SP Plug and Socket with 20A SP MCB with SS enclosure including connections for Flush Mounting etc.,complete for AC's. Makes : Legrand / Schneider / Siemens / L&T.
a) Labour charges :
| 1 |  | Skilled Electrician. | 0.25 | day | 1 | day | 735 | 183.75
| 2 |  | Helper (Electrical). | 0.25 | day | 1 | day | 615 | 153.75
| 3 |  | Mason Cl- I / Brick layer Cl- I | 0.15 | day | 1 | day | 645 | 96.75
|  |  | COST OF LABOUR | [5 empty] | 434.25
b) Material
| 2.16.8 | a | Supply of 20A Plug and Socket with SS enclosure. | 1 | Nos | 1 | No | 1590 | 1590
| 2.13.1 | a | Supply of 20A 10KA SP MCB, C/D Curve ISI Mark. | 1 | Nos | 1 | No | 325 | 325
|  |  | COST OF MATERIAL FOR FULSH MOUNTING | [5 empty] | 1915
|  |  | Rate per Each | [5 empty] | 2349
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 319.8163
2668.8164
|  |  | Rate per Each | [5 empty] | 2669
Supply and fixing of DP/FP Metal Enclosure with IP 20 Protection DB Make with 1 No 20A, 10 KA DP MCB including internal connection and labour charges for Flush Mounting etc.,complete. Makes of Enclousure : Legrand / Schneider / Siemens / L&T / Crabtree Xpro / ABB / C&S MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora.
LABOUR
| 1 |  | Skilled Electrician. | 0.25 | day | 1 | day | 695 | 173.75
| 2 |  | Lineman Electric / Telephone | 0.25 | day | 1 | day | 580 | 145
| 3 |  | Mason Cl- I / Brick layer Cl- I | 0.15 | day | 1 | day | 580 | 87
|  |  | COST OF LABOUR FOR FULSH MOUNTING | [5 empty] | 405.75
MATERIAL
| 2.17.11 | b | Supply of DP/TP/FP Metal Enclosure with IP 20 Protection. | 1 | Nos | 1 | No | 645 | 645
| ELEC-2.14.1 | c | Supply of 6-32A 10KA DP MCB, C/D Curve ISI Mark. | 1 | Nos | 1 | No | 916 | 916
| 9.4.11 |  | Cement. | 5 | Kg | 1 | Kg | 9 | 45
|  |  | COST OF MATERIAL FOR FULSH MOUNTING | [5 empty] | 1606
|  |  | TOTAL COST OF MATERIAL + LABOUR FOR FULSH MOUNTING | [5 empty] | 2011.75
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 273.8998
2285.6498
|  |  | Rate per Each | [5 empty] | 2286
18 |  |  | Supply and fixing of FP Metal Enclosure with IP 20 Protection DB Make with 1 No 63A, 10 KA DP MCB including internal connection and labour charges for Flush Mounting etc.,complete. Makes of Enclousure : Legrand / Schneider / Siemens / L&T / Crabtree Xpro / ABB / C&S MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree.
LABOUR
| 1 |  | Skilled Electrician. | 0.25 | day | 1 | day | 735 | 183.75
| 2 |  | Lineman Electric / Telephone | 0.25 | day | 1 | day | 615 | 153.75
| 3 |  | Mason Cl- I / Brick layer Cl- I | 0.15 | day | 1 | day | 645 | 96.75
|  |  | COST OF LABOUR FOR FULSH MOUNTING | [5 empty] | 434.25
MATERIAL
| 2.16.11 | b | Supply of DP/TP/FP Metal Enclosure with IP 20 Protection. | 1 | Nos | 1 | No | 680 | 680
| ELEC-2.13.1 | l | Supply of 40-63A FP MCB, C/D Curve ISI Mark. | 1 | Nos | 1 | No | 3150 | 3150
| 10.4.10 |  | Cement. | 5 | Kg | 1 | Kg | 9 | 45
|  |  | COST OF MATERIAL FOR FULSH MOUNTING | [5 empty] | 3875
|  |  | TOTAL COST OF MATERIAL + LABOUR FOR FULSH MOUNTING | [5 empty] | 4309.25
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 586.7044
4895.9544
|  |  | Rate per Each | [5 empty] | 4896
8 Way SPNDB
19 |  |  | Supply and fixing of 8 Way SPN DB with IP 43 Protection as per IS:13032 with 1 No 40A DP MCB as Incommer, and 6 Nos of 20A SP MCB 10KA, C/D Curve ISI Mark as out goings, concealing in wall etc complete. DB Makes : Legrand / Schneider / Siemens / L&T / Cabtree Xpro. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree.
LABOUR
| 1 |  | Skilled Electrician. | 0.5 | day | 1 | day | 735 | 367.5
| 2 |  | Lineman Electric / Telephone | 0.5 | day | 1 | day | 615 | 307.5
| 3 |  | Mason Cl- I / Brick layer Cl- I | 0.5 | day | 1 | day | 645 | 322.5
997.5
MATERIAL
| 2.15.1 | d | Supply of 8 Way SPN DB | 1 | Nos | 1 | No | 2200 | 2200
| ELEC-2.13.1 | e | Supply of 40A DP MCB | 1 | No | 1 | No | 1560 | 1560
| ELEC-2.13.1 | a | Supply of 20A 10KA SP MCB, C/D Curve ISI Mark. | 8 | Nos | 1 | No | 325 | 2600
| ELEC-10.4.10 |  | Cement. | 12.5 | Kg | 1 | Kg | 9 | 112.5
6472.5
|  |  | TOTAL COST OF MATERIAL + LABOUR FOR FLUSH MOUNTING | FLUSH |  |  |  |  | 7470
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 1017.0405
8487.0405
|  |  | Rate per Each | [5 empty] | 8487
4 Way TPNDB (LDB)
20 |  |  | Supply and fixing of 4 Way (8+12) TPN DB Horizontal with IP 43 Protection as per IS:13032 with 1 No., of 32A FP MCB 10KA, C/D Curve ISI Mark as incomer and 12 Nos 6-32 A 10KA SP MCBs 10KA, C/D Curve ISI Mark as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. (For Lighting DBs) DB Makes :Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro / ABB / C&S MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree.
MATERIAL
| ELEC-2.16.1 | b | Supply of 4 Way (8+12) TPN DB Horizontal with IP 43 Protection as per IS:13032 and suitable for 12 Nos S.P. out goings and for 1 No 4 pole Incommer etc complete. | 1 | Nos | 1 | No | 4600 | 4600
| ELEC-2.14.1 | g | Supply of 32A FP MCB | 1 | No | 1 | No | 1970 | 1970
| ELEC-2.14.1 | a | Supply of 6-32A 10KA SP MCB, C/D Curve ISI Mark. | 12 | Nos | 1 | No | 325 | 3900
| ELEC-10.4.10 |  | Cement. | 12.5 | Kg | 1 | Kg | 9 | 112.5
10582.5
LABOUR
| 1 |  | Skilled Electrician. | 0.7 | day | 1 | day | 735 | 514.5
| 2 |  | Lineman Electric / Telephone | 1 | day | 1 | day | 615 | 615
| 3 |  | Helper (Electrical). | 1 | day | 1 | day | 615 | 615
| 4 |  | Mason Cl- I / Brick layer Cl- I | 0.5 | day | 1 | day | 645 | 322.5
2067
|  |  | TOTAL COST OF MATERIAL + LABOUR FOR FLUSH MOUNTING | FLUSH |  |  |  |  | 12649.5
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 1722.2294
14371.7294
|  |  | Rate per Each | [5 empty] | 14372
4 Way TPNDB (PDB)
21 |  |  | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 with 1 No., of 63A FP MCB 10KA, C/D Curve ISI Mark as incomer and 12 Nos 6-32 A 10 KA SP MCBs 10KA, C/D Curve ISI Mark as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. (For Power DBs) DB Makes :Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro / ABB / C&S MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree.
MATERIAL
| 2.17.1 | b | Supply of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 and suitable for 12 Nos S.P. out goings and for 1 No 4 pole Incommer etc complete. | 1 | Nos | 1 | No | 4187 | 4187
| 2.13.1 | l | Supply of 63A FP MCB. | 1 | No | 1 | No | 3150 | 3150
| ELEC-2.14.1 | a | Supply of 6-32A 10KA SP MCB, C/D Curve ISI Mark. | 12 | Nos | 1 | No | 325 | 3900
| 10.4.10 |  | Cement. | 12.5 | Kg | 1 | Kg | 9 | 112.5
11349.5
LABOUR
| 1 |  | Skilled Electrician. | 0.7 | day | 1 | day | 735 | 514.5
| 2 |  | Lineman Electric / Telephone | 1 | day | 1 | day | 615 | 615
| 3 |  | Helper (Electrical). | 1 | day | 1 | day | 615 | 615
| 4 |  | Mason Cl- I / Brick layer Cl- I | 0.5 | day | 1 | day | 645 | 322.5
2067
|  |  | TOTAL COST OF MATERIAL + LABOUR FOR FLUSH MOUNTING | FLUSH |  |  |  |  | 13416.5
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 1826.6565
15243.1565
|  |  | Rate per Each | [5 empty] | 15243
4 Way VTPN DB
22 |  |  | Supply and fixing of 4 Way VTPN DB with IP 43 Protection as per IS:13032 with 1 No., of 125A 4P MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted as incomer with 4 Nos of 63A TP MCBs 10KA, C/D Curve ISI Mark as Out goings including internal connections and labour charges for FLUSH Mounting etc., complete. DB Makes :Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. MCCB Makes : L&T- D sine / Schneider-NS NSX / Legrand -DP X3 / Siemens-3V / Hager-h3 / C&S -Winbreak.
LABOUR
| 1 |  | Skilled Electrician. | 1.25 | day | 1 | day | 735 | 918.75
| 2 |  | Lineman Electric / Telephone | 1.5 | day | 1 | day | 615 | 922.5
| 3 |  | Helper (Electrical). | 1.5 | day | 1 | day | 615 | 922.5
|  |  | COST OF LABOUR FOR SURFACE MOUNTING | [5 empty] | 2763.75
MATERIAL
| 2.17.3 | b | Supply of 4 Way VTPN DB | 1 | Nos | 1 | No | 15830 | 15830
| 2.13.1 | i | Supply of 40-63A 10KA TP MCB, | 4 | Nos | 1 | No | 2375 | 9500
| 2.7.1 | d | Supply of 125A 4P MCCB,
|  |  | Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3VL / Hager- h3/C&S -Winbreak. | 1 | Nos | 1 | No | 13770 | 13770
|  |  | COST OF MATERIAL FOR SURFACE MOUNTING | [5 empty] | 39100
|  |  | TOTAL COST OF MATERIAL + LABOUR FOR SURFACE MOUNTING | SURFACE |  |  |  |  | 41863.75
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 5699.7496
47563.4996
|  |  | Rate per Each | [5 empty] | 47564
4 Way VTPN DB
Supply and fixing of 4 Way VTPN DB with IP 43 Protection as per IS:13032 with 1 No., of 63A 4P MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted as incomer with 4 Nos of 63A TP MCBs 10KA, C/D Curve ISI Mark as Out goings including internal connections and labour charges for FLUSH Mounting etc., complete. DB Makes : Legrand / Schneider / Siemens / L&T / Cabtree Xpro. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. MCCB Makes : Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak.
LABOUR
| 1 |  | Skilled Electrician. | 1.25 | day | 1 | day | 660 | 825
| 2 |  | Lineman Electric / Telephone | 1.5 | day | 1 | day | 550 | 825
| 3 |  | Helper (Electrical). | 1.5 | day | 1 | day | 550 | 825
|  |  | COST OF LABOUR FOR SURFACE MOUNTING | [5 empty] | 2475
MATERIAL
| 2.17.3 | a | Supply of 4 Way VTPN DB | 1 | Nos | 1 | No | 13110 | 13110
| 2.14.1 | f | Supply of 40-63A 10KA TP MCB, | 4 | Nos | 1 | No | 2064 | 8256
| 2.8.1 | b | Supply of 63A 4P MCCB,
|  |  | Makes : L&T- D shine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3VL / Hager- h3/C&S -Winbreak. | 1 | Nos | 1 | No | 9781 | 9781
|  |  | COST OF MATERIAL FOR SURFACE MOUNTING | [5 empty] | 31147
|  |  | TOTAL COST OF MATERIAL + LABOUR FOR SURFACE MOUNTING | SURFACE |  |  |  |  | 33622
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 4577.6353
38199.6353
|  |  | Rate per Each | [5 empty] | 38200
8 Way VTPN DB
23 |  |  | Supply and fixing of 8 Way VTPN DB with IP 43 Protection as per IS:13032 with 1 No., of 125A 4P MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted as incomer with 8 Nos of 63A TP MCBs 10KA, C/D Curve ISI Mark as Out goings including internal connections and labour charges for FLUSH Mounting etc., complete. DB Makes :Legrand / Schneider / Siemens / L&T / Hager / Cabtree Xpro. MCB Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. MCCB Makes : L&T- D sine / Schneider-NS NSX / Legrand -DP X3 / Siemens-3V / Hager-h3 / C&S -Winbreak.
LABOUR
| 1 |  | Skilled Electrician. | 1.25 | day | 1 | day | 735 | 918.75
| 2 |  | Lineman Electric / Telephone | 1.5 | day | 1 | day | 615 | 922.5
| 3 |  | Helper (Electrical). | 1.5 | day | 1 | day | 615 | 922.5
|  |  | COST OF LABOUR FOR SURFACE MOUNTING | [5 empty] | 2763.75
MATERIAL
| 2.17.3 | b | Supply of 8 Way VTPN DB | 1 | Nos | 1 | No | 19900 | 19900
| 2.14.1 | f | Supply of 40-63A 10KA TP MCB, | 8 | Nos | 1 | No | 2375 | 19000
| 2.8.1 | d | Supply of 125A 4P MCCB,
|  |  | Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3VL / Hager- h3/C&S -Winbreak. | 1 | Nos | 1 | No | 13770 | 13770
|  |  | COST OF MATERIAL FOR SURFACE MOUNTING | [5 empty] | 52670
|  |  | TOTAL COST OF MATERIAL + LABOUR FOR SURFACE MOUNTING | SURFACE |  |  |  |  | 55433.75
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 7547.3051
62981.0551
|  |  | Rate per Each | [5 empty] | 62982
23 | AR |  | Supply and fixing of cable adopteres box with cover for DBs including, massanory work etc., complete., Makes : Legrand / Schneider. | 1 | No | 1 | No | 600 | 600
63A MCCB Switch
24 |  |  | Supply installation testing and commissioning of 3 phase and neutral 415V free mounted indoor LT panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of 63A 4P 25 KA MCCB Switch. The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3VL / Hager-h3/C&S -Winbreak.
MATERIAL
|  |  | Fabrication: | L | H | D
|  |  | Size of panel : in Mtr | 0.3 | 0.3 | 0.3
|  |  | Front and back faces | 2 | 0.3 | 0.3 | 0.18
|  |  | Top and bottom faces | 2 | 0.3 | 0.3 | 0.18
|  |  | Side faces | 2 | 0.3 | 0.3 | 0.18
|  |  | Sub total |  |  |  | 0.54
|  |  | Add extra 10 % for wastage |  |  |  | 0.054
|  |  | Total |  |  |  | 0.594
| 7.13.1 | a+b/2 | Fabrication and erection of 14 / 16 SWG CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges. | 0.594 | Sqmt | 1 | Sqmt | 5978 | 3550.932 |  | 10868
|  |  | Incomer & Out goings | [7 empty] | 5434
| 2.7.1 | b | Supply of 63A / 60A 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 1 | Nos | 1 | No | 10790 | 10790
14340.932
|  |  | Transportation | 0.01 |  |  |  |  | 143.4093
|  |  | Control wiring with flexible wires and connections to MCBs with required lugs including commissioning and testing etc | 0.005 |  |  |  |  | 71.7047
|  |  | TOTAL COST OF MATERIAL AND LABOUR | [5 empty] | 14556.046
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 1981.8057
16537.8516
|  |  | Rate per Each | [5 empty] | 16538
125A MCCB Switch
25 |  |  | Supply installation testing and commissioning of 3 phase and neutral 415V free mounted indoor LT panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of 125A 4P MCCB Switch. The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3VL / Hager-h3/C&S -Winbreak.
|  |  | Fabrication: | L | H | D
|  |  | Size of panel : in Mtr | 0.45 | 0.45 | 0.5
|  |  | Front and back faces | 2 | 0.45 | 0.45 | 0.405
|  |  | Top and bottom faces | 2 | 0.45 | 0.5 | 0.45
|  |  | Side faces | 2 | 0.45 | 0.5 | 0.45
|  |  | Sub total |  |  |  | 1.305
|  |  | Add extra 10 % for wastage |  |  |  | 0.1305
|  |  | Total |  |  |  | 1.4355
| 7.13.1 | a+b/2 | Fabrication and erection of 14 / 16 SWG CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges. | 1.4355 | Sqmtr | 1 | Sqmtr | 5978 | 8581.419 | 3*25
Incomer & Out goings
| 2.7.1 | d | Supply of 125A 4Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted. | 1 | Nos | 1 | No | 13770 | 13770
22351.419
|  |  | Transportation | 0.01 |  |  |  |  | 223.5142
|  |  | Control wiring with flexible wires and connections to MCBs with required lugs including commissioning and testing etc | 0.005 |  |  |  |  | 111.7571
|  |  | TOTAL COST OF MATERIAL AND LABOUR | [5 empty] | 22686.6903
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 3088.7929
25775.4832
|  |  | Rate per Each | [5 empty] | 25775
250A 4Pole MCCB
26 |  |  | Supply installation testing and commissioning of 3 phase and neutral 415V free mounted indoor LT panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of 250 A 4P MCCB Switch. The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3VL / Hager-h3/C&S -Winbreak.
|  |  | Fabrication: | L | H | D
|  |  | Size of panel : in Mtr | 0.6 | 0.6 | 0.5
|  |  | Front and back faces | 2 | 0.6 | 0.6 | 0.72
|  |  | Top and bottom faces | 2 | 0.6 | 0.5 | 0.6
|  |  | Side faces | 2 | 0.6 | 0.5 | 0.6
|  |  | Sub total |  |  |  | 1.92
|  |  | Add extra 10 % for wastage |  |  |  | 0.192
|  |  | Total |  |  |  | 2.112
| 7.13.1 | a+b/2 | Fabrication and erection of 14 / 16 SWG CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges. | 2.112 | Sqmtr | 1 | Sqmtr | 5978 | 12625.536 | 3*25
| 2.8.1 | h | Supply of 250A 4Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 35/36 KA with thermal magnetic release Panel Mounted. | 1 | Nos | 1 | No | 32940 | 32940
45565.536
|  |  | Transportation | 0.01 |  |  |  |  | 455.6554
|  |  | Control wiring with flexible wires and connections to MCBs with required lugs including commissioning and testing etc | 0.005 |  |  |  |  | 227.8277
|  |  | TOTAL COST OF MATERIAL AND LABOUR | [5 empty] | 46249.019
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 6296.8039
52545.823
|  |  | Rate per Each | [5 empty] | 52546
400A 4Pole MCCB
Supply installation testing and commissioning of 3 phase and neutral 415V free mounted indoor LT panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of 400 A 4P MCCB Switch. The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3VL / Hager-h3/C&S -Winbreak.
|  |  | Fabrication: | L | H | D |  | Nos
|  |  | Size of panel : in Mtr | 0.75 | 0.75 | 0.45
|  |  | Front and back faces |  | 0.75 |  | 1.5 | 2
|  |  | Top and bottom faces |  | 0.75 | 0.45 | 0.675 | 2
|  |  | Side faces |  | 0.75 | 0.45 | 0.675 | 2
|  |  | Sub total |  |  |  | 2.85
|  |  | Add extra 10 % for wastage |  |  |  | 0.285
|  |  | Total |  |  |  | 3.135
| 7.13.1 | a+b/2 | Fabrication and erection of 14 / 16 SWG CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges. | 3.135 | Sqmtr | 1 | Sqmtr | 4940 | 15486.9 | 3*25
| 2.8.1 | j | Supply of 400A 4Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 35/36 KA with thermal magnetic release Panel Mounted. | 1 | Nos | 1 | No | 37611 | 37611
53097.9
|  |  | Bus bar arrangement with insulators | 0 |  |  |  |  | 0
|  |  | Hard ware such as base channel etc. | 0 |  |  |  |  | 0
|  |  | Transportation | 0.01 |  |  |  |  | 530.979
|  |  | Control wiring with flexible wires and connections to MCBs with required lugs including commissioning and testing etc | 0.005 |  |  |  |  | 265.4895
|  |  | TOTAL COST OF MATERIAL AND LABOUR | [5 empty] | 53894.3685
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 7337.7183
61232.0868
|  |  | Rate per Each | [5 empty] | 61232
Supply,transpotation,installation,testing and commissioning of HT OUTDOOR type single panel switchgear with VCB of floor mounted, metal clad 11KV, 630A, not less than 16 -KA (350 / 500 MVA) VCB Panel, with 1No VCBs totally enclosed and horizantal drawout type, horizontal isolation type breaker as per IS 13118 as amended upto date and additional specifications having capacities as mentioned below , single break trip free mechanism, motorised/manually charged and auto manually closing breaker suitable for use on 12KV , 3phase, 50HZ AC supply with self contained fully interlocked rackin and rackout mechanism air insulated allumium Busbars of 630A capacity, Breaker featured with ON/OFF indicator with hand trip device, spring relief coil, shunt trip coil and auxillary switch of 6NO + 6NC and equiped with following switchgears and accessories incomming connections suitable for 3x95Sqmm XLPE 11KV Cable as required etc complete with adaptor box for outgoing termination.
| 7.16.15 |  | Single VCB PANEL | 1 | Nos | 1 | No | 658845 | 658845
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 89701.7467
748546.7467
|  |  | Rate per Each | [5 empty] | 748547
V |  |  | Earthings
27 |  |  | Providing independent earthing for Important equipment with 40mm dia 'B' class 2.5m long G.I pipe and 19mm dia 'B' class G.I pipe of 0.3mtr. long connected with reducer providing G.I funnel with mesh enclosed in C.C/ brick massonry chamber of 450m x 450m x 400mm with R.C.C. Slab cover duly providing staggered holes filling with 20Kg Salt and 40Kg Charcoal or 40Kg bentonite powder from the bottom of the pipe giving earth connection from electrode through G.I strip of 40 x 6mm x 200mm length with all accessories and labour charges complete, as per IS specifications 732/1982 (Part II)
| 8.16.7 |  | Earthing Cost | 1 | No | 1 | No | 5840 | 5840
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 795.116
6635.116
|  |  | Rate per Each | [5 empty] | 6635
28 |  |  | Providing independent earthing by exacavating a pit to a depth of 2.25Mtr in all soils as per size specified in the data for Sophisticated Electronic equipment with 600mm x 600mm x 3.15mm thick copper plate rigidly fixed to 19mm dia 'B' Class G.I Pipe of 2.5Mtr lengthwith funnel as per National Electric Code and earth connection from electrode GI strip of 40mm x 5mm x 200mm length to be bolted with nut bolts to G.I.pipe including 25mm x 3mm copper strip of 6Mtrs length connected from plate to GI strip including filling with 20Kg Salt and 40Kg Charcoal or 40Kg bentonite powder from the bottom of the pipe and providing CC / Brick massonry chamber 450mmX450mmX400mm and covered with R.C.C. Slab including all accessories and labour charges etc complete as per IS specification 732/1982 (Part II).
| 8.16.8 |  | Earthing Cost | 1 | No | 1 | No | 16670 | 16670
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 2269.6205
18939.6205
|  |  | Rate per Each | [5 empty] | 18940
29 |  |  | Supply and Run of 25mm x 6mm G.I Strip including cost of all accessories and labour charges etc., complete. (1.18Kgs/1Mtr)
a) Labour charges :
| 1 |  | Skilled Electrician. | 1 | day | 1 | day | 735 | 735
| 3 |  | Helper (Electrical). | 1 | day | 1 | day | 615 | 615
|  |  | Labour for 100 Mtrs | [5 empty] | 1350
|  |  | Labour for 1 Mtr | [5 empty] | 13.5
b) Material
| 10.3.6 |  | G.I. Strip / Plate / Wire (per K. G). | 118 | Kgs | 1 | Kg | 108 | 12744
Sundries.
|  |  | Cost of Material for 100 Metres | [5 empty] | 12744
|  |  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 127.44
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 140.9
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 19.1835
160.0835
|  |  | Rate per Meter | [5 empty] | 160
30 |  |  | Supply and Run of 50mm x 6mm G.I Strip including cost of all accessories and labour charges etc., complete. (2.36 Kg / Mtr)
a) Labour charges :
| 1 |  | Skilled Electrician. | 2 | day | 1 | day | 735 | 1470
| 3 |  | Helper (Electrical). | 2 | day | 1 | day | 615 | 1230
|  |  | Labour for 100 Mtrs | [5 empty] | 2700
|  |  | Labour for 1 Mtr | [5 empty] | 27
b) Material
| 10.3.6 |  | G.I. Strip / Plate / Wire (per K. G). | 236 | Kgs | 1 | Kg | 108 | 25488
|  |  | Sundries. | [5 empty] | 200
|  |  | Cost of Material for 100 Metres | [5 empty] | 25688
|  |  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 256.88
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 283.8
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 38.6394
322.4394
|  |  | Rate per Meter | [5 empty] | 322
31 |  |  | Supply and Run of 25mm x 3mm copper strip (Cuurrent Carrying Capacity 270A) including cost of all accessories and labour charges etc., complete. (0.663Kgs/1Mtr)
a) Labour charges :
| 1 |  | Skilled Electrician. | 1 | day | 1 | day | 735 | 735
| 3 |  | Helper (Electrical). | 1.5 | day | 1 | day | 615 | 922.5
|  |  | Labour for 100 Mtrs | [5 empty] | 1657.5
|  |  | Labour for 1 Mtr | [5 empty] | 16.575
b) Material
| 10.3.1 |  | Copper plate / Copper strip (Per K.G). | 66.3 | Kgs | 1 | Kg | 1148 | 76112.4
Sundries.
|  |  | Cost of Material for 100 Metres | [5 empty] | 76112.4
|  |  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 761.124
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 777.6
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 105.8702
883.4702
|  |  | Rate per Meter | [5 empty] | 883
Supply and Run of 25mm x 6mm copper strip (Cuurrent Carrying Capacity 270A) including cost of all accessories and labour charges etc., complete. (1.34 Kg / Mtr)
a) Labour charges :
| 1 |  | Skilled Electrician. | 1 | day | 1 | day | 695 | 695
| 3 |  | Helper (Electrical). | 1.75 | day | 1 | day | 580 | 1015
|  |  | Labour for 100 Mtrs | [5 empty] | 1710
|  |  | Labour for 1 Mtr | [5 empty] | 17.1
b) Material
| ELEC-9.3.1 |  | Copper plate / Copper strip (Per K.G). | 134 | Kgs | 1 | Kg | 1044 | 139896
Sundries.
|  |  | Cost of Material for 100 Metres | [5 empty] | 139896
|  |  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 1398.96
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 1416
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 192.7884
1608.7884
|  |  | Rate per Meter | [5 empty] | 1609
32 |  |  | Supply and Run of No.8 SWG G.I wire including cost of all accessories and labour charges etc., complete. (0.104Kgs/1Mtr)
a) Labour charges :
| 3 |  | Helper (Electrical). | 2 | day | 1 | day | 615 | 1230
|  |  | Labour for 100 Mtrs | [5 empty] | 1230
|  |  | Labour for 1 Mtr | [5 empty] | 12.3
b) Material
| 9.3.6 |  | G.I. Strip / Plate / Wire (per K. G). | 10.4 | Kgs | 1 | Kg | 108 | 1123.2
| 10.1.4 |  | U Nails. | 150 | Nos | 100 | Nos | 44 | 66
Sundries.
|  |  | Cost of Material for 100 Metres | [5 empty] | 1189.2
|  |  | Cost of Material Rate per Mtr= C/100 | [5 empty] | 11.892
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 24.1
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 3.2812
27.3812
|  |  | Rate per Meter | [5 empty] | 27
VI |  |  | FIXTURES
33 |  |  | Supply, transportation and fixing of 22W +/ 10% , >/ 2300 lumens, 1200mm length LED light housing made with alluminium anodised body, wide operating voltage with PF≥0.9, Surge protection: > 2KV, THD<10%, with inbuilt driver and frosted cover CCT: 3000K - 6500K as desired by the department as per IS, minimum CRI≥80 etc., complete with 5 years warranty with BIS Certification with BIS Certification LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Goldmedal. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs.
a) Labour charges
| 1 |  | Skilled Electrician. | 0.1 | day | 1 | day | 735 | 73.5
| 2 |  | Lineman Electric / Telephone | 0.1 | day | 1 | day | 615 | 61.5
|  |  | Labour for 1 No | [5 empty] | 135
b) Material
| 1.5.4 |  | Supply of 23 / 0060 twin core twisted / flat heavy Copper wire.
|  |  | Makes : Finolex / RR Kabel / Havells / Polycab / GM / Million / V-Guard / Gold Medal / Kundancab / HPL / RPG / Nandicab / Nakoda / Payal / Finecab / Gemini / Vimal / Suncab | 1 | Mtr | 100 | Mtrs | 1325 | 13.25
| 1.4.4 | d | Supply of No.8 Screws of 35/38mm. | 2 | Nos | 100 | Nos | 135 | 2.7
| 10.1.2 |  | Rawl Plugs. | 2 | Nos | 100 | Nos | 45 | 0.9
|  |  | Fixing arrangements on wall with required support on wall | 2 | Nos | 1 | Nos | 5 | 10
| 3.3.16 |  | 22W, +/ 10% , >/ 2300 lumens, 1200mm length LED light | 1 | Nos | 1 | Nos | 615 | 615
|  |  | Cost of Material | [5 empty] | 641.85
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 776
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 105.6524
881.6524
|  |  | Rate per Each | [5 empty] | 882
36W, 2' x2' (600mm x 600mm) Recessed / Surface mounted LED luminaire
34 |  |  | Supply, transportation and fixing 32-36W (>=3240 Lumens) 2' x2' (600mm x 600mm) slim panel Recessed / Surface LED luminaire Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >90 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% with non integrated driver etc., complete with 2 years warranty with BIS Certification. LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Goldmedal.. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs.
a) Labour charges
| 1 |  | Skilled Electrician. | 0.05 | day | 1 | day | 735 | 36.75
| 3 |  | Helper (Electrical). | 0.125 | day | 1 | day | 615 | 76.875
|  |  | Labour for 1 No | [5 empty] | 113.625
b) Material
| ELEC-1.5.4 |  | Supply of 23 / 0060 twin core twisted / flat heavy Copper wire. | 2 | Mtr | 100 | Mtrs | 1325 | 26.5
|  |  | Alluminium Flat (As per requirement) | [5 empty] | 50
| ELEC-3.3.17 | a | Supply and Transportation of 36W Edge lit, 2' x 2' (600mm x 600mm) slim panel LED luminaire | 1 | Nos | 1 | Nos | 2780 | 2780
|  |  | Cost of Material | [5 empty] | 2856.5
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 2970
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 404.3655
3374.3655
|  |  | Rate per Each | [5 empty] | 3374
12W Down lighter Recessed / Surface Mounting
Supply, transportation and fixing 12 W +/-10% (>= 1200 Lumens) LED Down Light Recessed / Surface mounting round / square with housing made of Powder coated Pressure die cast aluminium housing with extended heat sink, with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor > 0.9, Surge protection: > 2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI >80, and THD is less than 15% etc., complete with 5 years warranty with BIS Certification. LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs.
a) Labour charges
| 1 |  | Skilled Electrician. | 0.066 | day | 1 | day | 695 | 45.87
| 2 |  | Lineman Electric / Telephone | 0 | day | 1 | day | 580 | 0
| 3 |  | Helper (Electrical). | 0.1 | day | 1 | day | 580 | 58
|  |  | Labour for 1 No | [5 empty] | 103.87
b) Material
| 1.5.5 |  | Supply of 23 / 0060 twin core twisted / flat heavy Copper wire. | 1 | Mtr | 100 | Mtrs | 1260 | 12.6
| 1.4.4 | d | Supply of No.8 Screws of 35/38mm. | 2 | Nos | 100 | Nos | 128 | 2.56
| 9.1.2 |  | Rawl Plugs. | 2 | Nos | 100 | Nos | 45 | 0.9
|  |  | Fixing arrangements on wall with required support on wall | 0 | Nos | 1 | Nos | 5 | 0
| 3.5.4 | a | 12W Down lighter with system lumens of 1000lm, suitable for Recessed / Surface | 1 | Nos | 1 | Nos | 1283 | 1283
|  |  | Cost of Material | [5 empty] | 1299.06
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 1402.93
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 191.0089
1593.9389
|  |  | Rate per Each | [5 empty] | 1594
18W Down lighter Recessed / Surface Mounting
35 |  |  | Supply, transportation and fixing of 18 W +/-10% (>= 1800 Lumens) LED Down Light Recessed / Surface mounting round / square with housing made of Powder coated Pressure die cast aluminium housing with extended heat sink, with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor > 0.9, Surge protection: > 2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI >80, and THD is less than 15% etc., complete with 5 years warranty with BIS Certification. LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Goldmedal.. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs.
a) Labour charges
| 1 |  | Skilled Electrician. | 0.066 | day | 1 | day | 735 | 48.51
| 2 |  | Lineman Electric / Telephone | 0 | day | 1 | day | 615 | 0
| 3 |  | Helper (Electrical). | 0.1 | day | 1 | day | 615 | 61.5
|  |  | Labour for 1 No | [5 empty] | 110.01
b) Material
| 1.5.5 |  | Supply of 23 / 0060 twin core twisted / flat heavy Copper wire. | 1 | Mtr | 100 | Mtrs | 1325 | 13.25
| 1.4.4 |  | Supply of No.8 Screws of 35/38mm. | 2 | Nos | 100 | Nos | 135 | 2.7
| 10.1.2 |  | Rawl Plugs. | 2 | Nos | 100 | Nos | 45 | 0.9
|  |  | Fixing arrangements on wall with required support on wall | 0 | Nos | 1 | Nos | 5 | 0
| 3.3.4 | c | 18 W +/-10% (>= 1800 Lumens) | 1 | Nos | 1 | Nos | 1500 | 1500
|  |  | Cost of Material | [5 empty] | 1516.85
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 1626.86
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 221.497
1848.357
|  |  | Rate per Each | [5 empty] | 1848
36 |  |  | Supply, Transportation and fixing of 60 W +/-10% (>6000 Lumens) LED HIgh Bay Luminaire with high power COB LED made of pressure diecast alluminium housing with powder coated,Supply Input voltage 120 - 270 V AC, P.F > 0.90, high power LED's, System efficacy >100 lm / W and junction temprature < 70°C, with Ingrees protection IP65, IK05, Driver surge protection 4KV, external Surge protection ≥ 5KV with wide/ Narrow beam optics, THD<10% at 110 Volts AC, driver efficiency >90%, CCT: 3000K - 5700K, minimum CRI>70, etc., with required wiring complete with BIS certification with warranty 5 years warranty. The contractor has to furnish the manufacturer warranty letter, LM 79 and LM 80 certificates. LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL / Goldmedal.. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs.
a) Labour charges
| 1 |  | Skilled Electrician. | 0.2 | day | 1 | day | 735 | 147
| 2 |  | Lineman Electric / Telephone | 0.2 | day | 1 | day | 615 | 123
|  |  | Labour for 1 No | [5 empty] | 270
b) Material
| 1.6.3 | b | Supply of 3 Core 2.5 Sqmm Flat Copper cable | 4 | Mtrs | 100 | Mtrs | 12400 | 496
| 4 |  | Spl. MS Clamps with required fixing arrangements as directed. |  |  |  |  | LS | 154
| 5 |  | M.S flat and welding charges |  |  |  |  | LS | 100
| 3.5.7 | a | Supply of 60W LED energy saving envoironment friendly & Robust open type vertical Highbay/ Mediumbay with high powerCOB LED as light source | 1 | Nos | 1 | Nos | 6560 | 6560
|  |  | Cost of Material for 1 No | [5 empty] | 7310
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 7668
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 1043.9982
8711.9982
|  |  | Rate per each | [5 empty] | 8712
BH/SBH
37 |  |  | Supply, transportation and fixing ISI mark batten holder / slanting holder Makes : Anchor / Gold Medal Olive / Million Zoom in lieu of ceiling rose of light point complete with all connections and all labour charges with 5W LED Lamp LED Lamp MAKES: Phillips / OSRAM / Crompton / Eveready / Bajaj / Havells / Halonix / Jaquar / C&S / GM / / Gold Medal / Million.
a) Labour charges :
| 1 |  | Skilled Electrician. | 0.03 | day | 1 | day | 735 | 22.05
| 3 |  | Helper (Electrical). | 0.03 | day | 1 | day | 615 | 18.45
|  |  | Labour for 1 No | [5 empty] | 40.5
b) Material
| 1.7.1 | n | Supply of BH / SBH of Makes : GM G Home / Gold Medal Olive / Million Zoom / Anchor Penta Cherry / Great white Omega / HPL / Vimal / CPL. | 1 | No | 1 | No | 25 | 25
| 3.4.1 | c | Supply of 5 W LED Lamp | 1 | No | 1 | No | 92 | 92
| 1.7.1 | m | Less Cost of 3 Plate Jumbo Ceiling Rose Makes : Anchor / Gold Medal Olive / Million Zoom. | 1 | No | -1 | No | 25 | -25
|  |  | Cost of Material | [5 empty] | 92
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 132
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 17.9718
149.9718
|  |  | Rate per Each | [5 empty] | 150
Supply and fixing of Buzzer Calling Bell of Makes : GM / Million / Gold Medal on 4"x7" decolam block including giving connections, cost of all accessories and labour charges etc., complete.
a) Labour charges :
| 1 |  | Skilled Electrician. | 0.05 | day | 1 | day | 695 | 34.75
| 3 |  | Helper (Electrical). | 0.05 | day | 1 | day | 580 | 29
|  |  | Labour for 1 No | [5 empty] | 63.75
b) Material
| 1.4.2 | b | Supply of Decolam Board of Size 4" x 7". | 1 | Nos | 1 | No | 27 | 27
| 1.7.2 | a | Supply of Buzzer. Makes : GM / Million / Gold Medal / Anchor / Great white. | 1 | Nos | 1 | No | 55 | 55
|  |  | Cost of Material | [5 empty] | 82
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 145
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 19.7417
164.7417
|  |  | Rate per Each | [5 empty] | 165
Supply and fixing of Electronic Musical bell Makes : GM / Million / Gold Medal on 4"x7" decolam block including giving connections, cost of all accessories and labour charges etc., complete.
a) Labour charges :
| 1 |  | Skilled Electrician. | 0.05 | day | 1 | day | 695 | 34.75
| 3 |  | Helper (Electrical). | 0.055 | day | 1 | day | 580 | 31.9
|  |  | Labour for 1 No | [5 empty] | 66.65
b) Material
| 1.4.2 | b | Supply of Decolam Board of Size 4" x 7" | 1 | Nos | 1 | No | 27 | 27
| 1.7.2 | c | Supply of Electronic Musical Bell. Makes : GM / Million / Gold Medal / Anchor / Great white. | 1 | Nos | 1 | No | 266 | 266
|  |  | Cost of Material | [5 empty] | 293
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 359
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 48.8778
407.8778
|  |  | Rate per Each | [5 empty] | 408
VII |  |  | Ceiling Fans
38 | 5.1.1 |  | Supply, Transportation of energy efficient fan, 1200 mm sweep, aluminium body, consuming 28 W, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) motor, class of insulation: B, 3 no's blades, 30 cm long down rod, 2 no's canopies, shackle'kit, safety rope, copper winding, Power Factor greater than 0.90, Service Value (CMMAV) greater than 8.5, Air delivery minimum 235 CMM, 350 RPM( tolerance as per IS:374-2019), THD less than 10%. with remote or compatible to electronic step type regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise=75 degree C(max), insulation resistance more than 2 mega ohm, suitable for 230V, 50 HZ, single phase AC supply, earthing etc., including all standard accessories etc., complete. Makes : Atomberg (Efficio ) / Havells / Orient / Halonix | Each | 1 | 1 | Nos | 3085 | 3085
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 420.0227
3505.0228
|  |  | Rate per Each | [5 empty] | 3505
| 5.1.4 |  | Supply, Transportation of energy efficient decorative fan, 1400 mm sweep, aluminium body, consuming 35 W, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) motor, class of insulation: B, 3 no's blades, 30 cm long down rod, 2 no's canopies, shackle kit, safety rope, copper winding, Power Factor greater than 0.90, Service Value (CMM/W) greater than 7.8, Air delivery minimum 270 CMM, 275 RPM (tolerance as per IS:374-2019), THD less than 10%, remote or compatible to electronic step type regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise = 75 degree C (max), insulation resistance more than 2 mega ohm, suitable for 230V, 50 HZ, single phase AC supply, earthing etc., complete. Makes : Atomberg (Efficio + ) / Havells / Orient / RR / Halonix | Each | 1 | 1 | Nos | 3366 | 3366
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 458.2809
3824.2809
|  |  | Rate per Each | [5 empty] | 3824
39 |  |  | Supply and fixing of Modular type Stepped electronic regulator for sweep AC ceiling fans of 1200mm / 1400mm complete with connections. Makes : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Crabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T Englaze.
a) Labour charges
| 2 |  | Lineman Electric / Telephone | 0.05 | Nos | 1 | Nos | 615 | 30.75
|  |  | Labour for 1 No | [5 empty] | 30.75
b) Material
| 1.9.1 | n | Electronic Fan Regulator | 1 | Nos | 1 | Nos | 650 | 650
|  |  | Cost of Material for 1 No | [5 empty] | 650
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 680
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 92.582
772.582
|  |  | Rate per Each | [5 empty] | 773
40 |  |  | Labour charges for fixing of ceiling fan and regulator including transportation and giving connections with twin core wire etc., complete. Makes : Finolex / RR Kabel / Havells / Polycab / GM / Million / V-Guard / Gold Medal / HPL / RPG.
a) Labour charges
| 1 |  | Skilled Electrician. | 0.125 | day | 1 | day | 735 | 91.875
| 2 |  | Helper (Electrical). | 0.125 | day | 1 | day | 615 | 76.875
|  |  | Labour for 1 No | [5 empty] | 168.75
b) Material
| 1.5.5 |  | Supply of 23 / 0060 twin core twisted / flat heavy Copper wire. | 1 | Mtrs | 100 | Mtrs | 1325 | 13.25
|  |  | Cost of Material for fixing fan | [5 empty] | 13.25
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 182
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 24.7793
206.7793
|  |  | Rate per Each | [5 empty] | 207
41 |  |  | Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete
a) Labour charges
| 3 |  | Helper (Electrical). | 0.1 | day | 1 | day | 615 | 61.5
|  |  | Labour for 1 No | [5 empty] | 61.5
b) Material
| 10.1.21 |  | 19/20mm steel tube down rod with bolts & nuts for fan with maching colour. | 1 | Mtrs | 1 | Mtrs | 116 | 116
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 177.5
|  |  | Less cost of fan down rod supplied with new fan of about 9" in length equal to 0.23 Metre at above rate | 0.23 | Mtrs | 1 | Mtrs | 116 | 26.68
150.82
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 24.1666
174.9866
|  |  | Rate per Each | [5 empty] | 175
42 | 5.1.14 | b | Supply of 12" (300mm) Light duty exhaust fan with metal blades etc complete Makes : Crompton / Havells Ventilair-DB /Orient hill air. | Each | 1 | 1 | Nos | 1730 | 1730
|  |  | Transportation | 0.02 |  |  |  |  | 34.6
|  |  | Sub total | [5 empty] | 1764.6
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 240.2503
2004.8503
|  |  | Rate per Each | [5 empty] | 2005
43 |  |  | Supply,Transportation of 12" (300mm) ISI, 900 RPM Heavy duty exhaust fan with metallic blades wiremesh with all accessories etc complete Makes : Crompton / Almonard / Havells Turbo Force SP.
| 5.1.11 | a | Supply of 12" (300mm) ISI, 900 RPM Heavy duty exhaust fan | Each | 1 | 1 | Nos | 3410 | 3410
|  |  | Transportation | 0.02 |  |  |  |  | 68.2
3478.2
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 473.5569
3951.7569
|  |  | Rate per Each | [5 empty] | 3952
44 |  |  | Labour charges for fixing the exhaust fan in wall with necessary connections and masonary work of making hole, finishing etc., complete. Makes : Finolex / RR Kabel / Havells / Polycab / GM / Million / V-Guard / Gold Medal / Kundancab / HPL / RPG / Nakoda / Payal / Finecab
a) Labour charges
| 1 |  | Skilled Electrician. | 0.25 | day | 1 | day | 735 | 183.75
| 2 |  | Lineman Electric / Telephone | 0.25 | day | 1 | day | 615 | 153.75
| 4 |  | Mason Cl- I / Brick layer Cl- I | 0.25 | day | 1 | day | 645 | 161.25
|  |  | Labour for 1 No | [5 empty] | 498.75
| 1.5.5 |  | Supply of 23 / 0060 twin core twisted / flat heavy Copper wire. | 1 | Mtrs | 100 | Mtrs | 1325 | 13.25
| 10.4.11 |  | Cement. | 25 | Kg | 1 | Kg | 9 | 225
|  |  | Sundries such as Sand, Bolt, Nuts etc. | 1 | Job | 1 | Job | 10 | 10
|  |  | Cost of Material for fixing fan | [5 empty] | 248.25
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 747
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 101.704
848.7041
|  |  | Rate per Each | [5 empty] | 849
45 |  |  | Supply and fixing of GI louver shutter including GI mesh to avoid birds entry with necessary materials suitable for 300mm(12 inches) Exhaust fan.
| 5.1.17 | b | louver shutter including GI mesh to avoid birds entry with necessary materials suitable for 300mm | Each | 1 | 1 | Nos | 180 | 180
180
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 24.507
204.507
|  |  | Rate per Each | [5 empty] | 205
Mirror Lights
Supply, transportation and fixing Supply of 1 x 11W Mirror light with all standard accessories diffuser in lieu of ceiling rose of light point complete with all connections and all labour charges Makes:G.E. Venture / Phillips / Crompton / Bajaj.
a) Labour charges :
| 1 |  | Skilled Electrician. | 0.05 | day | 1 | day | 660 | 33
| 3 |  | Helper (Electrical). | 0.05 | day | 1 | day | 550 | 27.5
|  |  | Labour for 1 No | [5 empty] | 60.5
b) Material
| ELEC-3.6.1 | a | Supply of 1 x 11W Mirror light with all standard accessories diffuser | 1 | No | 1 | No | 544 | 544 | 21-22 Rate
| 1.7 | a | Less Cost of 3 Plate Jumbo Ceiling Rose Makes : Anchor / Gold Medal Olive / Million Zoom. | 1 | No | -1 | No | 23 | -23
|  |  | Cost of Material | [5 empty] | 521
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 581
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 79.1031
660.1032
|  |  | Rate per Each | [5 empty] | 660
2 feet Tube Lights
46 |  |  | Supply, transportation and fixing of 10W, 1000 lumens, 600mm length LED batten tube light, housing made with PC body, wide operating voltage with Single / double side connection, PF≥0.9, Surge protection: > 2KV, THD<15%, with inbuilt driver and frosted cover CCT: 3000K - 6500K as desired by the department and as per IS specifications, minimum CRI≥80,.etc complete with 5 years warranty with BIS Certification. LUMINAIRE MAKE: Phillips / OSRAM / GE Venture / Wipro / Crompton / Bajaj / Havells / Jaquar / Panasonic / Halonix / HPL. LED MAKE : PHILIPS LUMILEDS / CREE / NICHIA / OSRAM / SAMSUNG / LG LEDs.
a) Labour charges
| 1 |  | Skilled Electrician. | 0.1 | day | 1 | day | 660 | 66
| 2 |  | Lineman Electric / Telephone | 0.1 | day | 1 | day | 550 | 55
|  |  | Labour for 1 No | [5 empty] | 121
b) Material
| ELEC-1.5.5 |  | Supply of 23 / 0060 twin core twisted / flat heavy Copper wire.
|  |  | Makes : Finolex / RR Kabel / Havells / Polycab / GM / Million / V-Guard / Gold Medal / Kundancab / HPL / RPG / Nandicab / Nakoda / Payal / Finecab / Gemini / Vimal / Suncab | 1 | Mtr | 100 | Mtrs | 1200 | 12
| ELEC-1.4.4 | d | Supply of No.8 Screws of 35/38mm. | 2 | Nos | 100 | Nos | 128 | 2.56
| 9.1.4 |  | Rawl Plugs. | 2 | Nos | 100 | Nos | 43 | 0.86
|  |  | Fixing arrangements on wall with required support on wall | 2 | Nos | 1 | Nos | 5 | 10
|  |  | Cost of Material for fixing luminaire | [5 empty] | 25.42
| 3.5.15 |  | 10W, +/ 10% , >/ 1000 lumens, 600mm length LED light | 1 | Nos | 1 | Nos | 425 | 425
|  |  | Cost of Material | [5 empty] | 450.42
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 571
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 77.7416
648.7416
|  |  | Rate per Each | [5 empty] | 649
MPCC IN ESS
47 |  |  | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor LT panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Aluminium bus bar ( with rating of 0.8A/ Sqmm)supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, flexibility to accept the up four out going cables and necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges.
|  |  | Fabrication: |  | L | H | D |  | Nos
|  |  | Size of panel : in Mtr |  | 2.5 | 2.2 | 1.2
|  |  | Front and back faces |  | 2 | 2.5 | 2.2 | 11 | 2
|  |  | Top and bottom faces |  | 2 | 2.5 | 1.2 | 6 | 2
|  |  | Side faces |  | 2 | 2.2 | 1.2 | 5.28 | 2
|  |  | Vertical sheets |  | 5 | 2.2 | 1.2 | 13.2 | 2
[5 empty] | 0 | 1.6 | 1.2 | 0
|  |  | Horizontal sheets |  | 12 | 0.45 | 0.55 | 2.97 | 0
|  |  | Horizontal sheets |  |  |  |  | 0 | 6
|  |  | Sub total |  |  |  |  | 38.45 | 0
|  |  | Add extra 10 % for wastage |  |  |  |  | 3.845 | 0
|  |  | Total |  |  |  |  | 42.295
| 7.13.1 | a+b/2 | Fabrication and erection of 14 / 16 SWG CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges. | 42.295 | Sqmtr | 1 | Sqmtr | 4940 | 208937.3 | 3
Incomer
| ELEC-2.11.1 | f | 800A 4 Pole, 50kA, electrically drawout Air Circuit Breaker Confirms to IS 13947-2, IEC 60947-2 and BS-EN 60947 with Micro processer based having over load, shot circuit and earth fault Protection.-3Nos Makes : Siemens (Sentron- 3W) / L&T U Power / Schneider Master Pact / ABB Emax / C&S.Winmaster2 / Legrand DMX | 3 | Nos | 1 | No | 249645 | 748935
Out goings
| 2.8.1 | m | Supply of 800A 3Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 50 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 0 | Nos | 1 | No | 79957 | 0
| 2.8.1 | k | Supply of 630A 3Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 50 KA with thermal magnetic release Panel Mounted.Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 4 | Nos | 1 | No | 44841 | 179364
| 2.8.1 | i | Supply of 400A 3Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 36 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 4 | Nos | 1 | No | 31129 | 124516
| 2.8.1 | g | Supply of 250A 3Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 36 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 4 | Nos | 1 | No | 23000 | 92000
| 2.8.1 | e | Supply of 160A 3Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted.Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 0 | Nos | 1 | No | 13694 | 0
| 2.8.1 | c | Supply of 125A 3Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 4 | Nos | 1 | No | 10325 | 41300
| 2.8.1 | a | Supply of 63A / 60A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 0 | Nos | 1 | No | 8699 | 0
Metering
| ELEC-7.14.1 | a) | Supply and erection of 0-415V volt Digital meter of size 96x96mm on existing box / panel board including connections etc., complete of MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS | 1 | No | 1 | No | 2200 | 2200
| ELEC-7.14.2 | a) | Supply and erection of 0-100 / 200 / 400 / 600 /1000 CT Digital Ammeter of size 96x96mm on existing box / panel board including connections etc., complete MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS | 1 | No | 1 | No | 2200 | 2200
| 7.14.5 | b | Multifunction energy meter Class I RS 485 with LED display. MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS. | 1 | No | 1 | No | 8250 | 8250
| ELEC-7.14.6 | a) | Supply and erection of Analog selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete. Makes : L&T / C&S / SALZAR / HPL / Siemens. | 2 | No | 1 | No | 193 | 386
| ELEC-7.14.6 | b) | Supply and erection of Analog LED indicator lamps on the existing box / panel board. Makes : L&T / C&S / SALZAR / HPL / Siemens | 3 | No | 1 | No | 149 | 447
| 2.6.1 | a) | 32A fuse bases with 2A control fuses. Makes : C&S / GM / Million / Gold Medal. | 3 | No | 1 | No | 101 | 303
| 7.14.7 |  | Supply and erection of Analog LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete. KAPPA MAKE. MAKE : KAPPA | 3 | No | 1 | No | 484 | 1452
1410290.3
|  |  | Bus bar arrangement with insulators | 0.05 |  |  |  |  | 70514.515
|  |  | Hard ware such as base channel etc. | 0.02 |  |  |  |  | 28205.806
|  |  | Transportation | 0.02 |  |  |  |  | 28205.806
|  |  | Control wiring with flexible wires and MCBs including commissioning and testing etc | 0.05 |  |  |  |  | 70514.515
|  |  | TOTAL COST OF MATERIAL AND LABOUR | [5 empty] | 1607730.942
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 218892.5678
1826623.5098
|  |  | Rate per Each | [5 empty] | 1826624
APFCR panel for 165KVAR in sub-station
48 |  |  | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor LT panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Aluminium bus bar ( with rating of 0.8A/ Sqmm)supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, flexibility to accept the up four out going cables and necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges.
|  |  | Fabrication: |  | L | H | D |  | Nos
|  |  | Size of panel : in Mtr |  | 3 | 1.8 | 0.75
|  |  | Front and back faces |  | 2 | 3 | 1.8 | 10.8 | 2
|  |  | Top and bottom faces |  | 2 | 3 | 0.75 | 4.5 | 2
|  |  | Side faces |  | 2 | 1.8 | 0.75 | 2.7 | 2
|  |  | Vertical sheets |  | 4 | 1.8 | 0.75 | 5.4 | 2
|  |  | Horizontal sheets |  | 13 | 0.3 | 0.3 | 1.17 | 0
|  |  | Horizontal sheets |  |  |  |  | 0 | 6
|  |  | Sub total |  |  |  |  | 24.57 | 0
|  |  | Add extra 10 % for wastage |  |  |  |  | 2.457 | 0
|  |  | Total |  |  |  |  | 27.027
| 7.13.1 | a+b/2 | Fabrication and erection of 14 / 16 SWG CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges. | 27.027 | Sqmtr | 1 | Sqmtr | 4940 | 133513.38 | 3*25
| 2.8.1 | h | Supply of 250A 4 Pole MCCB, , Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 35/36KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 1 | Nos | 1 | No | 29878 | 29878
| 2.8.1 | b | Supply of 63A / 60A 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 8 | Nos | 1 | No | 9781 | 78248
| 2.14.1 | f | Supply of 63A 10KA TP MCB, C/D Curve ISI Mark Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree. | 1 | Nos | 1 | No | 2064 | 2064
| ELEC-7.14.10 | h | Supply and fixing of 25KVAR Rating capacitor duty contactor Makes : L&T / Siemens / Meher. | 2 | No | 1 | No | 4505 | 9010 |  | 2 | #REF!
| ELEC-7.14.10 | f | Supply and fixing of 15KVAR Rating capacitor duty contactor Makes : L&T / Siemens / Meher. | 4 | No | 1 | No | 3465 | 13860 |  | 4 | #REF!
| 7.14.10 |  | Supply and fixing of 10 KVAR Rating capacitor duty contactor Makes : L&T / Siemens / Meher. | 4 | No | 1 | No | 2333 | 9332 |  | 4 | #REF!
| ELEC-7.14.10 | b | Supply and fixing of 5KVAR Rating capacitor duty contactor Makes : L&T / Siemens / Meher. | 3 | No | 1 | No | 1860 | 5580 |  | 3 | #REF!
| ELEC-7.14.12 | d | Supply of MPP type heavy duty capacitor of operating voltage Makes:L&T/Siemens/Schneider/Epcos. | 165 | No | 1 | No | 440 | 72600 |  |  | #REF!
Metering
| ELEC-7.14.1 | a) | Supply and erection of 0-415V volt Digital meter of size 96x96mm on existing box / panel board including connections etc., complete of MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS | 1 | No | 1 | No | 2200 | 2200
| 7.14.2 | a) | Supply and erection of 0-100 / 200 / 400 / 600 /1000 CT Digital Ammeter of size 96x96mm on existing box / panel board including connections etc., complete MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS | 1 | No | 1 | No | 2200 | 2200
| ELEC-7.14.6 | a) | Multifunction energy meter Class I RS 485 with LED display. MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS. | 2 | No | 1 | No | 193 | 386
| ELEC-7.14.6 | b) | Supply and erection of Analog selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete. Makes : L&T / C&S / SALZAR / HPL / Siemens. | 24 | No | 1 | No | 149 | 3576
| ELEC-7.14.6 | c | Supply and erection of Analog LED indicator lamps on the existing box / panel board. Makes : L&T / C&S / SALZAR / HPL / Siemens | 16 | No | 1 | No | 83 | 1328
| 7.14.9 | b | Supply and fixing of 12 Stage APFC Relay with connection etc complete. Makes : L&T / Siemens / EPCOS / Schneider / Elmeasure | 1 | No | 1 | No | 16170 | 16170
| 2.6.1 | a) | 32A fuse bases with 2A control fuses. Makes : C&S / GM / Million / Gold Medal. | 3 | No | 1 | No | 101 | 303
| 7.14.7 |  | Supply and erection of Analog LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete. KAPPA MAKE. MAKE : KAPPA | 3 | No | 1 | No | 484 | 1452
381700.38
|  |  | Bus bar arrangement with insulators | 0.05 |  |  |  |  | 19085.019
|  |  | Hard ware such as base channel etc. | 0.02 |  |  |  |  | 7634.0076
|  |  | Transportation | 0.02 |  |  |  |  | 7634.0076
|  |  | Control wiring with flexible wires and MCBs including commissioning and testing etc | 0.05 |  |  |  |  | 19085.019
|  |  | TOTAL COST OF MATERIAL AND LABOUR | [5 empty] | 435138.4332
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 59244.0977
494382.5309
|  |  | Rate per Each | [5 empty] | 494383
Power panel In Hospital
49 |  |  | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor LT panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Aluminium bus bar ( with rating of 0.8A/ Sqmm)supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, flexibility to accept the up four out going cables and necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges.
|  |  | Fabrication: |  | L | H | D |  | Nos
|  |  | Size of panel : in Mtr |  | 2.25 | 2.1 | 0.6
|  |  | Front and back faces |  | 2 | 2.25 | 2.1 | 9.45 | 2
|  |  | Top and bottom faces |  | 2 | 2.25 | 0.6 | 2.7 | 2
|  |  | Side faces |  | 2 | 2.1 | 0.6 | 2.52 | 2
|  |  | Vertical sheets |  | 2 | 2.1 | 0.6 | 2.52 | 2
[5 empty] | 2 | 1.6 | 1 | 3.2
|  |  | Horizontal sheets |  | 15 | 0.45 | 0.55 | 3.7125 | 0
|  |  | Horizontal sheets |  |  |  |  | 0 | 6
|  |  | Sub total |  |  |  |  | 24.1025 | 0
|  |  | Add extra 10 % for wastage |  |  |  |  | 2.4103 | 0
|  |  | Total |  |  |  |  | 26.5128
| 7.13.1 | a+b/2 | Fabrication and erection of 14 / 16 SWG CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges. | 26.5128 | Sqmtr | 1 | Sqmtr | 4940 | 130972.985
| 2.8.1 | l | Supply of 630A 4Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 50 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 1 | Nos | 1 | No | 55502 | 55502
| 2.8.1 | i | Supply of 400A 4Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 36 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 6 | Nos | 1 | No | 37611 | 225666
| 2.8.1 | g | Supply of 250A 3Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 36 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 6 | Nos | 1 | No | 23000 | 138000
| 2.8.1 | c | Supply of 125A 3Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 4 | Nos | 1 | No | 10325 | 41300
Metering
| ELEC-7.14.1 | a) | Supply and erection of 0-415V volt Digital meter of size 96x96mm on existing box / panel board including connections etc., complete of MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS | 1 | No | 1 | No | 2200 | 2200
| ELEC-7.14.2 | a) | Supply and erection of 0-100 / 200 / 400 / 600 /1000 CT Digital Ammeter of size 96x96mm on existing box / panel board including connections etc., complete MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS | 1 | No | 1 | No | 2200 | 2200
| 7.14.5 | a) | Multifunction energy meter Class I RS 485 with LED display. MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS. | 1 | No | 1 | No | 8250 | 8250
| ELEC-7.14.6 | a) | Supply and erection of Analog selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete. Makes : L&T / C&S / SALZAR / HPL / Siemens. | 2 | No | 1 | No | 193 | 386
| ELEC-7.14.6 | b) | Supply and erection of Analog LED indicator lamps on the existing box / panel board. Makes : L&T / C&S / SALZAR / HPL / Siemens | 3 | No | 1 | No | 149 | 447
| 2.6.1 | a) | 32A fuse bases with 2A control fuses. Makes : C&S / GM / Million / Gold Medal. | 3 | No | 1 | No | 101 | 303
| 7.14.7 |  | Supply and erection of Analog LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete. KAPPA MAKE. MAKE : KAPPA | 3 | No | 1 | No | 484 | 1452
606678.985
|  |  | Bus bar arrangement with insulators | 0.05 |  |  |  |  | 30333.9493
|  |  | Hard ware such as base channel etc. | 0.02 |  |  |  |  | 12133.5797
|  |  | Transportation | 0.02 |  |  |  |  | 12133.5797
|  |  | Control wiring with flexible wires and MCBs including commissioning and testing etc | 0.05 |  |  |  |  | 30333.9493
|  |  | TOTAL COST OF MATERIAL AND LABOUR | [5 empty] | 691614.0429
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 94163.2519
785777.2948
|  |  | Rate per Each | [5 empty] | 785777
Lighting panel Hospital Building
50 |  |  | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor LT panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Aluminium bus bar ( with rating of 0.8A/ Sqmm)supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, flexibility to accept the up four out going cables and necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges.
|  |  | Fabrication: |  | L | H | D |  | Nos
|  |  | Size of panel : in Mtr |  | 2.25 | 1.98 | 0.45
|  |  | Front and back faces |  | 2 | 2.25 | 1.98 | 8.91 | 2
|  |  | Top and bottom faces |  | 2 | 2.25 | 0.45 | 2.025 | 2
|  |  | Side faces |  | 2 | 1.98 | 0.45 | 1.782 | 2
|  |  | Vertical sheets |  | 2 | 1.98 | 0.45 | 1.782 | 2
[5 empty] | 2 | 1.6 | 1 | 3.2
|  |  | Horizontal sheets |  | 13 | 0.45 | 0.55 | 3.2175 | 0
|  |  | Horizontal sheets |  |  |  |  | 0 | 6
|  |  | Sub total |  |  |  |  | 20.9165 | 0
|  |  | Add extra 10 % for wastage |  |  |  |  | 2.0917 | 0
|  |  | Total |  |  |  |  | 23.0082
| 7.13.1 | a+b/2 | Fabrication and erection of 14 / 16 SWG CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges. | 23.0082 | Sqmtr | 1 | Sqmtr | 4940 | 113660.261
| 2.8.1 | j | Supply of 400A 4Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 36 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 1 | Nos | 1 | No | 37611 | 37611
| 2.8.1 | g | Supply of 250A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 36 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 6 | Nos | 1 | No | 23000 | 138000
| 2.8.1 | e | Supply of 160A 3Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 8 | Nos | 1 | No | 13694 | 109552
| 2.8.1 | c | Supply of 125A 3Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 2 | Nos | 1 | No | 10325 | 20650
Metering
| ELEC-7.14.1 | a) | Supply and erection of 0-415V volt Digital meter of size 96x96mm on existing box / panel board including connections etc., complete of MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS | 1 | No | 1 | No | 2200 | 2200
| ELEC-7.14.2 | a) | Supply and erection of 0-100 / 200 / 400 / 600 /1000 CT Digital Ammeter of size 96x96mm on existing box / panel board including connections etc., complete MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS | 1 | No | 1 | No | 2200 | 2200
| 7.14.5 | a) | Multifunction energy meter Class I RS 485 with LED display. MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS. | 1 | No | 1 | No | 8250 | 8250
| ELEC-7.14.6 | a) | Supply and erection of Analog selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete. Makes : L&T / C&S / SALZAR / HPL / Siemens. | 2 | No | 1 | No | 193 | 386
| ELEC-7.14.6 | b) | Supply and erection of Analog LED indicator lamps on the existing box / panel board. Makes : L&T / C&S / SALZAR / HPL / Siemens | 3 | No | 1 | No | 149 | 447
| 2.6.1 | a) | 32A fuse bases with 2A control fuses. Makes : C&S / GM / Million / Gold Medal. | 3 | No | 1 | No | 101 | 303
| 7.14.7 |  | Supply and erection of Analog LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete. KAPPA MAKE. MAKE : KAPPA | 3 | No | 1 | No | 484 | 1452
434711.261
|  |  | Bus bar arrangement with insulators | 0.05 |  |  |  |  | 21735.5631
|  |  | Hard ware such as base channel etc. | 0.02 |  |  |  |  | 8694.2252
|  |  | Transportation | 0.02 |  |  |  |  | 8694.2252
|  |  | Control wiring with flexible wires and MCBs including commissioning and testing etc | 0.05 |  |  |  |  | 21735.5631
|  |  | TOTAL COST OF MATERIAL AND LABOUR | [5 empty] | 495570.8375
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 67471.9695
563042.8071
|  |  | Rate per Each | [5 empty] | 563043
Sub power Panel-1 / Floor power panel
51 |  |  | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor LT panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Aluminium bus bar ( with rating of 0.8A/ Sqmm)supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, flexibility to accept the up four out going cables and necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges.
|  |  | Fabrication: |  | L | H | D |  | Nos
|  |  | Size of panel : in Mtr |  | 2.25 | 1.98 | 0.45
|  |  | Front and back faces |  | 2 | 2.25 | 1.98 | 8.91 | 2
|  |  | Top and bottom faces |  | 2 | 2.25 | 0.45 | 2.025 | 2
|  |  | Side faces |  | 2 | 1.98 | 0.45 | 1.782 | 2
|  |  | Vertical sheets |  | 2 | 1.98 | 0.45 | 1.782 | 2
[5 empty] | 2 | 1.6 | 1 | 3.2
|  |  | Horizontal sheets |  | 13 | 0.45 | 0.55 | 3.2175 | 0
|  |  | Horizontal sheets |  |  |  |  | 0 | 6
|  |  | Sub total |  |  |  |  | 20.9165 | 0
|  |  | Add extra 10 % for wastage |  |  |  |  | 2.0917 | 0
|  |  | Total |  |  |  |  | 23.0082
| 7.13.1 | a+b/2 | Fabrication and erection of 14 / 16 SWG CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges. | 23.0082 | Sqmtr | 1 | Sqmtr | 4940 | 113660.261
| 2.8.1 | h | Supply of 250A 4Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 36 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 1 | Nos | 1 | No | 29878 | 29878
| 2.8.1 | c | Supply of 125A 3Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 4 | Nos | 1 | No | 10325 | 41300
| 2.8.1 | a | Supply of 63A / 60A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 2 | Nos | 1 | No | 8699 | 17398
| 2.14.1 | f | 40-63A 10KA TP MCB, C/D Curve ISI Mark of Makes : Makes : Legrand-DX3 / Schneider-Acti9 / Siemens / L&T Exora / Cabtree | 12 | Nos | 1 | No | 2064 | 24768
Metering
| ELEC-7.14.1 | a) | Supply and erection of 0-415V volt Digital meter of size 96x96mm on existing box / panel board including connections etc., complete of MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS | 1 | No | 1 | No | 2200 | 2200
| ELEC-7.14.2 | a) | Supply and erection of 0-100 / 200 / 400 / 600 /1000 CT Digital Ammeter of size 96x96mm on existing box / panel board including connections etc., complete MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS | 1 | No | 1 | No | 2200 | 2200
| 7.14.5 | a) | Multifunction energy meter Class I RS 485 with LED display. MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS. | 1 | No | 1 | No | 8250 | 8250
| ELEC-7.14.6 | a) | Supply and erection of Analog selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete. Makes : L&T / C&S / SALZAR / HPL / Siemens. | 2 | No | 1 | No | 193 | 386
| ELEC-7.14.6 | b) | Supply and erection of Analog LED indicator lamps on the existing box / panel board. Makes : L&T / C&S / SALZAR / HPL / Siemens | 3 | No | 1 | No | 149 | 447
| 2.6.1 | a) | 32A fuse bases with 2A control fuses. Makes : C&S / GM / Million / Gold Medal. | 3 | No | 1 | No | 101 | 303
| 7.14.7 |  | Supply and erection of Analog LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete. KAPPA MAKE. MAKE : KAPPA | 3 | No | 1 | No | 484 | 1452
242242.261
|  |  | Bus bar arrangement with insulators | 0.05 |  |  |  |  | 12112.113
|  |  | Hard ware such as base channel etc. | 0.02 |  |  |  |  | 4844.8452
|  |  | Transportation | 0.02 |  |  |  |  | 4844.8452
|  |  | Control wiring with flexible wires and MCBs including commissioning and testing etc | 0.05 |  |  |  |  | 12112.113
|  |  | TOTAL COST OF MATERIAL AND LABOUR | [5 empty] | 276156.1775
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 37598.6636
313754.8411
|  |  | Rate per Each | [5 empty] | 313755
Sub Lighting Panel-1
52 |  |  | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor LT panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Aluminium bus bar ( with rating of 0.8A/ Sqmm)supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, flexibility to accept the up four out going cables and necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges.
|  |  | Fabrication: |  | L | H | D |  | Nos
|  |  | Size of panel : in Mtr |  | 2.25 | 1.98 | 0.45
|  |  | Front and back faces |  | 2 | 2.25 | 1.98 | 8.91 | 2
|  |  | Top and bottom faces |  | 2 | 2.25 | 0.45 | 2.025 | 2
|  |  | Side faces |  | 2 | 1.98 | 0.45 | 1.782 | 2
|  |  | Vertical sheets |  | 2 | 1.98 | 0.45 | 1.782 | 2
[5 empty] | 2 | 1.6 | 1 | 3.2
|  |  | Horizontal sheets |  | 13 | 0.45 | 0.55 | 3.2175 | 0
|  |  | Horizontal sheets |  |  |  |  | 0 | 6
|  |  | Sub total |  |  |  |  | 20.9165 | 0
|  |  | Add extra 10 % for wastage |  |  |  |  | 2.0917 | 0
|  |  | Total |  |  |  |  | 23.0082
| 7.13.1 | a+b/2 | Fabrication and erection of 14 / 16 SWG CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges. | 23.0082 | Sqmtr | 1 | Sqmtr | 4940 | 113660.261
| 2.8.1 | f | Supply of 160A 4Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 1 | Nos | 1 | No | 17881 | 17881
| 2.8.1 | c | Supply of 125A 3Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted. MMakes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 4 | Nos | 1 | No | 10325 | 41300
| 2.8.1 | a | Supply of 63A / 60A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 2 | Nos | 1 | No | 8699 | 17398
| 2.14.1 | f | 40-63A 10KA TP MCB, C/D Curve ISI Mark of Makes : Legrand-DX3 / Schneider-Acti9. | 12 | Nos | 1 | No | 2064 | 24768
Metering
| ELEC-7.14.1 | a) | Supply and erection of 0-415V volt Digital meter of size 96x96mm on existing box / panel board including connections etc., complete of MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS | 1 | No | 1 | No | 2200 | 2200
| ELEC-7.14.2 | a) | Supply and erection of 0-100 / 200 / 400 / 600 /1000 CT Digital Ammeter of size 96x96mm on existing box / panel board including connections etc., complete MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS | 1 | No | 1 | No | 2200 | 2200
| 7.14.5 | a) | Multifunction energy meter Class I RS 485 with LED display. MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS. | 1 | No | 1 | No | 8250 | 8250
| ELEC-7.14.6 | a) | Supply and erection of Analog selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete. Makes : L&T / C&S / SALZAR / HPL / Siemens. | 2 | No | 1 | No | 193 | 386
| ELEC-7.14.6 | b) | Supply and erection of Analog LED indicator lamps on the existing box / panel board. Makes : L&T / C&S / SALZAR / HPL / Siemens | 3 | No | 1 | No | 149 | 447
| 2.6.1 | a) | 32A fuse bases with 2A control fuses. Makes : C&S / GM / Million / Gold Medal. | 3 | No | 1 | No | 101 | 303
| 7.14.7 |  | Supply and erection of Analog LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete. KAPPA MAKE. MAKE : KAPPA | 3 | No | 1 | No | 484 | 1452
230245.261
|  |  | Bus bar arrangement with insulators | 0.05 |  |  |  |  | 11512.2631
|  |  | Hard ware such as base channel etc. | 0.02 |  |  |  |  | 4604.9052
|  |  | Transportation | 0.02 |  |  |  |  | 4604.9052
|  |  | Control wiring with flexible wires and MCBs including commissioning and testing etc | 0.05 |  |  |  |  | 11512.2631
|  |  | TOTAL COST OF MATERIAL AND LABOUR | [5 empty] | 262479.5975
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 35736.5972
298216.1947
|  |  | Rate per Each | [5 empty] | 298216
Utility Panel
53 |  |  | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor LT panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Aluminium bus bar ( with rating of 0.8A/ Sqmm)supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, flexibility to accept the up four out going cables and necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges.
|  |  | Fabrication: |  | L | H | D |  | Nos
|  |  | Size of panel : in Mtr |  | 2.25 | 1.98 | 0.45
|  |  | Front and back faces |  | 2 | 2.25 | 1.98 | 8.91 | 2
|  |  | Top and bottom faces |  | 2 | 2.25 | 0.45 | 2.025 | 2
|  |  | Side faces |  | 2 | 1.98 | 0.45 | 1.782 | 2
|  |  | Vertical sheets |  | 2 | 1.98 | 0.45 | 1.782 | 2
[5 empty] | 2 | 1.6 | 1 | 3.2
|  |  | Horizontal sheets |  | 13 | 0.45 | 0.55 | 3.2175 | 0
|  |  | Horizontal sheets |  |  |  |  | 0 | 6
|  |  | Sub total |  |  |  |  | 20.9165 | 0
|  |  | Add extra 10 % for wastage |  |  |  |  | 2.0917 | 0
|  |  | Total |  |  |  |  | 23.0082
| 7.13.1 | a+b/2 | Fabrication and erection of 14 / 16 SWG CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges. | 23.0082 | Sqmtr | 1 | Sqmtr | 4940 | 113660.261 | 3*25
| 2.8.1 | h | Supply of 250A 4Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 36 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 1 | Nos | 1 | No | 29878 | 29878
| 2.8.1 | c | Supply of 125A 3Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 4 | Nos | 1 | No | 10325 | 41300
| 2.8.1 | a | Supply of 63A / 60A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 4 | Nos | 1 | No | 8699 | 34796
Metering
| ELEC-7.14.1 | a) | Supply and erection of 0-415V volt Digital meter of size 96x96mm on existing box / panel board including connections etc., complete of MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS | 1 | No | 1 | No | 2200 | 2200
| ELEC-7.14.2 | a) | Supply and erection of 0-100 / 200 / 400 / 600 /1000 CT Digital Ammeter of size 96x96mm on existing box / panel board including connections etc., complete MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS | 1 | No | 1 | No | 2200 | 2200
| 7.14.5 | a) | Multifunction energy meter Class I RS 485 with LED display. MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS. | 1 | No | 1 | No | 8250 | 8250
| ELEC-7.14.6 | a) | Supply and erection of Analog selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete. Makes : L&T / C&S / SALZAR / HPL / Siemens. | 2 | No | 1 | No | 193 | 386
| ELEC-7.14.6 | b) | Supply and erection of Analog LED indicator lamps on the existing box / panel board. Makes : L&T / C&S / SALZAR / HPL / Siemens | 27 | No | 1 | No | 149 | 4023
| 2.6.1 | a) | 32A fuse bases with 2A control fuses. Makes : C&S / GM / Million / Gold Medal. | 3 | No | 1 | No | 101 | 303
| 7.14.7 |  | Supply and erection of Analog LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete. KAPPA MAKE. MAKE : KAPPA | 3 | No | 1 | No | 484 | 1452
238448.261
|  |  | Bus bar arrangement with insulators | 0.05 |  |  |  |  | 11922.4131
|  |  | Hard ware such as base channel etc. | 0.02 |  |  |  |  | 4768.9652
|  |  | Transportation | 0.02 |  |  |  |  | 4768.9652
|  |  | Control wiring with flexible wires and MCBs including commissioning and testing etc | 0.05 |  |  |  |  | 11922.4131
|  |  | TOTAL COST OF MATERIAL AND LABOUR | [5 empty] | 271831.0175
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 37009.793
308840.8106
|  |  | Rate per Each | [5 empty] | 308841
HVAC Panel
54 |  |  | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor LT panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Aluminium bus bar ( with rating of 0.8A/ Sqmm)supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, flexibility to accept the up four out going cables and necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges.
|  |  | Fabrication: |  | L | H | D |  | Nos
|  |  | Size of panel : in Mtr |  | 2.25 | 1.98 | 0.45
|  |  | Front and back faces |  | 2 | 2.25 | 1.98 | 8.91 | 2
|  |  | Top and bottom faces |  | 2 | 2.25 | 0.45 | 2.025 | 2
|  |  | Side faces |  | 2 | 1.98 | 0.45 | 1.782 | 2
|  |  | Vertical sheets |  | 2 | 1.98 | 0.45 | 1.782 | 2
[5 empty] | 2 | 1.6 | 1 | 3.2
|  |  | Horizontal sheets |  | 13 | 0.45 | 0.55 | 3.2175 | 0
|  |  | Horizontal sheets |  |  |  |  | 0 | 6
|  |  | Sub total |  |  |  |  | 20.9165 | 0
|  |  | Add extra 10 % for wastage |  |  |  |  | 2.0917 | 0
|  |  | Total |  |  |  |  | 23.0082
| 7.13.1 | a+b/2 | Fabrication and erection of 14 / 16 SWG CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges. | 23.0082 | Sqmtr | 1 | Sqmtr | 4940 | 113660.261
| 2.8.1 | h | Supply of 250A 4Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 36 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 1 | Nos | 1 | No | 29878 | 29878
| 2.8.1 | c | Supply of 125A 3Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 2 | Nos | 1 | No | 10325 | 20650
| 2.8.1 | a | Supply of 63A / 60A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 8 | Nos | 1 | No | 8699 | 69592
Metering
| ELEC-7.14.1 | a) | Supply and erection of 0-415V volt Digital meter of size 96x96mm on existing box / panel board including connections etc., complete of MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS | 1 | No | 1 | No | 2200 | 2200
| ELEC-7.14.2 | a) | Supply and erection of 0-100 / 200 / 400 / 600 /1000 CT Digital Ammeter of size 96x96mm on existing box / panel board including connections etc., complete MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS | 1 | No | 1 | No | 2200 | 2200
| ELEC-7.14.6 | a) | Multifunction energy meter Class I RS 485 with LED display. MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS. | 1 | No | 1 | No | 8250 | 8250
| ELEC-7.14.6 | a) | Supply and erection of Analog selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete. Makes : L&T / C&S / SALZAR / HPL / Siemens. | 2 | No | 1 | No | 193 | 386
| ELEC-7.14.6 | b) | Supply and erection of Analog LED indicator lamps on the existing box / panel board. Makes : L&T / C&S / SALZAR / HPL / Siemens | 27 | No | 1 | No | 149 | 4023
| 2.6.1 | a) | 32A fuse bases with 2A control fuses. Makes : C&S / GM / Million / Gold Medal. | 3 | No | 1 | No | 101 | 303
| 7.14.7 |  | Supply and erection of Analog LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete. KAPPA MAKE. MAKE : KAPPA | 3 | No | 1 | No | 484 | 1452
252594.261
|  |  | Bus bar arrangement with insulators | 0.05 |  |  |  |  | 12629.7131
|  |  | Hard ware such as base channel etc. | 0.02 |  |  |  |  | 5051.8852
|  |  | Transportation | 0.02 |  |  |  |  | 5051.8852
|  |  | Control wiring with flexible wires and MCBs including commissioning and testing etc | 0.05 |  |  |  |  | 12629.7131
|  |  | TOTAL COST OF MATERIAL AND LABOUR | [5 empty] | 287957.4575
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 39205.4078
327162.8654
|  |  | Rate per Each | [5 empty] | 327163
VIII |  |  | Telephone
46 |  |  | Supply and fixing of Modular telephone Jack with connector on modular box with cover frame in existing consealed pipe wiring including cost and coveyance of all material and all labour charges etc., complete in N.R.B. / R.B. Makes : Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus / Cabtree Amare / Logus Platina / Gold Medal GIFA / GM-Zenova/ L&T- Englaze
a) Labour charges :
| 1 |  | Lineman Electric / Telephone | 0.055 | day | 1 | day | 615 | 33.825
|  |  | Labour for 1 No | [5 empty] | 33.825
b) Material
| 1.3.1 | a | Supply of 1 or 2 Module box. | 1 | Nos | 1 | No | 80 | 80
| 1.3.2 | a | Supply of 1 or 2 Modular Cover Frame | 1 | Nos | 1 | No | 85 | 85
| 1.9.1 | o | Supply of Modular socket type Telephone jack with Connector. | 1 | Nos | 1 | No | 140 | 140
|  |  | Cost of Material | [5 empty] | 305
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 338
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 46.0187
384.0187
|  |  | Rate per Each | [5 empty] | 384
47 |  |  | Supply, Transportation and Run of 1 of 2 Pair 0.5mm telephone copper cable in the existing conduit pipe and labour charges etc., complete. Makes : Finolex / Delton / Surabi / Polycab.
b) Labour charges
| 1 |  | Skilled Electrician. | 0.5 | day | 1 | day | 735 | 367.5
| 2 |  | Lineman Electric / Telephone | 1 | day | 1 | day | 615 | 615
| 3 |  | Helper (Electrical). | 0.5 | day | 1 | day | 615 | 307.5
|  |  | Labour for 100 Mtrs | [5 empty] | 1290
|  |  | Labour for 1 Mtr | [5 empty] | 12.9
a) Material
| 9.1.1 | a | Supply of 2 Pair, 0.5mm telephone copper | 100 | Mtrs | 100 | Mtrs | 1155 | 1155
|  |  | Cost of Material for 100 Mtrs | [5 empty] | 1155
|  |  | Cost of Material for 1 Mtrs | [5 empty] | 11.55
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 24.4
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 3.3221
27.7221
|  |  | Rate per Meter | [5 empty] | 28
48 |  |  | Supply, Transportation and Run of 1 of 20 Pair telephone copper cable in the existing cable tray/ conduit pipe and labour charges etc., complete. Makes :Finolex / Delton / Surabi / Polycab
b) Labour charges
| 1 |  | Skilled Electrician. | 0.7 | day | 1 | day | 735 | 514.5
| 2 |  | Lineman Electric / Telephone | 1 | day | 1 | day | 615 | 615
| 3 |  | Helper (Electrical). | 1 | day | 1 | day | 615 | 615
|  |  | Labour for 100 Mtrs | [5 empty] | 1744.5
|  |  | Labour for 1 Mtr | [5 empty] | 17.445
a) Material
| 8.1.1 | d | Supply of 20 Pair telephone Copper wire .(ELEC-8.1.16) | 1 | Mtrs | 1 | Mtrs | 90 | 90
|  |  | Cost of Material for 1 Mtrs | [5 empty] | 90
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 107.4
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 14.6225
122.0225
|  |  | Rate per Meter | [5 empty] | 122
49 |  |  | Supply, Transportation and Fixing of 20 pair Telephone distribution box with back mount frame, krone connector, powder coated metal body with lock and key arrangement including all accessories and labour charges etc., complete.
b) Labour charges
| 1 |  | Skilled Electrician. | 0.1 | day | 1 | day | 735 | 73.5
| 2 |  | Lineman Electric / Telephone | 0.121 | day | 1 | day | 615 | 74.415
|  |  | Labour for 1 Mtr | [5 empty] | 147.915
a) Material
| 8.1.2 | b | Supply of 20 pair Telephone distribution box with back mount frame, krone connector, powder coated metal body with lock and key arrangement. | 1 | Nos | 1 | Nos | 1230 | 1230
|  |  | Cost of Material for 1 Mtrs | [5 empty] | 1230
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 1377.9
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 187.6011
1565.5011
|  |  | Rate per Each | [5 empty] | 1566
50 |  |  | Supply, Transportation and Fixing of 100 pair Telephone distribution box with back mount frame, krone connector, powder coated metal body with lock and key arrangement including all accessories and labour charges etc., complete.
b) Labour charges
| 1 |  | Skilled Electrician. | 0.15 | day | 1 | day | 735 | 110.25
| 2 |  | Lineman Electric / Telephone | 0.15 | day | 1 | day | 615 | 92.25
|  |  | Labour for 1 Mtr | [5 empty] | 202.5
a) Material
| 8.1.2 | d | 100 pair Telephone distribution box | 1 | Nos | 1 | Nos | 4615 | 4615
|  |  | sundries | [5 empty] | 30
|  |  | Cost of Material for 1 Mtrs | [5 empty] | 4645
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 4847.5
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 659.9871
5507.4871
|  |  | Rate per Each | [5 empty] | 5507
Large (EPABX) System
51 |  |  | Supply, Installation, Testing and Commissioning of IP Based digtal Telephone (EPABX) system--complied with following specifications: > IP @ Core, PCM/TDM switching, Non blocking, > Must Support PRI, E1, Analog Junctions > Must Support PC Console, > Must support Mobile SIP (Android and I O.S) > Must support Voice Mail > Must support Card based GSM > Inbuilt Call Details Software with search engine software
| 9.4.1 |  | > 8 Analog Trunks > 8 Digital Extensions > 96 Analog Extensions > Expandable to 220 Ports wired or more at extra cost | 1 | No | 1 | Each | 400000 | 400000
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 54460
454460
|  |  | Rate per Each | [5 empty] | 454460
IX |  |  | LAN Networking System
52 |  |  | Supply, Transportation and Run of Cat - 6 UTP cable for LAN in the existing conduit pipe and labour charges etc., complete. Makes : D Link / AMP / Molex / Legrand / Krone.
b) Labour charges
| 1 |  | Skilled Electrician. | 0.5 | day | 1 | day | 735 | 367.5
| 2 |  | Lineman Electric / Telephone | 1 | day | 1 | day | 615 | 615
| 3 |  | Helper (Electrical). | 0.75 | day | 1 | day | 615 | 461.25
|  |  | Labour for 100 Mtrs | [5 empty] | 1443.75
|  |  | Labour for 1 Mtr | [5 empty] | 14.4375
a) Material
| 9.1.3 | a | Supply of LAN Cable cat - 6 UTP cable. | 100 | Mtrs | 100 | Mtrs | 2920 | 2920
|  |  | Cost of Material for 100 Mtrs | [5 empty] | 2920
|  |  | Cost of Material for 1 Mtrs | [5 empty] | 29.2
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 43.6
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 5.9361
49.5361
|  |  | Rate Per Meter | [5 empty] | 50
53 |  |  | Supply, Transportation and Fixing of Cat 6 RJ-45 information outlets including duel face plate with all accessories and labour charges etc., complete. Makes : D Link / AMP / Molex / Legrand / Krone.
b) Labour charges
| 1 |  | Skilled Electrician. | 0.067 | day | 1 | day | 735 | 49.245
| 2 |  | Lineman Electric / Telephone | 0.067 | day | 1 | day | 615 | 41.205
| 3 |  | Helper (Electrical). | 0.067 | day | 1 | day | 615 | 41.205
|  |  | Labour for 1 Mtr | [5 empty] | 131.655
a) Material
| 9.1.5 | a | Supply of Cat 6 RJ-45 information outlets including duel face plate. | 1 | Nos | 1 | Nos | 390 | 390
|  |  | Cost of Material for 1 Mtrs | [5 empty] | 390
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 521.6
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 71.0158
592.6158
|  |  | Rate per Each | [5 empty] | 593
54 |  |  | Supply, Transportation and Fixing of 24 Port - 10 / 100 / 1000 Gigabit Ethernet switches including all accessories and labour charges etc., complete. Makes : Digisol / TP Link / D link.
b) Labour charges
| 1 |  | Skilled Electrician. | 0.4 | day | 1 | day | 735 | 294
| 2 |  | Lineman Electric / Telephone | 0.307 | day | 1 | day | 615 | 188.805
|  |  | Labour for 1 Mtr | [5 empty] | 482.805
a) Material
| 9.1.7 | a | Supply of 24 Port manageble switches. | 1 | Nos | 1 | Nos | 8900 | 8900
|  |  | Cost of Material for 1 | [5 empty] | 8900
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 9382.8
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 1277.4682
10660.2682
|  |  | Rate per Each | [5 empty] | 10660
55 |  |  | Supply, Transportation and Fixing of 24 port patch panels including all accessories and labour charges etc., complete. Makes : D Link / AMP / Molex / Legrand / Krone
b) Labour charges
| 1 |  | Skilled Electrician. | 0.3 | day | 1 | day | 735 | 220.5
| 2 |  | Lineman Electric / Telephone | 0.4 | day | 1 | day | 615 | 246
|  |  | Labour for 1 Mtr | [5 empty] | 466.5
a) Material
| 9.1.11 |  | Supply of 24 port patch panels.
|  |  | Makes : D Link / AMP / Molex / Legrand / Krone. | 1 | Nos | 1 | Nos | 6670 | 6670
|  |  | sundries | [5 empty] | 12.5
|  |  | Cost of Material for 1 Mtrs | [5 empty] | 6682.5
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 7149
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 973.3363
8122.3363
|  |  | Rate per Each | [5 empty] | 8123
56 |  |  | Supply, Transportation and Fixing of 19" 6U Wall mounting net work rack with power spike including all accessories and labour charges etc., complete. Makes : HCL / VAL / Rittal / APW
b) Labour charges
| 1 |  | Skilled Electrician. | 0.3 | day | 1 | day | 735 | 220.5
| 2 |  | Lineman Electric / Telephone | 0.396 | day | 1 | day | 615 | 243.54
|  |  | Labour for 1 Mtr | [5 empty] | 464.04
a) Material
| 8.1.10 | a | Supply of 6U Wall mounting net work rack with power spike including all accessories. | 1 | Nos | 1 | Nos | 7040 | 7040
|  |  | Cost of Material for 1 | [5 empty] | 7040
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 7504
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 1021.6696
8525.6696
|  |  | Rate per Each | [5 empty] | 8526
Airconditioners
57 |  |  | Supply, transportation and installation of split AC unit with high wall mounted 100% copper indoor unit and outdoor condencing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.0 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord (Voltage range 160- 264 volts) and cordless remote control with 5 years warranty compressor and comprehensive maintenance for 2 years
( 1.5 TR 3 STAR)
a |  |  | 1.5 TR 3 Star capable of delivering 18000 BTU/hr Make: Carrier / Daikin / Blue Star / Hitachi
| 6.1.1 | a | 1.5 Ton ( 3 star rates) | 1 | Nos | 1 | Each | 37000 | 37000
| 6.7.28 |  | Installation charges | 1 | Nos | 1 | Each | 1760 | 1760
|  |  | Transportation @ 2% | [5 empty] | 740
LS for Hard ware etc.,
|  |  | Rate per each | [5 empty] | 39500
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 5377.925
44877.925
|  |  | Rate per Each | [5 empty] | 44878
( 1.8 / 2.0 TR 3 STAR)
b |  |  | 2.0 / 1.8 TR 3 Star capable of delivering 21600 BTU/hr and above Makes : Daikin / Thoshiba / O General / Carrier / Blue Star / Hitachi
| 6.1.1 | b | 1.8 / 2.0 Ton ( 2-3 star rates) | 1 | Nos | 1 | Each | 46000 | 46000
| 6.7.28 |  | Installation charges | 1 | Nos | 1 | Each | 1760 | 1760
|  |  | Transportation @ 2% | [5 empty] | 920
LS for Hard ware etc.,
|  |  | Rate per each | [5 empty] | 48680
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 6627.782
55307.782
|  |  | Rate per Each | [5 empty] | 55308
Stabilizers
58 |  |  | Supply and erecting fully automatic line voltage stabilizer for operation on input voltage 200 to 250V. rated for 4 KVA maximum load and time delay model with Volt meter, selector switch, 6A / 16A flush type, 5 pin socket for out put and with 3 core flexible chord and 3 pin 6/16A plug top suitable for AC for continuous operation including cost and conveyance of all mateials and all labour charges etc., complete. Makes : V-Guard / Real Guard / Uni Stab / ITL. | [8 empty] | 50 | 80 | 4000
|  |  | a) Labour Charges | [8 empty] | 4 | 47202 | 188808
| 1 |  | Skilled Electrician | 0.1 | day | 1 | day | 735 | 73.5 |  |  | 4 | 3334 | 13336
| 2 |  | Helper | 0.1 | day | 1 | day | 615 | 61.5 |  |  |  |  | 206144
|  |  | b) Material | [8 empty] | 50 | 132 | 6600
| 6.12.1 | d | 4 KVA Stabilizer | 1 | No | 1 | each | 3030 | 3030 |  |  | 50 | 190 | 9500
|  |  | Transportation Charges on Unit Cost | 0.02 |  |  |  |  | 60.6
|  |  | Rate per Each | [5 empty] | 3226 |  |  |  | 0.18 | 37105.92
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 439.2199 |  |  |  | roud | 752.08
[9 empty] | 3665.2199 |  |  |  |  | 260102
|  |  | Rate per Each | [5 empty] | 3665 |  |  |  |  | 263000
2898
59 |  |  | Supply and erecting fully automatic line voltage stabilizer for operation on input voltage 200 to 250V. rated for 5 KVA maximum load and time delay model with Volt meter, selector switch, 6A / 16A flush type, 5 pin socket for out put and with 3 core flexible chord and 3 pin 6/16A plug top suitable for AC for continuous operation including cost and conveyance of all mateials and all labour charges etc., complete. Makes : V-Guard / Real Guard / Uni Stab / ITL.
a) Labour Charges
| 1 |  | Skilled Electrician | 0.1 | day | 1 | day | 735 | 73.5
| 2 |  | Helper | 0.1 | day | 1 | day | 615 | 61.5
b) Material
| 6.10.1 | e | 5 KVA Stabilizer | 1 | No | 1 | each | 3640 | 3640
|  |  | Transportation Charges on Unit Cost | 0.02 |  |  |  |  | 72.8
|  |  | Rate per Each | [5 empty] | 3848
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 523.9052
4371.9052
|  |  | Rate per Each | [5 empty] | 4372
|  |  | Sub total |  |  |  | #REF!
|  |  | Add extra 10 % for wastage |  |  |  | #REF!
|  |  | Total |  |  |  | #REF!
| 7.13.1 | a+b/2 | Fabrication and erection of 14 / 16 SWG CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges. | #REF! | Sqmt | 1 | Sqmt | 4940 | #REF!
Incomer & Out goings
| 2.8.1 | b | Supply of 63A / 60A 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 1 | Nos | 1 | No | 9781 | 9781
#REF!
|  |  | Bus bar arrangement with insulators | 0 |  |  |  |  | #REF!
|  |  | Hard ware such as base channel etc. | 0 |  |  |  |  | #REF!
|  |  | Transportation | 0.01 |  |  |  |  | #REF!
|  |  | Control wiring with flexible wires and connections to MCBs with required lugs including commissioning and testing etc | 0.005 |  |  |  |  | #REF!
|  |  | TOTAL COST OF MATERIAL AND LABOUR | [5 empty] | #REF!
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | #REF!
#REF!
|  |  | Rate per Each | [5 empty] | #REF!
125A MCCB Switch
Supply installation testing and commissioning of 3 phase and neutral 415V free mounted indoor LT panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of 125A 4P MCCB Switch. The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3VL / Hager-h3/C&S -Winbreak.
|  |  | Fabrication: | L | H | D |  | Nos
|  |  | Size of panel : in Mtr | 0.45 | 0.45 | 0.4
|  |  | Front and back faces |  | 0.45 |  | 0.9 | 2
|  |  | Top and bottom faces |  | 0.45 | 0.4 | 0.36 | 2
|  |  | Side faces |  | 0.45 | 0.4 | 0.36 | 2
|  |  | Sub total |  |  |  | 1.62
|  |  | Add extra 10 % for wastage |  |  |  | 0.162
|  |  | Total |  |  |  | 1.782
| 7.13.1 | a+b/2 | Fabrication and erection of 14 / 16 SWG CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges. | 1.782 | Sqmtr | 1 | Sqmtr | 4940 | 8803.08 | 3*25
Incomer & Out goings
| 2.8.1 | d | Supply of 125A 4Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted. | 1 | Nos | 1 | No | 12486 | 12486
21289.08
|  |  | Bus bar arrangement with insulators | 0 |  |  |  |  | 0
|  |  | Hard ware such as base channel etc. | 0 |  |  |  |  | 0
|  |  | Transportation | 0.01 |  |  |  |  | 212.8908
|  |  | Control wiring with flexible wires and connections to MCBs with required lugs including commissioning and testing etc | 0.005 |  |  |  |  | 106.4454
|  |  | TOTAL COST OF MATERIAL AND LABOUR | [5 empty] | 21608.4162
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 2941.9859
24550.4021
|  |  | Rate per Each | [5 empty] | 24550
250A 4Pole MCCB
Supply installation testing and commissioning of 3 phase and neutral 415V free mounted indoor LT panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of 250 A 4P MCCB Switch. The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3VL / Hager-h3/C&S -Winbreak.
|  |  | Fabrication: | L | H | D |  | Nos
|  |  | Size of panel : in Mtr | 0.6 | 0.6 | 0.45
|  |  | Front and back faces |  | 0.6 |  | 1.2 | 2
|  |  | Top and bottom faces |  | 0.6 | 0.45 | 0.54 | 2
|  |  | Side faces |  | 0.6 | 0.45 | 0.54 | 2
|  |  | Sub total |  |  |  | 2.28
|  |  | Add extra 10 % for wastage |  |  |  | 0.228
|  |  | Total |  |  |  | 2.508
| 7.13.1 | a+b/2 | Fabrication and erection of 14 / 16 SWG CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges. | 2.508 | Sqmtr | 1 | Sqmtr | 4940 | 12389.52 | 3*25
| 2.8.1 | h | Supply of 250A 4Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 35/36 KA with thermal magnetic release Panel Mounted. | 1 | Nos | 1 | No | 29878 | 29878
42267.52
|  |  | Bus bar arrangement with insulators | 0 |  |  |  |  | 0
|  |  | Hard ware such as base channel etc. | 0 |  |  |  |  | 0
|  |  | Transportation | 0.01 |  |  |  |  | 422.6752
|  |  | Control wiring with flexible wires and connections to MCBs with required lugs including commissioning and testing etc | 0.005 |  |  |  |  | 211.3376
|  |  | TOTAL COST OF MATERIAL AND LABOUR | [5 empty] | 42901.5328
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 5841.0437
48742.5765
|  |  | Rate per Each | [5 empty] | 48743
400A 4Pole MCCB
Supply installation testing and commissioning of 3 phase and neutral 415V free mounted indoor LT panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of 400 A 4P MCCB Switch. The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3VL / Hager-h3/C&S -Winbreak.
|  |  | Fabrication: | L | H | D |  | Nos
|  |  | Size of panel : in Mtr | 0.75 | 0.75 | 0.45
|  |  | Front and back faces |  | 0.75 |  | 1.5 | 2
|  |  | Top and bottom faces |  | 0.75 | 0.45 | 0.675 | 2
|  |  | Side faces |  | 0.75 | 0.45 | 0.675 | 2
|  |  | Sub total |  |  |  | 2.85
|  |  | Add extra 10 % for wastage |  |  |  | 0.285
|  |  | Total |  |  |  | 3.135
| 7.13.1 | a+b/2 | Fabrication and erection of 14 / 16 SWG CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges. | 3.135 | Sqmtr | 1 | Sqmtr | 4940 | 15486.9 | 3*25
| 2.8.1 | j | Supply of 400A 4Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 35/36 KA with thermal magnetic release Panel Mounted. | 1 | Nos | 1 | No | 37611 | 37611
53097.9
|  |  | Bus bar arrangement with insulators | 0 |  |  |  |  | 0
|  |  | Hard ware such as base channel etc. | 0 |  |  |  |  | 0
|  |  | Transportation | 0.01 |  |  |  |  | 530.979
|  |  | Control wiring with flexible wires and connections to MCBs with required lugs including commissioning and testing etc | 0.005 |  |  |  |  | 265.4895
|  |  | TOTAL COST OF MATERIAL AND LABOUR | [5 empty] | 53894.3685
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 7337.7183
61232.0868
|  |  | Rate per Each | [5 empty] | 61232
l
60 | ELEC-4.10.1 | f | Supply and Installation of 100mm x 25mm x 2mm thick GI perforated cable tray with out cover along with required angle supports, with coupler plates, Anchor bolts and nuts etc complete and the tray should be fitted on the wall / Ceiling etc. complete. Makes: DEC/MNR/ H FAB or equivalent | 1 | Mtr | 1 | Mtr | 350 | 350 |  | 455
|  |  | Add 30% Extra for Perforated cable tray with cover on below rates. | 0.3 |  |  |  |  | 105
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 61.9482
516.9483
|  |  | Rate per Meter | [5 empty] | 517
61 | ELEC-4.10.1 | e | Supply and Installation of 150mm x 50mm x 2mm thick GI perforated cable tray with out cover along with required angle supports, with coupler plates, Anchor bolts and nuts etc complete and the tray should be fitted on the wall / Ceiling etc. complete. Makes: DEC/MNR/ H FAB or equivalent | 1 | Mtr | 1 | Mtr | 600 | 600
|  |  | Add 30% Extra for Perforated cable tray with cover on below rates. | 0.3 |  |  |  |  | 180
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 106.197
886.197
|  |  | Rate per Meter | [5 empty] | 886
62 | ELEC-4.10.1 | d | Supply and Installation of 300mm x 50mm x 2mm thick GI perforated cable tray with out cover along with required angle supports, with coupler plates, Anchor bolts and nuts etc complete and the tray should be fitted on the wall / Ceiling etc. complete. Makes: DEC/MNR/ H FAB or equivalent | 1 | Mtr | 1 | Mtr | 1080 | 1080
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 147.042
1227.042
|  |  | Rate per Meter | [5 empty] | 1227
63 | ELEC-4.10.1 | c | Supply and Installation of 450mm x 50mm x 2mm thick GI perforated cable tray with out cover along with required angle supports, with coupler plates, Anchor bolts and nuts etc complete and the tray should be fitted on the wall / Ceiling etc. complete. Makes: DEC/MNR/ H FAB or equivalent | 1 | Mtr | 1 | Mtr | 1280 | 1280
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 174.272
1454.272
|  |  | Rate per Meter | [5 empty] | 1454
64 | ELEC-4.10.2 | c | Supply, Transportation and Installation of 600mm x 75mm x 2mm thick GI Ladder type cable tray along with required coupler plates, T's, Bends, Reducers, Anchor bolts, nuts, washers and slotted channels / Angle Iron Channels etc complete and the tray should be fitted on the wall / Ceiling etc. complete for finished item of work. Makes: DEC/MNR/ H FAB or equivalent | 1 | Mtr | 1 | Mtr | 1960 | 1960
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 266.854
2226.854
|  |  | Rate per Meter | [5 empty] | 2227
65 |  |  | Supply , fabrication and transportation of MS channel iron/ angle iron /flats including two coats of aluminium paint and one coat of red oxide paint including all labour charges etc complete.
| 9.1.27 |  | Mild Steel Items | 1 | Kg | 1 | Kg | 85 | 85
|  |  | Labour charges for fabricating steel works TBSC-T.I-16 | 1 | Kg | 1 | Kg | 40 | 40
|  |  | TOTAL | [5 empty] | 125
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 17.0188
142.0188
|  |  | Rate per One Kg | [5 empty] | 142
Lighting Panel
66 |  |  | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor LT panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Aluminium bus bar ( with rating of 0.8A/ Sqmm)supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, flexibility to accept the up four out going cables and necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges.
|  |  | Fabrication: |  | L | H | D |  | Nos
|  |  | Size of panel : in Mtr |  | 1.9 | 1.75 | 0.4
|  |  | Front and back faces |  | 1.9 | 1.9 | 1.75 | 6.3175
|  |  | Top and bottom faces |  | 1.9 | 1.9 | 0.4 | 1.444
|  |  | Side faces |  | 1.9 | 1.75 | 0.4 | 1.33
|  |  | Vertical sheets |  | 1.9 | 1.75 | 0.4 | 1.33
[5 empty] | 1.9 | 1.6 | 1 | 3.04
|  |  | Horizontal sheets |  | 4 | 0.4 | 0.4 | 0.64
|  |  | Horizontal sheets |  |  |  |  | 0
|  |  | Sub total |  |  |  |  | 14.1015
|  |  | Add extra 10 % for wastage |  |  |  |  | 1.4102
|  |  | Total |  |  |  |  | 15.5117
| 8.13.1 | a+b/2 | Fabrication and erection of 14 / 16 SWG CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges. | 15.5117 | Sqmtr | 1 | Sqmtr | 5978 | 92728.6437
| 2.7.1 | f | Supply of 160A 4-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH | 1 | Nos | 1 | No | 19715 | 19715
| 2.7.1 | f | Supply of 125 A 3-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH | 6 | Nos | 1 | No | 11380 | 68280
| 2.7.1 | a | Supply of 63 A 3-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH | 4 | Nos | 1 | No | 9600 | 38400
Metering
| ELEC-8.14.1 | a) | Supply and erection of 0-415V Digital Volt meter size 96x96mm on exisiting panel board including connections etc., complete. MAKES : CONZERVE / ELMEASURE / LK (L&T) / SEIMENS | 1 | No | 1 | No | 2425 | 2425
| ELEC-8.14.2 | a) | Supply and erection of 0-100 / 200 / 400 / 600 /1000 Digital Ammeter of size 96x96mm on existing panel board including connections etc., complete. MAKES : CONZERVE / ELMEASURE / LK (L&T) / SEIMENS. | 1 | No | 1 | No | 2425 | 2425
| ELEC-8.14.6 | a) | Supply and erection of Analog selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete. Makes : LK (L&T) / C&S / SALZAR / HPL / Siemens. | 2 | No | 1 | No | 215 | 430
| ELEC-8.14.6 | b) | Supply and erection of Analog LED indicator lamps on the existing box / panel board. Makes : LK (L&T) / C&S / SALZAR / HPL / Siemens | 3 | No | 1 | No | 165 | 495
| 2.6.1 | a) | 32A fuse bases with 2A control fuses. Makes : C&S / GM / Million / Gold Medal. | 3 | No | 1 | No | 110 | 330 |  |  | 112872.8
| 8.14.7 |  | Supply and erection of Analog LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete. KAPPA MAKE. MAKE : KAPPA | 3 | No | 1 | No | 530 | 1590
226818.6437
|  |  | Bus bar arrangement with insulators | 0.05 |  |  |  |  | 11340.9322
|  |  | Hard ware such as base channel etc. | 0.02 |  |  |  |  | 4536.3729
|  |  | Transportation | 0.02 |  |  |  |  | 4536.3729
|  |  | Control wiring with flexible wires and MCBs including commissioning and testing etc | 0.005 |  |  |  |  | 1134.0932
|  |  | TOTAL COST OF MATERIAL AND LABOUR | [5 empty] | 248366.4149
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 33815.0874
282181.5022
|  |  | Rate per Each | [5 empty] | 282182
Power Panel
67 |  |  | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor LT panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Aluminium bus bar ( with rating of 0.8A/ Sqmm)supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, flexibility to accept the up four out going cables and necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges.
|  |  | Fabrication: |  | L | H | D |  | Nos
|  |  | Size of panel : in Mtr |  | 1.9 | 1.75 | 0.4
|  |  | Front and back faces |  | 1.9 | 1.9 | 1.75 | 6.3175
|  |  | Top and bottom faces |  | 1.9 | 1.9 | 0.4 | 1.444
|  |  | Side faces |  | 1.9 | 1.75 | 0.4 | 1.33
|  |  | Vertical sheets |  | 1.9 | 1.75 | 0.4 | 1.33
[5 empty] | 1.9 | 1.6 | 1 | 3.04
|  |  | Horizontal sheets |  | 6 | 0.4 | 0.55 | 1.32
|  |  | Horizontal sheets |  |  |  |  | 0
|  |  | Sub total |  |  |  |  | 14.7815
|  |  | Add extra 10 % for wastage |  |  |  |  | 1.4782
|  |  | Total |  |  |  |  | 16.2597
| 7.13.1 | a+b/2 | Fabrication and erection of 14 / 16 SWG CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges. | 16.2597 | Sqmtr | 1 | Sqmtr | 5978 | 97200.1877 |  | 10868 | 5434
| 2.7.1 | h | Supply of 250A 4-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 36 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH | 1 | Nos | 1 | No | 32940 | 32940
| 2.7.1 | e | Supply of 160A 3-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH | 4 | Nos | 1 | No | 15100 | 60400
| 2.7.1 | f | Supply of 125 A 3-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH | 4 | Nos | 1 | No | 11380 | 45520
| 2.8.1 | a | Supply of 63 A 3-pole MCCB Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 kA with thermal magnetic release Panel Mounted. Makes : LK (L&T) - D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3 / C&S -Winbreak / BCH | 6 | Nos | 1 | No | 9600 | 57600
Metering
| ELEC-7.14.1 | a) | Supply and erection of 0-415V Digital Volt meter size 96x96mm on exisiting panel board including connections etc., complete. MAKES : CONZERVE / ELMEASURE / LK (L&T) / SEIMENS | 1 | No | 1 | No | 2425 | 2425
| ELEC-7.14.2 | a) | Supply and erection of 0-100 / 200 / 400 / 600 /1000 Digital Ammeter of size 96x96mm on existing panel board including connections etc., complete. MAKES : CONZERVE / ELMEASURE / LK (L&T) / SEIMENS. | 1 | No | 1 | No | 2425 | 2425
| ELEC-7.14.6 | a) | Supply and erection of Analog selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete. Makes : LK (L&T) / C&S / SALZAR / HPL / Siemens. | 2 | No | 1 | No | 215 | 430
| ELEC-7.14.6 | b) | Supply and erection of Analog LED indicator lamps on the existing box / panel board. Makes : LK (L&T) / C&S / SALZAR / HPL / Siemens | 3 | No | 1 | No | 165 | 495
| 2.6.1 | a) | 32A fuse bases with 2A control fuses. Makes : C&S / GM / Million / Gold Medal. | 3 | No | 1 | No | 110 | 330
| 7.14.7 |  | Supply and erection of Analog LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete. KAPPA MAKE. MAKE : KAPPA | 3 | No | 1 | No | 530 | 1590
301355.1877
|  |  | Bus bar arrangement with insulators | 0.05 |  |  |  |  | 15067.7594
|  |  | Hard ware such as base channel etc. | 0.02 |  |  |  |  | 6027.1038
|  |  | Transportation | 0.02 |  |  |  |  | 6027.1038
|  |  | Control wiring with flexible wires and MCBs including commissioning and testing etc | 0.005 |  |  |  |  | 1506.7759
|  |  | TOTAL COST OF MATERIAL AND LABOUR | [5 empty] | 329983.9305
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 44927.3121
374911.2427
|  |  | Rate per Each | [5 empty] | 374911
Power Panel For Hospital
68 |  |  | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor LT panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Aluminium bus bar ( with rating of 0.8A/ Sqmm)supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, flexibility to accept the up four out going cables and necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges.
|  |  | Fabrication: |  | L | H | D |  | Nos
|  |  | Size of panel : in Mtr |  | 1.35 | 1.9 | 0.6
|  |  | Front and back faces |  | 1.35 | 1.35 | 1.9 | 3.4628
|  |  | Top and bottom faces |  | 1.35 | 1.35 | 0.6 | 1.0935
|  |  | Side faces |  | 1.9 | 1.9 | 0.6 | 2.166
|  |  | Vertical sheets |  | 1.5 | 1.9 | 0.6 | 1.71
[5 empty] | 1.5 | 1.8 | 0.5 | 1.35
|  |  | Horizontal sheets |  | 0.5 | 0.45 | 0.55 | 0.12375
|  |  | Horizontal sheets |  | 0.5 | 0.45 | 0.55 | 0.12375
|  |  | Sub total |  |  |  |  | 10.0297
|  |  | Add extra 10 % for wastage |  |  |  |  | 1.003
|  |  | Total |  |  |  |  | 11.0327
| 7.13.1 | a+b/2 | Fabrication and erection of 14 / 16 SWG CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges. | 11.0327 | Sqmtr | 1 | Sqmtr | 5978 | 65953.63
| 2.8.1 | L | Supply of 400A 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 35/36 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 1 | Nos | 1 | No | 41470 | 41470
| 2.8.1 | c | Supply of 250A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 35/36 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 4 | Nos | 1 | No | 25360 | 101440
| 2.8.1 | c | Supply of 125A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 5 | Nos | 1 | No | 11380 | 56900
| 2.8.1 | a | Supply of 63A / 60A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 3 | Nos | 1 | No | 9600 | 28800
Metering
| ELEC-7.14.1 | a) | Supply and erection of 0-415V volt Digital meter of size 96x96mm on existing box / panel board including connections etc., complete of MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS | 1 | No | 1 | No | 2425 | 2425
| ELEC-7.14.2 | a) | Supply and erection of 0-100 / 200 / 400 / 600 /1000 CT Digital Ammeter of size 96x96mm on existing box / panel board including connections etc., complete MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS | 1 | No | 1 | No | 2425 | 2425
| ELEC-7.14.6 | a) | Supply and erection of Analog selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete. Makes : L&T / C&S / SALZAR / HPL / Siemens. | 2 | No | 1 | No | 215 | 430
| ELEC-7.14.6 | b) | Supply and erection of Analog LED indicator lamps on the existing box / panel board. Makes : L&T / C&S / SALZAR / HPL / Siemens | 3 | No | 1 | No | 165 | 495
| 2.6.1 | a) | 32A fuse bases with 2A control fuses. Makes : C&S / GM / Million / Gold Medal. | 3 | No | 1 | No | 110 | 330
| 7.14.7 |  | Supply and erection of Analog LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete. KAPPA MAKE. MAKE : KAPPA | 3 | No | 1 | No | 530 | 1590
302258.63
|  |  | Bus bar arrangement with insulators | 0.05 |  |  |  |  | 15112.9315
|  |  | Hard ware such as base channel etc. | 0.02 |  |  |  |  | 6045.1726
|  |  | Transportation | 0.02 |  |  |  |  | 6045.1726
|  |  | Control wiring with flexible wires and MCBs including commissioning and testing etc | 0.005 |  |  |  |  | 1511.2932
|  |  | TOTAL COST OF MATERIAL AND LABOUR | [5 empty] | 330973.1999
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 45062.0012
376035.2011
|  |  | Rate per Each | [5 empty] | 376035
Lighting Panel For Hospital
69 |  |  | Supply installation testing and commissioning of 3 phase and neutral 415V free standing floor mounted indoor LT panel made out of No.16/14 gauge CRCA sheet steel after 7 tank process and painting with powder coating. The panel shall consists of suitable rating TPN Aluminium bus bar ( with rating of 0.8A/ Sqmm)supported with DMC /SMC barriers and colour coaded with heat shrinkable sleeves, flexibility to accept the up four out going cables and necessary cable chamber . The panel shall have comprised of following switch gear . Including supply and fixing the same and painting with powder coating including internal connections cost and conveyance of all materials & labour charges.
|  |  | Fabrication: |  | L | H | D |  | Nos
|  |  | Size of panel : in Mtr |  | 1.35 | 1.9 | 0.6
|  |  | Front and back faces |  | 1.35 | 1.35 | 1.9 | 3.4628
|  |  | Top and bottom faces |  | 1.35 | 1.35 | 0.6 | 1.0935
|  |  | Side faces |  | 1.9 | 1.9 | 0.6 | 2.166
|  |  | Vertical sheets |  | 1.5 | 1.9 | 0.6 | 1.71
[5 empty] | 1.5 | 1.8 | 0.5 | 1.35
|  |  | Horizontal sheets |  | 0.5 | 0.45 | 0.55 | 0.12375
|  |  | Horizontal sheets |  | 0.5 | 0.45 | 0.55 | 0.12375
|  |  | Sub total |  |  |  |  | 10.0297
|  |  | Add extra 10 % for wastage |  |  |  |  | 1.003
|  |  | Total |  |  |  |  | 11.0327
| 7.13.1 | a+b/2 | Fabrication and erection of 14 / 16 SWG CRCA sheet steel enclosure for power control cubicle panel / boxes etc., including cutting, bending drilling, welding and reveting etc., complete with cleaning with 7 tank process and painting with powder coating including cost and conveyance of all materials and labour charges. | 11.0327 | Sqmtr | 1 | Sqmtr | 5978 | 65953.63
| 2.8.1 | j | Supply of 250 A 4 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 36 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 1 | Nos | 1 | No | 32940 | 32940
| 2.8.1 | c | Supply of 125A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 4 | Nos | 1 | No | 11380 | 45520
| 2.8.1 | a | Supply of 63A / 60A 3 Pole MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 16 KA with thermal magnetic release Panel Mounted. Makes : L&T- D sine / Schneider-NS NSX/Legrand -DP X3/ Siemens-3V / Hager-h3/C&S -Winbreak. | 8 | Nos | 1 | No | 9600 | 76800
Metering
| ELEC-7.14.1 | a) | Supply and erection of 0-415V volt Digital meter of size 96x96mm on existing box / panel board including connections etc., complete of MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS | 1 | No | 1 | No | 2425 | 2425
| ELEC-7.14.2 | a) | Supply and erection of 0-100 / 200 / 400 / 600 /1000 CT Digital Ammeter of size 96x96mm on existing box / panel board including connections etc., complete MAKES : CONZERVE / ELMEASURE / L&T / SEIMENS | 1 | No | 1 | No | 2425 | 2425
| ELEC-7.14.6 | a) | Supply and erection of Analog selector switch for voltmeter / Ammeter on the existing box / panel including connections etc., complete. Makes : L&T / C&S / SALZAR / HPL / Siemens. | 2 | No | 1 | No | 215 | 430
| ELEC-7.14.6 | b) | Supply and erection of Analog LED indicator lamps on the existing box / panel board. Makes : L&T / C&S / SALZAR / HPL / Siemens | 3 | No | 1 | No | 165 | 495
| 2.6.1 | a) | 32A fuse bases with 2A control fuses. Makes : C&S / GM / Million / Gold Medal. | 3 | No | 1 | No | 110 | 330
| 7.14.7 |  | Supply and erection of Analog LT current transformer with bar primary 100/5A to 1000 / 5A ratio in the existing box / panel including connections etc., complete. KAPPA MAKE. MAKE : KAPPA | 3 | No | 1 | No | 530 | 1590
228908.63
|  |  | Bus bar arrangement with insulators | 0.05 |  |  |  |  | 11445.4315
|  |  | Hard ware such as base channel etc. | 0.02 |  |  |  |  | 4578.1726
|  |  | Transportation | 0.02 |  |  |  |  | 4578.1726
|  |  | Control wiring with flexible wires and MCBs including commissioning and testing etc | 0.005 |  |  |  |  | 1144.5432
|  |  | TOTAL COST OF MATERIAL AND LABOUR | [5 empty] | 250654.9499
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 34126.6714
284781.6213
|  |  | Rate per Each | [5 empty] | 284782
Load Break Switch
70 | 8.16.12 |  | Supply, Transportation, Installation and Commissioning of 11 KV, 630A, 25 KA Outdoor type Load Break Switch as detailed below with suitable CC foundation and 2 Nos GI pipe earthing with brick massonry chambers etc complete for finished item of work. a) Load break switch: 11KV,630A, 25 KA with fuse trip, earth switch, manually operated spring chargesd mechanis with 2 no + 2 NC. b) HT HRC fuse upto 63A - 3 nos. c) Bus bar connection. d) Indication lamps. e) Manual trip Push buttion. Make : Megawin / Pentagon / Venkateshwara / Jyothi. | RMS | 1 | 1 | One Rmt | 146440 | 146440
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 19937.806
166377.806
|  |  | Rate per Each | [5 empty] | 166378
71 |  |  | U.G Cables
a) | 4.1.1 | f | Supply of 16 Sqmm 4 Core XLPE insulated, 1100V grade armoured alluminium cable as per specification confirming to IS:7098 Makes : Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / RR kable / Finecab / RPG. | RMS | 1 | 1 | One Rmt | 280 | 280
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 38.122
318.122
|  |  | Rate per Meter | [5 empty] | 319
b) | 4.1.1 | h | Supply of 35 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable as per specification confirming to IS:7098 Makes : Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / RR kable / Finecab / RPG. | RMS | 1 | 1 | One Rmt | 430 | 430
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 58.5445
488.5445
|  |  | Rate per Meter | [5 empty] | 489
c) | 4.1.1 | i | Supply of 50 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable as per specification confirming to IS:7098 Makes : Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / RR kable / Finecab / RPG. | RMS | 1 | 1 | One Rmt | 570 | 570 |  | 50 | 30 | 539 | 16170
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 77.6055
647.6055
|  |  | Rate per Meter | [5 empty] | 648
d) | 4.1.1 | j | Supply of 70 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable as per specification confirming to IS:7098 Makes : Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / RR kable / Finecab / RPG. | RMS | 1 | 1 | One Rmt | 730 | 730
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 99.3895
829.3895
|  |  | Rate per Meter | [5 empty] | 830
e) | 4.1.1 | k | Supply of 95 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable as per specification confirming to IS:7098 Makes : Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / RR kable / Finecab / RPG. | RMS | 1 | 1 | One Rmt | 950 | 950
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 129.3425
1079.3425
|  |  | Rate per Meter | [5 empty] | 1080
f) | 4.1.1 | l | Supply of 120 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable as per specification confirming to IS:7098 Makes : Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / RR kable / Finecab / RPG. | RMS | 1 | 1 | One Rmt | 1170 | 1170
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 159.2955
1329.2955
|  |  | Rate per Meter | [5 empty] | 1330
g) | 4.1.1 | n | Supply of 185 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable as per specification confirming to IS:7098 Makes :Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / RR kable / Finecab / RPG. | RMS | 1 | 1 | One Rmt | 1620 | 1620
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 220.563
1840.563
|  |  | Rate per Meter | [5 empty] | 1841
h) | 4.1.1 | o | Supply of 240 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable as per specification confirming to IS:7098 Makes :Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / RR kable / Finecab / RPG. | RMS | 1 | 1 | One Rmt | 2060 | 2060
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 280.469
2340.469
|  |  | Rate per Meter | [5 empty] | 2341
i) | 4.1.1 | p | Supply of 300 Sqmm 3.5 Core XLPE insulated, 1100V grade armoured alluminium cable as per specification confirming to IS:7098 Makes : Torrent / Unicab / Universal / Polycab / Havells / Gloster / KEI / Finolex / RR kable / Finecab / RPG. | RMS | 1 | 1 | One Rmt | 2510 | 2510
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 341.7365
2851.7365
|  |  | Rate per Meter | [5 empty] | 2852
72 |  |  | Earth work excavation of Trench in hard ground soil and Sand filling shall be provided at the bottom of trench before laying the cable and laying of U.G cables from 95 Sqmm up to 400 sqmm covering the cable with bricks and back filling of Trench duly providing route indicator at every 8 Mtrs distance embedded in C.C including cost and conveyance of materials and labour charges etc., complete.
b) Labour charges
| 1 |  | Skilled Electrician. | 1.6 | day | 1 | day | 735 | 1176
| 2 |  | Helper (Electrical). | 3.3 | day | 1 | day | 615 | 2029.5
| 3 |  | Man Mazdoor for spreading the sand and back filling of the exacavated soils. | 2.5 | day | 1 | day | 615 | 1537.5
| 4 |  | Man Mazdoor for concreating and embedding of cable route indicators. | 2.1 | day | 1 | day | 545 | 1144.5
|  |  | Labour Charges for 100 Mtrs | [5 empty] | 5887.5
|  |  | Labour Charges for 1 Mtr | [5 empty] | 58.875
a) Material
| 10.4.15 |  | Earth work excacvation | 36 | Cum | 1 | Cum | 318 | 11448
| 10.4.11 |  | Cost of Sand. | 4 | Cum | 1 | Cum | 1274 | 5096
| 10.4.12 |  | Cost of Bricks. | 1000 | Nos | 952 | Nos | 9702 | 9236.304
| 10.4.10 |  | Cement. | 25 | Kg | 1 | Kg | 9 | 225
| 10.1.25 |  | Cable root Indicators. | 12 | Nos | 1 | Nos | 124 | 1488
|  |  | Cost of Material for laying of cable in trench for | 100 | Mtrs |  |  |  | 27493.304
|  |  | Cost of Material for laying of cable in trench for | 1 | Mtrs |  |  |  | 274.933
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 333
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 45.3379
378.3379
|  |  | Rate per Meter | [5 empty] | 378
73 |  |  | Earth work excavation of Trench in hard ground soil and Sand filling shall be provided at the bottom of trench before laying the cable and laying of U.G cables up to 70 sqmm covering the cable with back filling of Trench duly providing route indicator embedded in C.C including cost and conveyance of materials and labour charges etc., complete.
b) Labour charges
| 1 |  | Skilled Electrician. | 1 | day | 1 | day | 735 | 735
| 2 |  | Helper (Electrical). | 2 | day | 1 | day | 615 | 1230
| 3 |  | Man Mazdoor for spreading the sand and back filling of the exacavated soils. | 2.5 | day | 1 | day | 615 | 1537.5
| 4 |  | Man Mazdoor for concreating and embedding of cable route indicators. | 2.1 | day | 1 | day | 545 | 1144.5
|  |  | Labour Charges for 100 Mtrs | [5 empty] | 4647
|  |  | Labour Charges for 1 Mtr | [5 empty] | 46.47
a) Material
| 10.4.15 |  | Earth work excacvation including all soils for trench, | 36 | Cum | 1 | Cum | 318 | 11448
| 10.4.11 |  | Cost of Sand. | 4 | Cum | 1 | Cum | 1274 | 5096
| 10.4.12 |  | Cost of Bricks. | 1000 | Nos | 952 | Nos | 9702 | 9236.304
| 10.4.10 |  | Cement. | 25 | Kg | 1 | Kg | 9 | 225
| 10.1.25 |  | Cable root Indicators. | 12 | Nos | 1 | Nos | 124 | 1488
|  |  | Cost of Material for laying of cable in trench for | 100 | Mtrs |  |  |  | 27493.304
|  |  | Cost of Material for laying of cable in trench for | 1 | Mtrs |  |  |  | 274.933
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 321
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 43.7041
364.7042
|  |  | Rate per Meter | [5 empty] | 365
74 |  |  | Laying of PVC armoured under ground cable from 95 Sq.mm to 400 Sqmm fixing on chromium plated metallic base saddles on wall as per IS 1255 and as directed by the department including cost and conveyance of all materials and labour charges etc., complete.
b) Labour charges
| 1 |  | Skilled Electrician. | 1.5 | day | 1 | day | 735 | 1102.5
| 3 |  | Helper (Electrical). | 2.3 | day | 1 | day | 615 | 1414.5
|  |  | Labour Charges for 100 Mtrs | [5 empty] | 2517
|  |  | Labour Charges for 1 Mtr | [5 empty] | 25.17
a) Material
| 10.1.2 |  | Rawl Plugs. | 4 | Nos | 100 | Nos | 45 | 1.8
| 1.4.4 | f | Supply of No.8 Screws of 63/75mm. | 4 | Nos | 100 | Nos | 190 | 7.6
| 9.4.25 | h | Supply of Saddle / Clamps suitable for fixing 3.5 Core 300 Sqmm Cable. | 2 | Nos | 100 | Nos | 1134 | 22.68
32.08
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 58
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 7.8967
65.8967
|  |  | Rate per Meter | [5 empty] | 66
75 |  |  | Laying of PVC armoured under ground cable up to 70 Sqmm fixing on chromium plated metallic base saddles on wall as per IS 1255 and as directed by the department including cost and conveyance of all materials and labour charges etc., complete.
b) Labour charges
| 1 |  | Skilled Electrician. | 1.5 | day | 1 | day | 735 | 1102.5
| 3 |  | Helper (Electrical). | 2.3 | day | 1 | day | 615 | 1414.5
|  |  | Labour Charges for 100 Mtrs | [5 empty] | 2517
|  |  | Labour Charges for 1 Mtr | [5 empty] | 25.17
a) Material
| 9.1.2 |  | Rawl Plugs. | 4 | Nos | 100 | Nos | 45 | 1.8
| 1.4.4 | d | Supply of No.8 Screws of 35/38mm. | 4 | Nos | 100 | Nos | 190 | 7.6
| 9.4.25 | e | Supply of Saddle / Clamps suitable for fixing 3.5 Core 50 Sqmm Cable. | 2 | Nos | 100 | Nos | 668 | 13.36
|  |  | Cost of Material for Laying on wall for | 1 | Mtr |  |  |  | 22.76
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 48
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 6.5352
54.5352
|  |  | Rate per Meter | [5 empty] | 55
76 |  |  | Cable Terminations:
a |  |  | Termination of UG cables for 4 core 10 sq.mm & 4 core 16 sq.mm XLPE insulated armoured cable with fixing of heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket, with required lugs etc complete. Makes: SMI / Commet / Dowels.
b) Labour charges
| 1 |  | Skilled Electrician. | 0.02 | day | 1 | day | 735 | 14.7
| 2 |  | Lineman Electric / Telephone | 0.02 | day | 1 | day | 615 | 12.3
| 3 |  | Helper (Electrical). | 0.02 | day | 1 | day | 615 | 12.3
|  |  | Labour Charges for each | [5 empty] | 39.3
a) Material
| 4.3.2 | c | Double compression weather proof type brass cable Glands for 4 core XLPE armoured cable up to 16.0 Sq.mm | 1 | Nos | 1 | Nos | 430 | 430
| 4.4.2 | a | aluminium lugs for cable upto 16 Sq.mm | 4 | Nos | 1 | Nos | 35 | 140
570
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 609
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 82.9153
691.9153
|  |  | Rate per Each | [5 empty] | 692
b |  |  | Termination of UG cables for 3.5 core 35 sqmm XLPE insulated armoured cable with fixing of heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket, with required lugs etc complete. Makes: SMI / Commet / Dowels.
b) Labour charges
| 1 |  | Skilled Electrician. | 0.03 | day | 1 | day | 735 | 22.05
| 2 |  | Lineman Electric / Telephone | 0.03 | day | 1 | day | 615 | 18.45
| 3 |  | Helper (Electrical). | 0.03 | day | 1 | day | 615 | 18.45
|  |  | Labour Charges for each | [5 empty] | 58.95
a) Material
| 4.3.2 | d | Double compression weather proof type brass cable glands for 3.5 core XLPE armoured cable from 35 Sqmm | 1 | Nos | 1 | Nos | 515 | 515
| 4.4.2 | a | aluminium lugs for cable upto 16 Sq.mm | 1 | Nos | 1 | Nos | 35 | 35
| 4.4.2 | c | aluminium lugs for cable of 35 Sq.mm | 3 | Nos | 1 | Nos | 50 | 150
700
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 758
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 103.2017
861.2017
|  |  | Rate per Each | [5 empty] | 861
c |  |  | Termination of UG cables for 3.5 core 50 sq.mm XLPE insulated armoured cable with fixing of heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket, with required lugs etc complete. Makes: SMI / Commet / Dowels.
b) Labour charges
| 1 |  | Skilled Electrician. | 0.05 | day | 1 | day | 735 | 36.75
| 2 |  | Lineman Electric / Telephone | 0.05 | day | 1 | day | 615 | 30.75
| 3 |  | Helper (Electrical). | 0.05 | day | 1 | day | 615 | 30.75
|  |  | Labour Charges for each | [5 empty] | 98.25
a) Material
| 4.3.2 | e | Double compression weather proof type brass cable glands for 3.5 core XLPE armoured cable from 50.0 Sq.mm | 1 | Nos | 1 | Nos | 640 | 640
| 4.4.2 | b | aluminium lugs for cable of 25 Sq.mm | 1 | Nos | 1 | Nos | 40 | 40
| 4.4.2 | d | aluminium lugs for cable of 50 Sq.mm | 3 | Nos | 1 | Nos | 55 | 165
845
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 943
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 128.3894
1071.3894
|  |  | Rate per Each | [5 empty] | 1071
d |  |  | Termination of UG cables for 3.5 core 70 sq.mm XLPE insulated armoured cable with fixing of heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket, with required lugs etc complete. Makes: SMI / Commet / Dowels.
b) Labour charges
| 1 |  | Skilled Electrician. | 0.07 | day | 1 | day | 735 | 51.45
| 2 |  | Lineman Electric / Telephone | 0.07 | day | 1 | day | 615 | 43.05
| 3 |  | Helper (Electrical). | 0.07 | day | 1 | day | 615 | 43.05
|  |  | Labour Charges for each | [5 empty] | 137.55
a) Material
| 4.3.2 | f | Double compression weather proof type brass cable glands for 3.5 core XLPE armoured cable from 70 Sqmm | 1 | Nos | 1 | Nos | 990 | 990
| 4.4.2 | c | aluminium lugs for cable of 35 Sq.mm | 1 | Nos | 1 | Nos | 50 | 50
| 4.4.2 | e | aluminium lugs confirming to I.S specifications for cable of 70 Sq.mm | 3 | Nos | 1 | Nos | 60 | 180
1220
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 1357
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 184.7555
1541.7556
|  |  | Rate per Each | [5 empty] | 1542
e |  |  | Termination of UG cables for 3.5 core 95 sq.mm XLPE insulated armoured cable with fixing of heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket, with required lugs etc complete. Makes: SMI / Commet / Dowels.
b) Labour charges
| 1 |  | Skilled Electrician. | 0.095 | day | 1 | day | 735 | 69.825
| 2 |  | Lineman Electric / Telephone | 0.095 | day | 1 | day | 615 | 58.425
| 3 |  | Helper (Electrical). | 0.095 | day | 1 | day | 615 | 58.425
|  |  | Labour Charges for each | [5 empty] | 186.675
a) Material
| 4.3.2 | f | Double compression weather proof type brass cable glands for 3.5 core XLPE armoured cable from 95 Sqmm | 1 | Nos | 1 | Nos | 990 | 990
| 4.4.2 | d | aluminium lugs for cable of 50 Sq.mm | 1 | Nos | 1 | Nos | 55 | 55
| 4.4.2 | f | aluminium lugs confirming to I.S specifications for cable of 95 Sq.mm | 3 | Nos | 1 | Nos | 70 | 210
1255
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 1441
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 196.1921
1637.1922
|  |  | Rate per Each | [5 empty] | 1637
f |  |  | Termination of UG cables for 3.5 core 120 sqmm XLPE insulated armoured cable with fixing of heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket, with required lugs etc complete. Makes: SMI / Commet / Dowels.
b) Labour charges
| 1 |  | Skilled Electrician. | 0.12 | day | 1 | day | 735 | 88.2
| 2 |  | Lineman Electric / Telephone | 0.12 | day | 1 | day | 615 | 73.8
| 3 |  | Helper (Electrical). | 0.12 | day | 1 | day | 615 | 73.8
|  |  | Labour Charges for each | [5 empty] | 235.8
a) Material
| 4.3.2 | g | Double compression weather proof type brass cable glands for 3.5 core XLPE armoured cable from 120 Sqmm to 150.0 Sq.mm | 1 | Nos | 1 | Nos | 1340 | 1340
| ELEC-4.4.2 | e | aluminium lugs for cable of 70 Sq.mm | 1 | Nos | 1 | Nos | 60 | 60
| ELEC-4.4.2 | g | aluminium lugs for cable of 120 Sq.mm | 3 | Nos | 1 | Nos | 90 | 270
1670
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 1905
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 259.3657
2164.3657
|  |  | Rate per Each | [5 empty] | 2164
g |  |  | Termination of UG cables for 3.5 core 185 sqmm XLPE insulated armoured cable with fixing of heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket, with required lugs etc complete. Makes: SMI / Commet / Dowels.
b) Labour charges
| 1 |  | Skilled Electrician. | 0.185 | day | 1 | day | 735 | 135.975
| 2 |  | Lineman Electric / Telephone | 0.185 | day | 1 | day | 615 | 113.775
| 3 |  | Helper (Electrical). | 0.185 | day | 1 | day | 615 | 113.775
|  |  | Labour Charges for each | [5 empty] | 363.525
a) Material
| 4.3.2 | h | Double compression weather proof type brass cable glands for 3.5 core XLPE armoured cable for 185 Sqmm | 1 | Nos | 1 | Nos | 1630 | 1630
| ELEC-4.4.2 | f | aluminium lugs confirming to I.S specifications for cable of 95 Sq.mm. | 1 | Nos | 1 | Nos | 70 | 70
| ELEC-4.4.2 | i | aluminium lugs confirming to I.S specifications for cable of 185 Sq.mm | 3 | Nos | 1 | Nos | 160 | 480
2180
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 2543
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 346.2294
2889.2294
|  |  | Rate per Each | [5 empty] | 2889
h |  |  | Termination of UG cables for 3.5 core 240 Sqmm XLPE insulated armoured cable with fixing of heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket, with required lugs etc complete. Makes: SMI / Commet / Dowels.
b) Labour charges
| 1 |  | Skilled Electrician. | 0.2 | day | 1 | day | 735 | 147
| 2 |  | Lineman Electric / Telephone | 0.2 | day | 1 | day | 615 | 123
| 3 |  | Helper (Electrical). | 0.2 | day | 1 | day | 615 | 123
|  |  | Labour Charges for each | [5 empty] | 393
a) Material
| 4.3.2 | i | Double compression weather proof type brass cable glands for 3.5 core XLPE armoured cable for 240 Sqmm | 1 | Nos | 1 | Nos | 2100 | 2100
| ELEC-4.4.2 | g | aluminium lugs confirming to I.S specifications for cable of 120 Sq.mm. | 1 | Nos | 1 | Nos | 90 | 90
| ELEC-4.4.2 | j | aluminium lugs confirming to I.S specifications for cable of 240 Sq.mm | 3 | Nos | 1 | Nos | 200 | 600
2790
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 3183
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 433.3654
3616.3654
|  |  | Rate per Each | [5 empty] | 3616
i |  |  | Termination of UG cables for 3.5 Core 300 Sqmm XLPE insulated armoured cable with fixing of heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket, with required lugs etc complete. Makes: SMI / Commet / Dowels.
b) Labour charges
| 1 |  | Skilled Electrician. | 0.2 | day | 1 | day | 735 | 147
| 2 |  | Lineman Electric / Telephone | 0.2 | day | 1 | day | 615 | 123
| 3 |  | Helper (Electrical). | 0.2 | day | 1 | day | 615 | 123
|  |  | Labour Charges for each | [5 empty] | 393
a) Material
| 4.3.2 | j | Double compression weather proof type brass cable glands glands for 3.5 core XLPE armoured cable for 300 Sqmm | 1 | Nos | 1 | Nos | 2430 | 2430
| ELEC-4.4.2 | h | aluminium lugs confirming to I.S specifications for cable of 150 Sq.mm. | 1 | Nos | 1 | Nos | 140 | 140
| ELEC-4.4.2 | k | aluminium lugs confirming to I.S specifications for cable of 300 Sq.mm | 3 | Nos | 1 | Nos | 270 | 810
3380
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 3773
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 513.6939
4286.6939
|  |  | Rate per Each | [5 empty] | 4287
77 | 10.1.33 |  | Supply of Rubber hand gloves suitable for 11 KV. | Nos | 1 | 2 | EACH | 1000 | 2000
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 272.3
2272.3
|  |  | Rate Per Pair | [5 empty] | 2272
78 | 10.4.26 | b | Supply and fixing of PVC synthetic elastomer electrically insulated mat with Class B insulation conforming to IS: 15652-2006 having 2.5mm thickness upto 11KV. | Sqmtrs | 1 | 1 | One Sqmtrs | 4967 | 4967
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 676.257
5643.2571
|  |  | Rate per Each | [5 empty] | 5643
79 | 10.2.7 |  | Providing & Fixing of Shock instrution chart in English / Hindi / Telugu duly framed with front glass | Nos | 1 | 1 | EACH | 576 | 576
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 78.4224
654.4224
|  |  | Rate per Each | [5 empty] | 654
80 | 10.2.1 | a | Providing & Fixing of Danger Notice Plates of size 250x200mm, shall comply with IS:2551-1982. | Nos | 1 | 1 | EACH | 286 | 286
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 38.9389
324.9389
|  |  | Rate per Each | [5 empty] | 325
81 | 10.4.28 |  | Providing floor mounting stand for keeping 4No of fire bucket 1500mm length, 900mm height made out of 40x40x6mm angle iron welded with 4 hooks and duly painted with one coat of red lead and two coats of enamel paint. | Nos | 1 | 1 | EACH | 1402 | 1402
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 190.8823
1592.8823
|  |  | Rate per Each | [5 empty] | 1593
82 | 10.4.27 |  | Providing & Supply of round bottom G.I sheet bucket of 9 Ltrs. Capacity as per IS:2546 made out of 24 gauge GI sheet with extra handle at bottom duly painted inside and red out side with printed with FIRE Mark for stand and hook and filled with sand and arranged to existing stand or hook. | Nos | 1 | 1 | EACH | 344 | 344
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 46.8356
390.8356
|  |  | Rate per Each | [5 empty] | 391
83 | 10.1.32 |  | First Aid box 18" x 12" x 8" containing material as prescribed by St. John Ambulance brigade OR Indian Red Cross complete as required. | Nos | 1 | 1 | EACH | 1512 | 1512
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 205.8588
1717.8588
|  |  | Rate per Each | [5 empty] | 1718
84 | AR |  | Preparation of Drawings of existing or new installations and obtaining approval from the CEIG complete as per the requirement at site.(AR) | Nos | 1 | 1 | EACH | 40000 | 40000
|  |  | Rate Per Job | [5 empty] | 40000
85 | Ele 15.1.1 | b | Supply, transportation, installation, testing and commissioning of 8 passenger Gearless & Machine Room less elevator with following specifications with connected minor civil works required for installation of Lift including all accessories, scoffolding, requried channels, loading and unloading of materials etc, including comprehensive maintenance of lifts during the defect liability period. Makes: Schindler / Kone / OTIS / Mitsubishi or equivalent. Make & Model will be Approved by the Head Office / Engineer-in-charge.
| For Girls Hostel |  | Rate per each Lift for Ground + 3 Floors. 4 Stops | 1 |  | NO |  | 1511700 | 1511700
|  |  | Add 3 floor (If building is above 5 floors, speed 1.5 - 1.75 Mtr / Sec. Further, for increase in speed of the motor, floor for the above, Rs. 1,50,000/- to be added | 3 |  | stops |  | 150000 | 450000
1961700
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 267085.455
2228785.455
|  |  | Rate per Each | [5 empty] | 2228785
| Ele 15.1.1 | b | Supply, transportation, installation, testing and commissioning of 8 passenger Gearless & Machine Room less elevator with following specifications with connected minor civil works required for installation of Lift including all accessories, scoffolding, requried channels, loading and unloading of materials etc, including comprehensive maintenance of lifts during the defect liability period. Makes: Schindler / Kone / OTIS / Mitsubishi or equivalent. Make & Model will be Approved by the Head Office / Engineer-in-charge.
| For boys Hostel |  | Rate per each Lift for Ground + 3 Floors. 4 Stops | 1 |  | NO |  | 1511700 | 1511700
|  |  | Add 1 floor (Further, increase in floor for the above, rate per floor @ Rs. 1,00,000/- to be added) | 1 |  | stops |  | 100000 | 100000
1611700
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 219432.955
1831132.955
|  |  | Rate per Each | [5 empty] | 1831133
| Ele 15.1.1 | b | Supply, transportation, installation, testing and commissioning of 8 passenger Gearless & Machine Room less elevator with following specifications with connected minor civil works required for installation of Lift including all accessories, scoffolding, requried channels, loading and unloading of materials etc, including comprehensive maintenance of lifts during the defect liability period. Makes: Schindler / Kone / OTIS / Mitsubishi or equivalent. Make & Model will be Approved by the Head Office / Engineer-in-charge.
| Interns Hostels |  | Rate per each Lift for Ground + 3 Floors. 4 Stops | 1 |  | NO |  | 2233800 | 2233800
2233800
|  |  | Add Contractors Profit | 0.13615 |  |  |  |  | 304131.87
2537931.87
|  |  | Rate per Each | [5 empty] | 2537932

## INV
GIRLS HOSTEL | [5 empty] | BOYS HOSTEL | [5 empty] | SR. RESIDENTS HOSTEL
S.NO | ELECTRICAL FIXTURE | QUANTITY | UNITS | LOAD ( W ) | TOTAL LOAD IN (W) | S.NO | ELECTRICAL FIXTURE | QUANTITY | UNITS | LOAD ( W ) | TOTAL LOAD IN (W) | S.NO | ELECTRICAL FIXTURE | QUANTITY | UNITS | LOAD ( W ) | TOTAL LOAD IN (W)
1 | TUBE LIGHT | 950 | Pt | 20 | 19000 | 1 | TUBE LIGHT | 410 | Pt | 20 | 8200 | 1 | TUBE LIGHT | 200 | Pt | 20 | 4000
2 | FAN 48" | 480 | Pt | 60 | 28800 | 2 | FAN 48" | 215 | Pt | 60 | 12900 | 2 | FAN 48" | 90 | Pt | 60 | 5400
3 | SBH 5W | 300 | No | 5 | 1500 | 3 | SBH 5W | 100 | No | 5 | 500 | 3 | SBH 5W | 200 | No | 5 | 1000
4 | BULK HEAD | 0 | No | 10 | 0 | 4 | BULK HEAD | 0 | No | 10 | 0 | 4 | BULK HEAD | 0 | No | 10 | 0
5 | MIRROR LIGHT | 10 | No | 10 | 100 | 5 | MIRROR LIGHT | 10 | No | 10 | 100 | 5 | MIRROR LIGHT | 10 | No | 10 | 100
6 | EXHAUST FAN LD | 10 | No | 60 | 600 | 6 | EXHAUST FAN LD | 20 | No | 60 | 1200 | 6 | EXHAUST FAN LD | 90 | No | 60 | 5400
7 | EXHAUST FAN HD | 75 | No | 60 | 4500 | 7 | EXHAUST FAN hD | 25 | No | 60 | 1500 | 7 | EXHAUST FAN hD | 0 | No | 60 | 0
8 | 2'x2' LED DOWN LIGHT | 0 | No | 36 | 0 | 8 | 2'x2' LED DOWN LIGHT | 0 | No | 36 | 0 | 8 | 2'x2' LED DOWN LIGHT | 0 | No | 36 | 0
9 | 12W LED LIGHT | 0 | No | 12 | 0 | 9 | 12W LED LIGHT | 0 | No | 12 | 0 | 9 | 12W LED LIGHT | 0 | No | 12 | 0
10 | 18W LED LIGHT | 0 | No | 18 | 0 | 10 | 18W LED LIGHT | 0 | No | 18 | 0 | 10 | 18W LED LIGHT | 0 | No | 18 | 0
11 | CELLING POINT | 30 | No | 0 | 0 | 11 | CELLING POINT | 20 | No | 0 | 0 | 11 | CELLING POINT | 10 | No | 0 | 0
12 | CALLING BELL | 5 | No | 0 | 0 | 12 | CALLING BELL | 5 | No | 0 | 0 | 12 | CALLING BELL | 5 | No | 0 | 0
13 | 6A COMMON | 255 | Pt | 60 | 15300 | 13 | 6A COMMON | 110 | Pt | 60 | 6600 | 13 | 6A COMMON | 100 | Pt | 60 | 6000
14 | 6A SEPARATE | 30 | Pt | 60 | 1800 | 14 | 6A SEPARATE | 15 | Pt | 60 | 900 | 14 | 6A SEPARATE | 5 | Pt | 60 | 300
15 | 16A SOCKET | 35 | Pt | 500 | 17500 | 15 | 16A SOCKET | 20 | Pt | 500 | 10000 | 15 | 16A SOCKET | 5 | Pt | 500 | 2500
16 | COMPUTER SOCKET ( 4x(6A Soc+Switch) ) | 0 | Pt | 400 | 0 | 16 | COMPUTER SOCKET ( 4x(6A Soc+Switch) ) | 0 | Pt | 400 | 0 | 16 | COMPUTER SOCKET ( 4x(6A Soc+Switch) ) | 0 | Pt | 400 | 0
17 | COMPUTER SOCKET ( 3x(6A Soc+Switch) ) | 5 | Pt | 200 | 1000 | 17 | COMPUTER SOCKET ( 3x(6A Soc+Switch) ) | 5 | Pt | 200 | 1000 | 17 | COMPUTER SOCKET ( 3x(6A Soc+Switch) ) | 1 | Pt | 200 | 200
18 | CP-1 (2x(6A Soc+Switch) ) | 400 | Pt | 100 | 40000 | 18 | CP-1 (2x(6A Soc+Switch) ) | 200 | Pt | 100 | 20000 | 18 | CP-1 (2x(6A Soc+Switch) ) | 81 | Pt | 100 | 8100
19 | TELEPHONE | 2 | No | 0 | 0 | 19 | TELEPHONE | 2 | No | 0 | 0 | 19 | TELEPHONE | 1 | No | 0 | 0
20 | TELEVISION | 3 | No | 0 | 0 | 20 | TELEVISION | 5 | No | 0 | 0 | 20 | TELEVISION | 1 | No | 0 | 0
21 | LAN POINT | 2 | No | 0 | 0 | 21 | LAN POINT | 2 | No | 0 | 0 | 21 | LAN POINT | 1 | No | 0 | 0
22 | AC | 5 | No | 1500 | 7500 | 22 | AC | 5 | No | 1500 | 7500 | 22 | AC | 0 | No | 1500 | 0
23 | GEYSER | 50 | No | 1000 | 50000 | 23 | GEYSER | 15 | No | 1000 | 15000 | 23 | GEYSER | 90 | No | 1000 | 90000
24 | BHP (1x(6A Soc+Switch) 1x(16A Soc+Switch)) | 0 | No | 500 | 0 | 24 | BHP (1x(6A Soc+Switch) 1x(16A Soc+Switch)) | 0 | No | 500 | 0 | 24 | BHP (1x(6A Soc+Switch) 1x(16A Soc+Switch)) | 0 | No | 500 | 0
25 | BHP - 2 (2x(6A Soc+Switch)2x(16A Soc+Switch) ) | 0 | No | 1200 | 0 | 25 | BHP - 2 (2x(6A Soc+Switch)2x(16A Soc+Switch) ) | 0 | No | 1200 | 0 | 25 | BHP - 2 (2x(6A Soc+Switch)2x(16A Soc+Switch) ) | 0 | No | 1200 | 0
26 | BHP - 3 (3x(6A Soc+Switch)1x(16A Soc+Switch) ) | 0 | No | 1300 | 0 | 26 | BHP - 3 (3x(6A Soc+Switch)1x(16A Soc+Switch) ) | 0 | No | 1300 | 0 | 26 | BHP - 3 (3x(6A Soc+Switch)1x(16A Soc+Switch) ) | 0 | No | 1300 | 0
27 | CCTV - DOME CAMERA | 70 | No | 0 | 0 | 27 | CCTV - DOME CAMERA | 15 | No | 0 | 0 | 27 | CCTV - DOME CAMERA | 10 | No | 0 | 0
28 | CCTV - BULLET CAMERA | 4 | No | 0 | 0 | 28 | CCTV - BULLET CAMERA | 2 | No | 0 | 0 | 28 | CCTV - BULLET CAMERA | 2 | No | 0 | 0
29 | O.T LIGHT | 0 | No | 0 | 0 | 29 | O.T LIGHT | 0 | No | 0 | 0 | 29 | O.T LIGHT | 0 | No | 0 | 0
30 | 63A MCCB | 0 |  |  | 0 | 30 | 63A MCCB | 0 |  |  | 0 | 30 | 63A MCCB | 0 |  |  | 0
31 | 125A MCCB | 0 |  |  | 0 | 31 | 125A MCCB | 0 |  |  | 0 | 31 | 125A MCCB | 0 |  |  | 0
32 | DB's FOR LIGHTING( 3-PHASE) | 25 |  |  | 0 | 32 | DB's FOR LIGHTING( 3-PHASE) | 10 |  |  | 0 | 32 | DB's FOR LIGHTING( 3-PHASE) | 10 |  |  | 0
33 | DB's FOR LIGHTING( 1-PHASE) | 5 |  |  | 0 | 33 | DB's FOR LIGHTING( 1-PHASE) | 5 |  |  | 0 | 33 | DB's FOR LIGHTING( 1-PHASE) | 1 |  |  | 0
34 | DB's FOR POWER | 25 |  |  | 0 | 34 | DB's FOR POWER | 10 |  |  | 0 | 34 | DB's FOR POWER | 10 |  |  | 0
35 | TOTAL LIGHT POINT'S | 1295 |  |  |  | 35 | TOTAL LIGHT POINT'S | 545 |  |  |  | 35 | TOTAL LIGHT POINT'S | 425
36 | TOTAL FAN'S & EXHAUST FAN | 565 |  |  |  | 36 | TOTAL FAN'S & EXHAUST FAN | 260 |  |  |  | 36 | TOTAL FAN'S & EXHAUST FAN | 180
37 | TOTAL POINTS | 1860 |  |  |  | 37 | TOTAL POINTS | 805 |  |  |  | 37 | TOTAL POINTS | 605
38 | TOTAL 16A OCKETS , AC's POINTS & DB'S POINTS | 380 |  |  |  | 38 | TOTAL 16A OCKETS , AC's POINTS & DB'S POINTS | 175 |  |  |  | 38 | TOTAL 16A OCKETS , AC's POINTS & DB'S POINTS | 131
39 | TOTAL COMPUTER , TELEPHONE & LAN POINTS | 412 |  |  |  | 39 | TOTAL COMPUTER , TELEPHONE & LAN POINTS | 214 |  |  |  | 39 | TOTAL COMPUTER , TELEPHONE & LAN POINTS | 85
40 | TOTAL LOAD |  |  |  | 187600 | 40 | TOTAL LOAD |  |  |  | 85400 | 40 | TOTAL LOAD |  |  |  | 123000
41 | ASSESSMENT OF CONDUIT |  |  |  |  | 41 | ASSESSMENT OF CONDUIT |  |  |  |  | 41 | ASSESSMENT OF CONDUIT
42 | FOR LIGHT POINTS |  |  |  | 5580 | 42 | FOR LIGHT POINTS |  |  |  | 2415 | 42 | FOR LIGHT POINTS |  |  |  | 1815
43 | FOR CIRCUIT |  |  |  | 4856.25 | 43 | FOR CIRCUIT |  |  |  | 2043.75 | 43 | FOR CIRCUIT |  |  |  | 1593.75
44 | FOR 16A SOC , DB's & AC's |  |  |  | 11400 | 44 | FOR 16A SOC , DB's & AC's |  |  |  | 5250 | 44 | FOR 16A SOC , DB's & AC's |  |  |  | 3930
45 | FOR TELEPHONE & LAN |  |  |  | 12360 | 45 | FOR TELEPHONE & LAN |  |  |  | 6420 | 45 | FOR TELEPHONE & LAN |  |  |  | 2550
46 | TOTAL LENGHT OF CONDUIT |  |  |  | 34196.25 | 46 | TOTAL LENGHT OF CONDUIT |  |  |  | 16128.75 | 46 | TOTAL LENGHT OF CONDUIT |  |  |  | 9888.75
47 | CONDUIT IN SLAB |  |  |  | 20517.75 | 47 | CONDUIT IN SLAB |  |  |  | 9677.25 | 47 | CONDUIT IN SLAB |  |  |  | 5933.25
48 | CONDUIT IN WALL |  |  |  | 13678.5 | 48 | CONDUIT IN WALL |  |  |  | 6451.5 | 48 | CONDUIT IN WALL |  |  |  | 3955.5
49 | RUN OF MAINS |  |  |  |  | 49 | RUN OF MAINS |  |  |  |  | 49 | RUN OF MAINS
50 | 1OF 1.5SQ MM FOR SWITCH BOARD CIRCUIT |  |  |  | 1695 | 50 | 1OF 1.5SQ MM FOR SWITCH BOARD CIRCUIT |  |  |  | 780 | 50 | 1OF 1.5SQ MM FOR SWITCH BOARD CIRCUIT |  |  |  | 540
51 | 3 OF 1.5SQ MM FOR SWITCH BOARD CIRCUIT |  |  |  | 5580 | 51 | 3 OF 1.5SQ MM FOR SWITCH BOARD CIRCUIT |  |  |  | 2415 | 51 | 3 OF 1.5SQ MM FOR SWITCH BOARD CIRCUIT |  |  |  | 1815
52 | 3 OF 2.5 SQ MM FOR SWITCH BOARD CIRCUIT |  |  |  | 11887.5 | 52 | 3 OF 2.5 SQ MM FOR SWITCH BOARD CIRCUIT |  |  |  | 5590.625 | 52 | 3 OF 2.5 SQ MM FOR SWITCH BOARD CIRCUIT |  |  |  | 3120.625
53 | 3 OF 4.0 SQ MM FOR 16 SOCKET'S |  |  |  | 525 | 53 | 3 OF 4.0 SQ MM FOR 16 SOCKET'S |  |  |  | 300 | 53 | 3 OF 4.0 SQ MM FOR 16 SOCKET'S |  |  |  | 75
54 | 3 OF 6.0 SQ MM FOR AC's & SINGLE PHASE DB's |  |  |  | 125 | 54 | 3 OF 6.0 SQ MM FOR AC's & SINGLE PHASE DB's |  |  |  | 125 | 54 | 3 OF 6.0 SQ MM FOR AC's & SINGLE PHASE DB's |  |  |  | 0
55 | 5 OF 6.0 SQ MM FOR LDB's |  |  |  | 900 | 55 | 5 OF 6.0 SQ MM FOR LDB's |  |  |  | 450 | 55 | 5 OF 6.0 SQ MM FOR LDB's |  |  |  | 330
56 | 5 OF 10.0 SQ MM FOR PDB's |  |  |  | 750 | 56 | 5 OF 10.0 SQ MM FOR PDB's |  |  |  | 300 | 56 | 5 OF 10.0 SQ MM FOR PDB's |  |  |  | 300
57 | TOTAL LOAD |  |  |  | 187600 | 57 | TOTAL LOAD |  |  |  | 85400 | 57 | TOTAL LOAD |  |  |  | 123000
58 | TOTAL CURRENT |  |  |  | 35960277.1363 | 58 | TOTAL CURRENT |  |  |  | 16369976.9053 | 58 | TOTAL CURRENT |  |  |  | 23577367.2055
59 | DIVERSITY FACTOR | 0.66 |  |  |  | 59 | DIVERSITY FACTOR | 0.66 |  |  |  | 59 | DIVERSITY FACTOR | 0.66
60 | TOTAL LOAD AFTER DIVERSITY FACTOR IN KW |  |  |  | 123.816 | 60 | TOTAL LOAD AFTER DIVERSITY FACTOR IN KW |  |  |  | 56.364 | 60 | TOTAL LOAD AFTER DIVERSITY FACTOR IN KW |  |  |  | 81.18

## Sheet1
432
36
432
111 |  |  |  | 216
777
39
234