## Sheet2
SUPPLEMENTAL ITEMS
Sl.No |  | Item Description | UOM | Unit Rate (Rs.)
1 |  | Supply and installation of Under-deck Thermocol insulation sheets of 40 mm thick having more than 30 Kg/m3 density to ceiling by brush application of bituminous adhesive to the sheets and secured with screw along with washer at the centre of the sheet supported with GI wire running diagonally to the sheet of 2mm dia. | Sqm | 1014 | 262.74
2 |  | Supply and placing of the Design Mix Plain Cement Concrete of M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Concrete Batching Plant with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials. | Cum | 11740 | 28.01
3 |  | Supply and Laying of Floor leveller compund (self smoothing mortar) to level the surface, having bulk density not less than 2 Kg/l for a fresh mortor, compressive strength not less than 20 N/mm2, initial setting time not more than 40 minutes and offer a 25 minutes working time, The surface should be walkabe after 30 min of laying. (ICUs) | Sqm | 1460 | 725.55
4 |  | 800 KVA Transformer OLTC for transformers with RTCC: Supply, Transportation, Installation, Testing and Commissioning of 800 KVA TRANSFORMER with all test reports. The Transformer shall be designed and manufactured as per IS:1180 OLTC with level-II with initial filling of oil as per IS 335-1993. 1000 A LT Breaker Kiosk - 01 No.The basic details of the Transformer are as under. Makes: Kirloskar / PETE / Esennar / Voltamp / Crompton / ABB / Schneider. | Nos | 5086347 | 1
5 | MPS | 4 Gas Digital Alarm Panels : 4 Gas Digital Alarm Panel consisting of atl necessary accessories ie Pressure sensors,reguIators,hand valves ,pressure gauges ecL(Oxygen, Nitrous oxide, Medical Air, Vacuum) | Nos | 42150 | 1
6 | MPS | 6 Gas Digital Alarm Panele : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. | Nos | 60008 | 6
7 | MPS | Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. | Nos | 22201 | 1
8 | MPS | 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen. | Job | 48103 | 1
9 | MPS | Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED. | Job | 222013 | 1
10 |  | Supply and installation of 50mm thick double skin modular wall Panels made of 0.8 mm thick powder coated GI on both the sides, with 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, flush on both sides with maximum allowable gap of 3- 4mm filled with food grade silicon sealant and placed on cold rolled galvanised bottom tracks with a recess to provide floor to wall coving flush with the wall panel. This includes all required harware for completion Panels to be covered with a protective film to avoid any damages during transportation and installation | Sqm | 7450 | 312.396
11 |  | Supply and installation of 50mm thick double skin ceiling system made of 0.8 mm thick Powder Coated GI sheets on both sides, 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, panels flush towards room side with maximum allowable gap of 3-4mm at panel to panel joints filled with silicon sealant. Ceiling panels are suspended from the RCC slab by using concealed AL ceiling grid with tie rod and adjustable turn buckle arrangement etc. This includes all required hardware for completion. Panels to be covered with a protective film to avoid any damages during transportation and installation | Sqm | 7450 | 171.234
12 |  | Providing dadooing to walls with glazed full body ceramic wall tiles of size 800 x 1600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. | Sqm | 4665 | 119.385
13 | MPS | Glass Sliding Door in TIR-2 & TIR-3 *Size 1.8mt x 2.1mt. *The door will be sliding. ”The material of door will be Glass. *The door will be operate by sensor. *The door movement will be easy and smooth. | Nos | 270276 | 2
14 |  | Monitor Stand beside Bed in ICUs & TIRs | Nos | 6176 | 31
15 |  | Recording in counselling room | Job | 155378 | 1
17 |  | Local Area Network (LAN) System | Job | 460242 | 1
18 |  | Supply, Transportation and installation of 20KVA / 312V DC on line UPS system | Nos | 629358 | 2
19 |  | V-Board Partitions on top of false ceiling for partitioning of sterile corridor and non-sterile corridor | Sqm | 3640 | 16
20 | MPS | Manual Hermetically Sealed Sliding Doors (1.20mt x 2.10 mt) the door shall be a hermetically sealed, single sliding. ”The track shall be of stainless stœl/Aluminum and the running surface for the top rollers shall be suitably angled to reduce resistanœ to movement ”Door opening handle tower bolt 2 Nos. of 100mm x 10mm, 2 Nos of handles 100mm Iong and Heavy duty and shall be strong and sturdy. h4aterial shall be of SS (gloss/Matt finish). Shall be provided withhigh quality cylindrical/ESPG lock. “The door material shall be of HPL Color shall match me interior and care shall be taken to make the leaf strong and light weight “One shall be able to open and Öose the door effortlessly manually Operated. “Door opening handle shall be strong and sturdy. Matenal shall be of SS (gloss/Matt finish). Shall be provided with high quality cylindrical/ESPG lock. “Door leaf shall have high quality synthetic rubber gasket with kmg life to ensure hermetic sealing (to maintain air pressure differential). Air tightriess99.99% at a pressure of 75Pa. the finished floor on either side of the door shall be perfectly level (maximum permissible difference +1mm). “The overall thickness of the fînished door shall be 55 to 60mm. The inner part of the door shall be filled with CFC free polyurethane foam thickness of48mm or nearby.(SeaIed airtight to prevent fui1her ingress of any microbial organism). The door and controls shall œmply with IEE regulation. Æl motors used shall be DC brushless / PMDC motors with essenôal isolaüon from mains. Door shall be with vision window 300 mm x 300 mm with doubte glazed Smm thick panels and hermetically sealed with lead line protection. Door movement shall have minimum noise. | Nos | 564363 | 1
21 | MPS | 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | Job | 48103 | 1
22 | MPS | 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | Job | 17401 | 1