## Sheet1
Electrical
57 | 22 a | Supply and Fixing of 25mm dia Conduit Pipes surface on wall. | 10000 | Rmt
58 | 22 b | Supply and Fixing of 25mm dia Conduit Pipes Concealed on wall. | 4000 | Rmt
Wiring with run of 2 of 1.5 Sqmm Copper cable for points wiring.
59 | 23 a |  | 570 | Pts
Wiring with run of 2 of 1.5 Sqmm Copper cable for stairecase points wiring.
60 | 23 b |  | 10 | Pts
61 | 23 c | Supply and fixing of 6A/10A ISI Mark 3/2 pin Modular socket Common switch board | 25 | Pts
Wiring with 3 of 1.5 sq.mm with 6A switch and 6A, 3/2 pin socket Modular type with 6A switch control fixing on separate board.
62 | 23 d |  | 50 | Pts
63 | 23 e | Supply and fixing of 6A switchs - 2 Nos and 6A 3/2 pin socket - 3 Nos Modular type with cover plate | 200 | Pts
64 | 23 f | Supply & fixing of 16A/6A, 2 in one socket with 16A switch control modular type | 200 | Nos
65 | 23 g | Supply & fixing of 32A, socket with switch control | 18 | Nos
modular
66 | 23 h | Supply & fixing of 64A, socket with 64A switch control modular type | 4 | Nos
67 | 24 a | Supply and Run of 1 of 1.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable.
|  |  | 2000 | Rmt
68 | 24 b | Supply and Run of 3 of 1.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable .
|  |  | 2000 | Rmt
69 | 24 c | Supply and Run of 3 of 2.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable.
|  |  | 8000 | Rmt
70 | 24 d | Supply and Run of 3 runs of 4.0 sq mm (phase neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper
|  | cable. | 5000 | Rmt
Supply and Run of 3 of 6.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable.
71 | 24 e |  | 300 | Rmt
Supply and Run of 5 of 6.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable.
72 | 24 f |  | 300 | Rmt
Supply and Run of 5 of 10.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable.
73 | 24 g |  | 500 | Rmt
74 | 25 a | Supply and fixing of DP Metal Enclosure with IP 20 Protection DB Make with 1 No 20A, 10 KA DP MCB | 8 | Nos
Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 (For Lighting DBs)
75 | 25 b |  | 10 | Nos
Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 (For Power DB's)
76 | 25 c |  | 14 | Nos
77 | 25 d | Supply and fixing of 8 Way VTPN DB with IP 43 Protection as per IS:13032 | 5 | Nos
Supply and fixing of cable adopteres box with cover for DBs including, massanory work etc., complete.,
78 | 25 e |  | 10 | Nos
79 | 26 a | Providing independent earthing for Important equipment with 40mm dia 'B' class 2.5m long G.I pipe (GI Earthing) | 18 | Nos
80 | 26 b | Providing independent earthing by exacavating a pit to a depth of 2.25Mtr in all soils as per size specified in the data for Sophisticated Electronic equipment (Copper Earthing). | 18 | Nos
81 | 26 b 1 | Providing independent earthing for Important equipment with 100mm dia Heavy gauge C.I Earthing | 6 | Nos
82 | 26 c | Supply and Run of 50mm x 6mm G.I Strip | 400 | Rmt
83 | 26 d | Supply and Run of 25mm x 3mm copper strip | 400 | Rmt
84 | 27 a | Supply, transportation and fixing of 22W +/ 10% , >/ 2300 lumens, 1200mm length LED light | 20 | Nos
Supply, transportation and fixing 32-36W (>=3600 Lumens), 2' x2' (600mm x 600mm) slim panel LED
85 | 27 b | luminaire | 60 | Nos
Supply, transportation and fixing 12 W +/-10% (>= 1200 Lumens) Down lighter back lit LED Down Light Recessed / Surface
86 | 27 c |  | 215 | Nos
87 | 27 d | Supply, transportation and fixing 18 W +/-10% (>= 1800 Lumens) Down lighter back lit LED Down Light | 95 | Nos
88 | 27 e | Supply, transportation and fixing ISI mark batten holder | 8 | Nos
/ slanting holder
Supply, Transportation of energy efficient fan, 1200 mm sweep, aluminium body, consuming 28
89 | 27 f | W, BEE 5 star rated, ceiling fan | 40 | Nos
90 | 27 f 1 | Supply and fixing of Modular type Stepped electronic regulator. | 40 | Nos
91 | 27 f 2 | Labour charges for fixing of ceiling fan and regulator | 40 | Nos
92 | 27 f 3 | Supply and erecting 19/20mm steel tube down rod of one meter length | 40 | Nos
93 | 27 g | Supply of 12" (300mm) Light duty exhaust fan | 5 | Nos
94 | 27 h | Supply,Transportation of 12" (300mm) ISI, 900 RPM Heavy duty exhaust fan | 10 | Nos
95 | 27 i | Labour charges for fixing the exhaust fan in wall with necessary connections | 15 | Nos
96 | 27 j | Supply and fixing of GI louver shutter including GI mesh | 15 | Nos
Main Power Panel with 1000A 4 Pole ACB as incomer - 1 No and out goings 800 A 4P MCCB - 1 No., 630 A 4P MCCB - 1 No., 400A 4P MCCB - 4 Nos & 250A 4P
MCCB - 3 No's with required Digital Ammeter and Voltmer, LED Indicators
97 | 28 a) |  | 1 | Nos
Floor Power Panel : Incomer: 630A 4 Pole MCCB,- 1 No Outgoings 250 A 4P MCCB - 4 No's 125 A 4P MCCB - 10 No's, 63 A 4P MCCB - 4 No's with required Digital Ammeter and Voltmer, LED Indicators
98 | 28 b) |  | 1 | Nos
Electrical Lighting Panels : Incomer: 250 A 4 Pole MCCB - 1 No, Out Goings 125 A 4P MCCB - 4 No's 63
99 | 28 c) | A 4P MCCB - 3 No's with required Digital Ammeter and Voltmer, LED Indicators | 2 | Nos
130KVAR Out Door Capacitor panel : Incomer: 250A FP MCCB - 1 No, 63A 10KA TP MCB - 9 Nos. 20
KVAR Capacitor Duty contactors - 5 Nos., 10 KVAR Capacitor Duty contactors - 2 Nos, .5 KVAR Capacitor Duty contactors - 2 Nos. 12 stage APFC Relay - 1 No
100 | 28 d) |  | 1 | Nos
630 KVA Transformer OLTC for transformers with RTCC: Supply, Transportation, Installation, Testing and Commissioning of 630 KVA TRANSFORMER with all test reports. The Transformer shall be designed and manufactured as per IS:1180 OLTC with level-II with initial filling of oil as per IS 335-1993. 1000 A LT Breaker Kiosk - 01 No.The basic details of the Transformer are as under. Makes: Kirloskar / PETE / Esennar / Voltamp / Crompton / ABB / Schneider.
101 | 29 a) |  | 1 | Nos
102 | 30 a) | Supply of 25 Sqmm 3.5 Core XLPE insulated UG Cable. | 200 | Rmt
103 | 30 b) | Supply of 50 Sqmm 3.5 Core XLPE insulated UG Cable. | 200 | Rmt
104 | 30 c) | Supply of 70 Sqmm 3.5 Core XLPE insulated UG Cable. | 75 | Rmt
105 | 30 d) | Supply of 120 Sqmm 3.5 Core XLPE insulated UG | 50 | Rmt
Cable.
106 | 30 e) | Supply of 185 Sqmm 3.5 Core XLPE insulated UG | 50 | Rmt
Cable.
107 | 30 f) | Supply of 240 Sqmm 3.5 Core XLPE insulated UG | 100 | Rmt
Cable.
108 | 30 g) | Supply of 300 Sqmm 3.5 Core XLPE insulated UG | 500 | Rmt
Cable.
109 | 31 a) | Termination of UG cables of 3.5 core 25 Sq.mm | 8 | Nos
110 | 31 b) | Termination of UG cables of 3.5 core 50 Sq.mm | 8 | Nos
111 | 31 c) | Termination of UG cables of 3.5 core 70 Sq.mm | 8 | Nos
112 | 31 d) | Termination of UG cables of 3.5 core 120 Sq.mm | 4 | Nos
113 | 31 e) | Termination of UG cables of 3.5 core 185 Sq.mm | 4 | Nos
114 | 31 f) | Termination of UG cables of 3.5 core 240 Sq.mm | 4 | Nos
115 | 31 g) | Termination of UG cables of 3.5 core 300 Sq.mm | 12 | Nos
116 | 31 h) | Earth work excavation of Trench laying of U.G cables up to 70 sqmm | 100 | Rmt
117 | 31 i) | Earth work excavation of Trench laying of U.G cables from 95 Sqmm | 100 | Rmt
118 | 31 j) | Laying of PVC armoured under ground cable up to 95 Sqmm on wall | 200 | Rmt
119 | 31 k) | Laying of PVC armoured under ground cable from 120 Sq.mm to 400 Sqmm saddles on wall | 700 | Rmt
120 | 32 a | Supply, Transportation and Installation of 150mm x 50mm x 2mm thick hot dip GI perforated cable tray | 200 | Rmt
Supply, Transportation and Installation of 300mm x 50mm x 2mm thick thick hot dip GI perforated cable
121 | 32 b | tray | 100 | Rmt
122 | 33 a | Supply, Transportation and installation of 10KVA / 312V DC on line UPS system | 7 | Nos
123 | 33 b | Supply and fixing of 12V, 150 AH MF battery | 182 | Nos
124 | 33 c | Supply and providing of UPS cum battery rack 20 | 7 | Nos
batteries
Supply, Transportation, Installation, Testing and commissioning of storage / Pressure type 5 Star rated water heater with ABS plastic body of 15 Ltrs
125 | 33 d |  | 7 | Nos
26 persons ICU bed cum passenger lift (1768 Kgs) G+8 Floors, 9 stops,9 Openings (Cost Includes amount for Construction of Shaft / Cladding from Ground to 8th
126 | 34 | Floor) | 1 | Nos