## Sheet1
S.No | Desciption | Quantity | Units
1 | Modular Double skin floor mounted EUROVENT Certified Air Handling Unit 3000CFM / 8.5 TR / 150mm SP made out of 45 plus or minus 2mm thick PUF insulated panels Thermal break aluminium profile frame work with 0.8mm thick pre painted / powder coated inner and outer skins comprising of mixing box with fresh air and return air dampers, pre filters with 10 and 5 microns combination filters in single frame, Interlaced/Intertwined DX Cooling Coil suitable for connecting 2 nos of 8.5TR capacity 1W plus 1S out door condensing units, SS304 drain pan with, blower section with Nicotra / Kruger make direct drive/ Plug type fan, vibration isolators, EFF1 motor and blower section with on/off switches to operate from outside, limit switch for the fan section access door with a view port, fine filter section with 3 microns filters inspection doors for all filter and fan sections and damper at the outlet of unit. Ports for differential pressure gauges across all filters and blower to measure differential pressure. AHU Make : VTS / Systemair/ Edgetech/ Zeco/Waves; Make - Blower - Nicotra / Kruger; Motor - Crompton Greaves / Siemens; Filter - Thermodyne / Freudenberg / Ultrafil/ AAF/ Camfil/ Usha /Matchmark at MGM Warangal | 1 | No
2 | SITC of filter module made out of heavy duty Aluminium powder coated extrusion with minimum of 13G . and to house 610 mm X 610 mm HEPA Filter at the rate 0.3 microns , 99.9997, H-14 Grade, Filter loading from clean room side with bewel gear arrangement damper with access from clean room suitable to house the following filter sizes pressure drop and Integrity testing ports into room. Includes SS capsule perforated diffuser. This includes all required supports and accessories etc. Capacity 1000 CFM. at MGM Warangal | 6 | No
3 | SITC of air cooled condensing units with two scroll compressors, air cooled condenser, power panel, vibration isolating pads, stand for ODU, thermostat, etc. of the following capacities. The nominal capacity of the condensing unit shall be as under. Air cooled condensing unit shall have horizontal discharge. All refrigerant piping accessories sight glass, drier, expansion valve, etc. shall be supplied with the condensing units and suitable to connect above AHUs. Refrigerant shall be R 407C / R 410A. Necessary thermostat, control wiring, etc. shall be included. Derating of the unit shall not be more than 15percentage under 45 deg. C ambient temperature. Condensing unit shall be capable of operating up 50 deg. C ambient temperature. 8.5 TR capacity at MGM Warangal | 1 | No
4 | SITC of Flange type, Flame proof FLP duct heaters of 5 kW capacity with Mineral Filled AISI SS304/SS321 Sheathed Tubular Heater with GI Helical fins, Tube dia 8.2mm min and Helical Finn dia 25mm min, enclosed in the frame, FLP Terminal box etc., Nickel Chromium Inner Element, Silicon Sealing to Restrict Moisture pickup, Silver brazed mounting plate etc., and heaters shall be controlled with PID thyrestor controller based on the analog output signal of 0-10 V DC of controller . And this should have saftey thermostat and cutouts and air stat etc. all safety controls. The capacities as follows and sizes of the heaters shall be as per the duct sizes and approved drawing. at MGM Warangal | 1 | No
5 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Liquid Line at MGM Warangal | 20 | Rmt
6 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Suction Line at MGM Warangal | 20 | Rmt
7 | SITC of CPVC drain ping with supports, clamps and 9 mm thk. Nitrile rubber tube insulation of the following sizes. Insulation shall have factory laminated glass cloth. 32mm Dia at MGM Warangal | 50 | Rmt
8 | SITC of CPVC drain ping with supports, clamps and 9 mm thk. Nitrile rubber tube insulation of the following sizes. Insulation shall have factory laminated glass cloth. 25mm Dia at MGM Warangal | 50 | Rmt
9 | SITC of Factory fabricated and boxed ducting using Aluminium Sheets / coils, should be fabricated as per SMACNA, galvanised hardware and supports, silicon sealant at all longitudinal joints, Galvanized /GI Electroplated iron angle flanges for all the joints, bracing angles and minimum 5mm thick neoprene rubber gasket.- Duct pressure testing at 75mm to be carried out before insulatiting the duct. pressure testing to be done as per SMACNA. Procedure to be approved by consultant. 20G - 1.0 mm Thick at MGM Warangal | 30 | Sqm
10 | SITC of Factory fabricated and boxed ducting using Aluminium Sheets / coils, should be fabricated as per SMACNA, galvanised hardware and supports, silicon sealant at all longitudinal joints, Galvanized /GI Electroplated iron angle flanges for all the joints, bracing angles and minimum 5mm thick neoprene rubber gasket.- Duct pressure testing at 75mm to be carried out before insulatiting the duct. pressure testing to be done as per SMACNA. Procedure to be approved by consultant. 22G - 0.8 mm Thick at MGM Warangal | 250 | Sqm
11 | Aluminium low leakage aerofoil design volume control dampers Suitable for manual and motorised operation at MGM Warangal | 2 | Sqm
12 | CBRI approved 16G GI Spring return actuated fire dampers rated for 90 minutes with limit switch. at MGM Warangal | 2 | Sqm
13 | SITC of SS perforated return raiser grilles with 10 microns filters with collar dampers at MGM Warangal | 2 | Sqm
14 | Extruded Al. powder coated EXHAUST / RETURN discrete grilles at MGM Warangal | 1 | Sqm
15 | SITC of Collar Dampers made of Al. extrusions with black powder coating for Grilles / Diffusers at MGM Warangal | 1 | Sqm
16 | SITC of Magnehelic gauges across pre and fine filter at AHUs including mounting arrangement, SS nozzles, food grade PVC tubing, etc. at MGM Warangal | 2 | No
17 | SITC of Magnehelic gauges to measure the room differential pressures in operation theatres with SS mounting box, SS nozzles, food grade PVC tubing, etc. at MGM Warangal | 2 | No
18 | SITC of Aluminium powder coated Fresh air and Exhaust Louvers of non- vision type with nylon mosquito net etc. at MGM Warangal | 1 | Sqm
19 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 32mm Thick for Exposed Supply Air duct and finished with UV Protective Paint. at MGM Warangal | 130 | Sqm
20 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Exposed Return Air Duct and finished with UV Protective Paint.at MGM Warangal | 40 | Sqm
21 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Supply air duct running inside the building. at MGM Warangal | 40 | Sqm
22 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 19mm Thick for Return air running inside the building. at MGM Warangal |  | Sqm