## BOD
BASE OF DESIGN DESCRIPTION
Project: GANDHI HOSPITAL IVF CENTRE ON FIFTH FLOOR
Make: Daikin VRV System
S.No. | Location | LENGTH(MM) | WIDTH(MM) | AREA(Sqft) | REQUIRED TR | DAIKIN STANDARD | Qty | Unit Type | Total TR
FIFTH FLOOR
1 | UPS ROOM | 2100 | 2745 | 62.0486 | 0.68943 | 0.83 | 1 | HI-WALL | 0.83
2 | COUNSELLING ROOM-1 | 2452 | 3242 | 85.5665 | 0.71305 | 1.04 | 1 | HI-WALL | 1.04
3 | COUNSELLING ROOM-2 | 2452 | 3242 | 85.5665 | 0.71305 | 1.04 | 1 | HI-WALL | 1.04
4 | ULTRASOUND | 2180 | 4505 | 105.7113 | 1.1746 | 1.65 | 1 | HI-WALL | 1.65
5 | PRE/POST OP | 6815 | 6600 | 484.1501 | 4.0346 | 3.31 | 1 | 4-WAY CASSETTE | 3.31
6 | SPERM COLLECTION ROOM | 2365 | 3300 | 84.007 | 0.70006 | 1.04 | 1 | HI-WALL | 1.04
7 | BLOOD COLLECTION & INJECTION ROOM | 2582 | 3300 | 91.715 | 0.76429 | 1.04 | 1 | HI-WALL | 1.04
8 | ANDROLOGY LAB | 4085 | 4249 | 186.831 | 1.5569 | 1.65 | 1 | HI-WALL | 1.65
9 | CROY ROOM | 3000 | 1600 | 51.6668 | 0.43056 | 0.83 | 1 | HI-WALL | 0.83
10 | OT-2 | 4200 | 6485 | 293.1768 | 2.4431 | 1.65 | 2 | HI-WALL | 3.3
[7 empty] | 11 |  | 15.73
[8 empty] | IDU HP | 18.9518
[8 empty] | ODU HP | 16
[8 empty] | DIVERSITY% | 118.4%
DAIKIN DX UNIT
1 | UPS ROOM | 2100 | 2745 | 62.0486 | 0.68943 | 1 | 1 | HI-WALL | 1
2 | ANDROLOGY LAB | 4085 | 4249 | 186.831 | 1.5569 | 1.5 | 1 | HI-WALL | 1.5
2

## HIGH SIDE
Quotation For Daikin VRV System
As World's No.1 Airconditioning Company, we are committed to delivering airconditioning solutions that enhance the quality of life all around the world. We are creating value through innovative technologies. As a Global Industry frontrunner, we are carrying out Research and Development on the world's most advanced airconditioning technology.
ANNEXURE I
HIGH SIDE WORK
S.No. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
Supply of Variable Refrigerent Volume Outdoor units with inverter technology scroll compressor , low noise propellor type aero spiral fan, Condenser coil with special acrylic pretreatment for improved resistance to salt corrosion,refrigerant shut off valves,safety devices, lead free PC boards suitable for operation on R410a and on 380 - 415 V, 50 Hz, 3 phase A/C supply etc. as per standards
Make: DAIKIN (Cooling Model)
1 | Supply of Variable Refrigerant Volume Outdoor units
a | 16 HP (Model: RXQ16ARY6) TOP DISCHARGE | No's | 1 | 276208 | 276208
b | DGT JOINT | No's | 1 | 6500 | 6500
2 | Supply of 4-Way Cassette ACs with Wirless Remotes
a | 3.31 TR (Model: FXFSQ100ARV16) | No's | 1 | 46329.5 | 46329.5
3 | Supply of Hi-Wall ACs with Wirless Remotes
a | 1.65 TR (MODEL NO: FXAQ50ARVE6) | No's | 5 | 27084 | 135420
b | 1.04 TR (MODEL NO: FXAQ32ARVE6) | No's | 4 | 24827 | 99308
c | 0.83 TR (MODEL NO: FXAQ25ARVE6) | No's | 1 | 24461 | 24461
| Total no.of IDU |  | 11
4 | Supply of Refnet Joints | Nos | 10 | 2500 | 25000
DX UNIT
1 | Supply of High Wall 5 Star Inverter AC, Single Phase
a | 1.5 TR (MODEL NO: FTKM50UV16U) | Nos | 2 | 36507.8125 | 73015.625
TOTAL HIGH SIDE EQUIPMENT VALUE |  |  |  |  | 686242.125
GST ON SUPPLY @28 % |  |  |  |  | 192147.795
TOTAL EQUIPMENT VALUE WITH TAX |  |  |  |  | 878389.92

## LOWSIDE
ANNEXURE II
LOW SIDE JOB
S.N. | DESCRIPTION | UNIT | QTY | Rate |  | Amount
|  |  |  | Supply | Instl. | Supply | Instl. | Remarks
1 | Lifiting ,Shifting,Positioning and Installation of Outdoor units | No's | 1 |  | 7500 |  | 7500
2 | Lifiting, Shifting, Positioning of VRV Indoor Units.
a | Cassette unit | No's | 1 |  | 3000 |  | 3000
b | Hi-Wall unit | No's | 10 |  | 2000 |  | 20000
3 | Supply & Installation of copper refrigerant piping duly insulated with nitrile insulation of 19mm thickness for Gas Pipe and 13mm thickness for Liquid Pipe / Including supports Clamps etc and incl bends, couplings and necessary fittings, for R 410 A Site Pressure tested to 550 psi. | Rmt | 190 | 1410 | 160 | 267900 | 30400 | Qty consider as per site measurments
4 | Pressure testing with nitrogen Gas, Vaccumising Including all consumables for all systems. Gas charging and commissioning R-410A. (16HP) | LOT | 1 | 30800 | 13200 | 30800 | 13200
5 | Supply and Installation of control cum transmission wiring of size 3C x 1.5 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing and accessories. | Rmt | 165 | 160 | 50 | 26400 | 8250
6 | Supply and Installation of cabling of size 2C x 1 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing and accessories as per the approved routing. At Gandhi Hospital | Rmt | 120 | 160 | 50 | 19200 | 6000 | Qty consider as per site measurments
7 | PVC insulated piping for condensate drain
a | 25/32 mm Dia | Rmt | 70 | 210 | 60 | 14700 | 4200 | Qty consider as per site measurments
b | 40 mm | Rmt | 20 | 240 | 60 | 4800 | 1200
8 | Refnet Joints | Nos | 10 |  | 500 |  | 5000
9 | ODU stands | Nos | 1 | 7000 | 500 | 7000 | 500
DX SYSTEM
1 | Installation & Commissioning
a | Split AC | Nos | 2 |  | 2000 |  | 4000
2 | Condenser stand
a | Split AC | Nos | 2 | 950 | 200 | 1900 | 400
BASIC VALUE | [5 empty] | 372700 | 103650
GST @18% | [5 empty] | 67086 | 18657
TOTAL LOW SIDE VALUE WITH TAX | [5 empty] | 562093
Note : The actual quantities will be Variable as per site actual measurements (final bill as per actual measurments) only.

## SUMMARY
Daikin VRV BOQ
PROJECT: GANDHI HOSPITAL IVF CENTRE ON FIFTH FLOOR
Date: 03-08-2023
| TOTAL HIGH SIDE EQUIPEMENT VALUE | 878389.92
| TOTAL LOW SIDE INSTALLATION VALUE | 562093
| TOTAL PROJECT CONTRACT VALUE | 1440482.92
Note : The actual quantities will be Variable as per site actual measurements only.
Note : Delivery lead time wthin 4 to 6 week after advance payment.
TERMS AND CONDITIONS:
01) Payment terms for high side is 100% advance along with the order.
02) Delivery: As per site requirement
03) Civil works, False Ceiling work will not comes in our scope.
04) Validity of this quote is up to 15 Days only.
05) If requirement of extra material at site will charge extra at actual.
06) Low side payment 50% advance along with work order,30% indoor,out door units instalation,
20% after VRV commissioning
07) Core Cutting, Chipping, Civil works and Scuffolding are in customer's scope only
We hope the above is in line with your requirement & incase you need any further clarification,
kindly do revert back to us.
08) Drain Pump for Split ac charges extra If required.
Very truly yours
For. COMFORT COOL SYSTEMS
Managing Directors
Mr.Govind Gupta & M.Suresh
Ph: 9885456671, 9885456672.