## Sheet1
Comfort Cool Systems
1-1-379/82, SRT-125, Jawahar Nagar
RTC X Roads, Hyderabad - 500020
Mob. 98854 56671, Email - ccs.daikin@gmail.com
DATE: 29-07-2023
|  |  |  | SUPPLY |  | INSTALL |  | REMARKS
S.No | Description of Item | Quantity | UNIT | RATE | AMOUNT | RATE | AMOUNT
1 | Condensing units - VRF/VRV System : Supply, Installation, Nitrogen testing , Vacuuming and Commissioning of air cooled variable refrigerant flow modular type condensing units, each comprising of multiple scroll compressors all inverter driven, full charge of refrigerant gas R-410a including additional gas filling , lubricating oil and all accessories as per the specifications. The condensing units shall be suitable to work on cooling mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B . The COP of the system shall be greater than 4 under ARI conditions for 100percentage load . The condensing units shall be suitable for operation on 415 plus or minus 10percentage volts, 50Hz, 3 phase AC power supply and , outdoor units to be mounted on MS platform with suitable Vibration Isolation pads to avoid vibrations. All the supports and angle base frame structure to be duly black painted with synthetic epoxy paint. the condensing units shall be of following capacities: The VRF ODU should be capable of working with total capacity of connected indoor units ranging between 100percentage to 140percentage of ODU capacity . COP minimum 3.5. Make : Daikin / LG / O General / Toshiba at MGM Warangal 14 HP AFTER DEERATION 18 HP (MODEL NO: RXQ18ARY6) NOTE: PRICE INCLUDE NITROGEN TESTING, VACCUMISING AND COMMISSIONINGOF VRV UNIT SYSTEM & ODU STAND, DGT JOINT FOR ODU | 1 | Nos | 348110 | 348110 | 71400 | 71400
2 | VRF Indoor Units : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 0.83 TR at MGM Warangal MODEL NO: FXAQ25ARVE6 | 2 | Nos | 26065 | 52130 | 2800 | 5600
3 | VRF Indoor Units : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.04 TR at MGM Warangal MODEL NO: FXAQ32ARVE6 | 2 | Nos | 28490 | 56980 | 2800 | 5600
4 | VRF Indoor Units : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.32 TR at MGM Warangal MODEL NO: FXAQ40ARVE6 | 2 | Nos | 26455 | 52910 | 2800 | 5600
5 | VRF Indoor Units : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.65 TR at MGM Warangal MODEL NO: FXAQ50ARVE6 | 4 | Nos | 29770 | 119080 | 2800 | 11200
6 | Cassette Units : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling mode.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 3.31TR – 4 way at MGM Warangal (MODEL NO: FXFSQ100ARV16) | 1 | Nos | 49368 | 49368 | 3800 | 3800
7 | Supply, Installation, Testing and Commissioning of Hard copper REFRIGERANT PIPING of 16swg various sizes with necessary supports, fittings, interconnecting the liquid and suction lines between the aircooled outdoor units and the indoor units. The piping shall be carried out of Hard drawn copper pipes of type K with soldered / brazed socket fittings. Isolating valves shall be provided to isolate each compressor, strainers, sight glass and any other component requiring proper operation and maintenance. Both the suction and liquid lines shall be insulated with 19mm thick closed cell insulation for above 25mm dia , 13mm thick for pipes below 25mm dia . The insulation finished with treated woven glass fiber reinforced covering for inside Piping and including making required holes in the wall and re finishing and water tight of holes after laying holes as per the specifications and approved drawings at MGM Warangal | 160 | Rmt | 1550 | 248000 | 180 | 28800 | IT CANNOT BE GIVEN IN LOT . WE CONSIDERED IT IN RMT
8 | Supply, Installation , Testing and Commissioning of Refnet joints to be provided in refrigerant pipe line. Material of construction for fittings shall be similar to refrigerant piping. at MGM Warangal | 10 | Nos | 2900 | 29000 | 500 | 5000
9 | Supply and Installation of control cum transmission wiring of size 3C x 1.5 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing and accessories as at MGM Warangal | 150 | Rmt | 190 | 28500 | 80 | 12000
10 | Supply and Installation of cabling of size 2C x 1 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing and accessories as per the approved routing. at MGM Warangal | 100 | Rmt | 180 | 18000 | 80 | 8000
11 | PVC insulated piping for condensate drain
a | 25/32 mm Dia | 70 | RMT | 240 | 16800 | 80 | 5600
b | 40 mm Dia | 20 | RMT | 260 | 5200 | 80 | 1600
BASIC VALUE |  |  |  |  | 1024078 |  | 164200
NOTE: GST WILL EXTRA FOR HIGH SIDE 28% & LOWSIDE 18%
NON TENDERED ITEM NOT IN OUR SCOPE
THIS OFFER VALIDITY ONLY FOR 10 DAYS
Note : Delivery lead time wthin 4 to 6 week after advance payment.
Note : The actual quantities will be Variable as per site actual measurements (final bill as per actual measurments) only.
TERMS AND CONDITIONS:
01) Payment terms for high side is 100% advance along with the order.
02) Delivery: As per site requirement (minimun 30 to 45 days after PO)
03) Civil works, False Ceiling work will not comes in our scope.
04) Validity of this quote is up to 15 Days only.
05) If requirement of extra material at site will charge extra at actual.
06) Low side payment 50% advance along with work order,30% indoor,out door units instalation,
20% after VRV commissioning
07) Core Cutting, Chipping, Electrical work,Civil works and Scuffolding are in customer's scope only
We hope the above is in line with your requirement & incase you need any further clarification,
kindly do revert back to us.
08) Drain Pump for Split ac charges extra If required.
Very truly yours
For. COMFORT COOL SYSTEMS
Managing Directors
Mr.Govind Gupta & M.Suresh
Ph: 9885456671, 9885456672.