## Civ-Det-CP
TELANGANA STATE MEDICAL SEVICES & INFRASTRUCTURE DEVELOPMENT CORPORATION
Name of the work | : | Design, Fabriction, establishing and commissioning of In - Vitro ferility centers (IVFC) alongwith allied Services on Turnkey basis at Gandhi hospital secunderabad.
Name of the Agency | : | M/s. Asta vardhman Consortium
Ref.Admn Sanction | : | G.o.Rt.100, dt.22.02.2023 of HM & FW Dept.
Agreement No | : | 344/A/TSMIDC/Spl.Proj/IVFCs/2022-23,Dt.05.07.2023
Division | : | EE/TSMSIDC Division/HYDERABAD.
Sub - Division | : | Dy.EE/TSMSIDC/Hyderabad Sub Division.
" RA-05-DETAILED " MB NO: 09
Issued to Dy.EE, RR Sub-Divn-I on____________
Name of the work | : | Design, Fabriction, establishing and commissioning of In - Vitro ferility centers (IVFC) alongwith allied Services on Turnkey basis at Gandhi hospital secunderabad.
Name of the Agency | : | M/s. Asta vardhman Consortium
Ref.Admn Sanction | : | G.o.Rt.100, dt.22.02.2023 of HM & FW Dept.
Agreement No | : | 344/A/TSMIDC/Spl.Proj/IVFCs/2022-23,Dt.05.07.2023
Division | : | EE/TSMSIDC Division/HYDERABAD.
Sub - Division | : | Dy.EE/TSMSIDC/R.R.Sub Division-I.
" RA-05-DETAILED " MB NO: 09

## Abs-4
ABSTRACT
| Name of the work:Design, Fabriction, establishing and commissioning of In - Vitro ferility centers (IVFC) alongwith allied Services on Turnkey basis at Gandhi hospital secunderabad. | [6 empty] | Agency: M/s. Asta Vardhman Consortium | [5 empty] | Agt.No: 344/A/TSMIDC/Spl.Proj/IVFCs/2022-23,Dt.05.07.2023
S.No | Discription Of Work etc., | Measurements Upto date | [6 empty] | Per | Total Volume |  | Deduct/previous Measurements |  | Since last measurement |  |  | Remarks
|  | No | L | B | D | Content | Rs | Ps. |  | Rs. | Ps | P.No. | Qty. | Qty | Value
[15 empty] | Rs. | Ps.
49 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete (Brick Masonary)
(Brick Masonary)
| V.P 01 ABNO 02 |  |  |  |  | 31.21 | 398 | Cum | 12422 |  |  | 31.21 | 12422 | 0
Old Cement Morter
| V.P 01 ABNO 02 |  |  |  |  | 37.13 | 8 | Sqm | 297 |  |  | 37.13 | 297 | 0
Unreinforcement Cement More Than 15cm
| V.P 01 ABNO 02 |  |  |  |  | 3.89 | 2842 | Cum | 11055 |  |  | 3.89 | 11055 | 0
Reinforcement Cement
| V.P 01 ABNO 02 |  |  |  |  | 0.7 | 3115 | Cum | 2181 |  |  | 0.7 | 2181 | 0
51 | Dismantling doors, windows and clear storey windows, Ventilators etc., (wood or steel) shutters including Chowkhats, architraves,hold fasts and other attachments etc., and stacking them within 100m lead including labour charge etc., and overheads & contractors profit complete for finished item of work.
| V.P 01 ABNO 02 |  |  |  |  | 5 | 468 | Each | 2340 |  |  | 5 | 2340 | 0
[5 empty] | AE | 2 | 374 | Each | 748 |  |  | 2 | 748 | 0
53 | Masonry work in CM (1:8) prop (cement: Screened sand) in super structure with / lime solid blocks of size 290mmx225mmx140mm from approved source having minimum crushing strength of 50 Kg/Sqcm including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, including sales & other taxes on all materials, all operational, incidental and labour charges such as mixing cement mortar, constructing masonry, scaffolding charges, lift charges, curing, etc., complete but excluding seigniorage charges for finished item of work. (APSS No. 501 & 504).
| V.P 01 ABNO 02 |  |  |  |  | 9.03 | 16055 | Cum | 144977 |  |  | 9.03 | 144977 | 0
54 | Reinforced brick Masonry for Partition Walls (11.0 cm thick) in CM (1:4) prop (cement: Screened sand) in super structure with / lime solid blocks of size 290mmx225mmx140mm from approved source having minimum crushing strength of 50 Kg/Sqcm including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, including sales & other taxes on all materials, all operational, incidental and labour charges such as mixing cement mortar, constructing masonry, scaffolding charges, lift charges, curing, etc., complete but excluding seigniorage charges for finished item of work. (APSS No. 501 & 504).
| V.P 01 ABNO 02 |  |  |  |  | 191.0305 | 1952 | Sqm | 372892 |  |  | 191.0305 | 372892 | 0
55 | Providing Thermo Mechanically Treated ( TMT) ( Fe-500/500D/550D from primery producer TATA, SAIL, VSP, JSW Steel, Goel steel, Jindal panther, X- Vega & balaji Shakthi as per IS 1786-2008) of Different Diameters RCC Works , including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and sizes and typing and lap - spacing with binding wire of 18 SWG, Forming grills for reinforcement work as per approved design and drawings, including and conveyanace of steel bars, including all wastages such as overlaps, coupling, chairs, spacer bars including cost and conveyance of binding wire cover blocks and incidential, operational, labour charges such as cutting bending, placing in position, typing incliding sales and other taxes on all materials etc., and overheads & contractors profit completefor finished item of work
| V.P 02 AB NO 02 |  |  |  |  | 0.103 | 116500 | MT | 12000 |  |  | 0.103 | 12000 | 0
Sup | Supply and placing of the Design Mix Concrete M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Weight Batcher / Concrete mixer with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials, centering using Casurina Ballies, Bamboos, Wooden Reapers, Runners, Wood Posts, Steel Plates etc., including all operational, incidental and labour charges such as weigh batching, machine mixing, lifting of concrete manually, laying concrete, curing , overheads & contractors profit etc., complete but excluding cost of steel and its fabrication charges for finished item of work (APSS No. 402) (For Lintels)
| V.P 02 AB NO 02 |  |  |  |  | 0.43 | 12775 | Cum | 5493 |  |  | 0.43 | 5493 | 0
56 | Plastering 12mm thick in two coats using screened sand with base coat of 8mm thick in CM (1:6) and top coat of 4mm thick in CM (1:4) with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales & other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and overheads & contractors profit complete for finished item of work. (SS 901,903 & 904).
| V.P 02 AB NO 02 |  |  |  |  | 536.1091 | 1041 | Sqm | 558090 |  |  | 536.1091 | 558090 | 0 |  |  |  | 22295.5
Sup | Flooring with 16 to 18 mm thick high polished granite stone slabs black colour as approved by the Engineer-in-Charge of length not less than 2.43 mts set over base coat of cement mortar (1:8) , 20mm thick using screened sand over CC bed already laid or RCC roof slab including neat grey cement slurry of honey like consistency spread @ 3.3 Kg per sqm and jointed neatly with white cement paste mixed with pigment of matching shade to full depth including cost and conveyance of all materials like cement , sand , water , granite slabs etc., to work site and all operational, incidental labour & lift charges, half rounding the edge , polishing charges and all other taxes on all materials, cost of base coat and overheads & contractors profit complete for finished item of work for platforms (S.S.701 & special) | [16 empty] | 22295.5
| V.P 02 AB NO 02 |  |  |  |  | 10.166 | 6300 | Sqm | 64071 |  |  | 10.166 | 64071 | 0
65 | Flooring with soluble salt porcelain vitrified tiles screen printed and polished of size 600 x 600 mm and thickness between 8 to 10mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630Parts 1 to 15 of any colour and finish in all shades and designs with borders and design as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM 1:8 prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread at the rate 3.3 kgs per Sqm. and jointed neatly with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site excluding cost of C.C. bed including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in- charge etc., and complete for finished item of work. TSSS No.701 and 707. 5th Floor at Gandhi Hospital
| V.P 02 AB NO 02 |  |  |  |  | 225 | 1725 | Sqm | 388125 |  |  | 225 | 388125 | 0
[6 empty] | 149.81 | 1380 | Sqm | 206738 |  |  | 149.81 | 206738 | 0
66 | Flooring with non-skid full body ceramic floor tiles of size 300mm x 300mm and thickness between 7 - 8mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630 Part 1 to 15 of any colour and finish in all shades and designs as approved by Engineer-in-charge, set over base coat of cement mortar 1:8, 12mm thick using screened sand over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread at the rate 3.3 Kgs per Sqm and jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, screened sand , water and tiles etc., complete for finished item of work. TSSS No.701 and 707 at Gandhi Hospital
| V.P 02 AB NO 02 |  |  |  |  | 14.618 | 1525 | Sqm | 22296 |  |  | 14.618 | 22296 | 0
68 | Providing dadooing to walls with glazed full body porcelain wall tiles of size 300 x 600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. 5th Floor at Gandhi Hospital
| V.P 02 AB NO 02 |  |  |  |  | 40 | 1423 | Sqm | 56920 |  |  | 40 | 56920 | 0
[6 empty] | 63.766 | 1138 | Sqm | 72566 |  |  | 63.766 | 72566 | 0
Sup | Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707)
| V.P 02 AB NO 02 |  |  |  |  | 107.179 | 114 | Rmt | 12219 |  |  | 107.179 | 12219 | 0
Electrical-1
96 | Supply and Fixing of 25mm outer dia medium grade, FRLS with IS:9537 part 3 rigid PVC pipe Concealed in with all required PVC/ Metalic junction boxes a including masonary work and labour charges etc., complete Makes:- Sudhakar / Modi
[6 empty] | 184.1 | 116 | Rmt | 21356 |  |  | 184.1 | 21356 | 0
97 | Supply and Fixing of 25mm outer dia medium grade, FRLS with IS:9537 part 3 rigid PVC pipe with all accessories fixing on wall / ceiling with chromium plated metallic base saddles including all labour charges etc., complete Makes:- Modi
| V.P 07 AB NO 02 |  |  |  |  | 500 | 107 | Rmt | 53500 |  |  | 500 | 53500 | 0
[5 empty] | AE | 560.2 | 86 | Rmt | 48177 |  |  | 560.2 | 48177 | 0
98 | Wiring with run of 2 of 22/0.3mm (1.5 Sqmm) FRLS / HFFR PVC insulated flexible ISI mark copper cable in existing PVC conduit pipe including Supply and fixing of Jumbo Ceiling rose and 6A/10A ISI Mark 1way Modular switch with required modular box and cover frame in existing Surface or Concealed pipe wiring including cost and conveyance of all material and all labour charges etc., complete for light, Fan, Exhaust fan and bell points in N.R.B. Makes of wires : Polycab (HFFR) Makes of switches :Honeywell Blenge Plus
| V.P 09 AB NO 02 |  |  |  |  | 110 | 945 | No | 103950 |  |  | 110 | 103950 | 0
[5 empty] | AE | 9 | 756 | No | 6804 |  |  | 9 | 6804 | 0
99 | Supply and fixing of 6A/10A ISI Mark 3/2 pin Modular socket with 6A/10A 1way Modular switch, 3 Module box with cover frame a Common switch board including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B. Makes of switches : Honeywell Blenge Plus
| V.P 11 AB NO 02 |  |  |  |  | 12 | 675 | No | 8100 |  |  | 12 | 8100 | 0
[5 empty] | AE | 18 | 540 | No | 9720 |  |  | 18 | 9720 | 0
100 | Supply and fixing of 16A switches - 1Nos and 6/16A 2 in one socket - 1Nos Modular type with cover plate and GI switch box fixing on separate board including all labour charges etc., complete. Makes of switches: - Hooney well Benzplus
| V.P 11 AB NO 02 |  |  |  |  | 14 | 1040 | No | 14560 |  |  | 14 | 14560 | 0
101 | Supply & fixing of 16A/6A, 2 in one socket - 2 Nos with 16A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benzplus
| V.P 12 AB NO 02 |  |  |  |  | 34 | 1755 | No | 59670 |  |  | 34 | 59670 | 0
104 | Supply and Run of 3 of 36/0.3mm (2.50 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
| V.P 14 AB NO 02 |  |  |  |  | 540.7 | 177 | Rmt | 95704 |  |  | 540.7 | 95704 | 0
105 | Supply and Run of 3 of 56/0.3mm (4.00 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
| V.P 18 AB NO 02 |  |  |  |  | 1170.8 | 255 | Rmt | 298554 |  |  | 1170.8 | 298554 | 0
106 | Supply and Run of 5 of 90/0.3mm (6.0 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
| V.P 18 AB NO 02 |  |  |  |  | 60 | 606 | Rmt | 36360 |  |  | 60 | 36360 | 0
[5 empty] | AE | 183.3 | 485 | Rmt | 88901 |  |  | 183.3 | 88901 | 0
107 | Supply & run of 5 of 10.0 Sqmm (140/0.3 mm) (3 phases, neutral and earth) FRLS / HFFR PVC insulated flexible copper cable in the existing conduit pipe for run of mains from Power panel board to TPN DB"s with pin type lugs and connections etc., complete. [for PDBs] Makes of wires: Polycab
| V.P 18 AB NO 02 |  |  |  |  | 40 | 967 | Rmt | 38680 |  |  | 40 | 38680 | 0
[6 empty] | 105.1 | 774 | Rmt | 81347 |  |  | 105.1 | 81347 | 0
109 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand and Supply and Fixing of 1 No., of 40A FP 30mA RCCB as incomer and 12 Nos 6-32 A 10kA SP MCBs Makes: Legrand-DX3 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. (For Lighting DBs) Make Legrand
| V.P 19 AB NO 02 |  |  |  |  | 3 | 18325 | No | 54975 |  |  | 3 | 54975 | 0
[6 empty] | 5 | 14660 | No | 73300 |  |  | 5 | 73300 | 0
110 | Supply and fixing of 8 Way VTPN DB with IP 43 Protection as per IS:13032 with 1 No., of 125A 4P MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted as incomer with 8 Nos of 63A, 10KA, TP MCBs C Curve ISI Mark as Out goings including internal connections and labour charges for FLUSH Mounting etc., complete. Makes : Legrand / Schneider
| V.P 19 AB NO 02 |  |  |  |  | 1 | 28460 | No | 28460 |  |  | 1 | 28460 | 0
114 | Supply, transportation and fixing of 24W edge lit LED Down light Square Housing Made of Aluminium alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser Square with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor > 0.9, Surge protection: > 2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI >80, and THD is less than 15% etc., with BIS Certification. Makes: Crompton
| V.P 20 AB NO 02 |  |  |  |  | 44 | 2652 | No | 116688 |  |  | 44 | 116688 | 0
115 | Supply and Transportation 36W Edge lit, 2' x2' (600mm x600mm) slim panel LED luminaire Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% etc., complete. Makes: Crompton
| V.P 21 AB NO 02 |  |  |  |  | 30 | 4350 | No | 130500 |  |  | 30 | 130500 | 0
[5 empty] | AE | 10 | 3480 | No | 34800 |  |  | 10 | 34800 | 0
119 | Supply and fixing of Modular type Stepped electronic regulator Makes : GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/ Cabtree Verna/ Million logus / Gold Medal Curve for sweep AC ceiling fans of 1200mm / 1400mm complete with connections.
| V.P 22 AB NO 02 |  |  |  |  | 12 | 827 | No | 9924 |  |  | 12 | 9924 | 0
[5 empty] | AE | 2 | 662 | No | 1324 |  |  | 2 | 1324 | 0
122 | SITC of Hot dip galvanized perforated cable tray of 300 mm Wide sizes for to run the cable from Floor Panel to Lab Panel & electrical room to AC panel and AC panel to Units. All necessary supports & accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. ( Elec 4.10.1 d)
| V.P 23 AB NO 02 |  |  |  |  | 80 | 1310 | Rmt | 104800 |  |  | 80 | 104800 | 0
[5 empty] | AE | 5.4 | 1048 | Rmt | 5659 |  |  | 5.4 | 5659 | 0
128 | Supply & installation of 50x6 GI flat for body earthing of electrical panel & AC Panel which is laid in 300mm cable tray
| V.P 24 AB NO 02 |  |  |  |  | 184.9 | 329 | Rmt | 60832 |  |  | 184.9 | 60832 | 0
129 | Supply & installation of 25x3 GI flat for body earthing of DBs & Cable tray which is laid in 100mm cable tray
| V.P 25 AB NO 02 |  |  |  |  | 100 | 163 | Rmt | 16300 |  |  | 100 | 16300 | 0
[5 empty] | AE | 16.3 | 130 | Rmt | 2119 |  |  | 16.3 | 2119 | 0
131 | Supply & installation of 4 sqmm Copper wire for Earthing of DBs Equipment
| V.P 25 AB NO 02 |  |  |  |  | 80 | 83 | Rmt | 6640 |  |  | 80 | 6640 | 0
[5 empty] | AE | 206 | 66 | Rmt | 13596 |  |  | 206 | 13596 | 0
132 | Supply, Lying & testing of 3.5Cx95 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/ Glostar/ Finolex Make of gland & Lungs: HMI/ Commet /Dowell’s
| V.P 25 AB NO 02 |  |  |  |  | 83 | 1207 | Rmt | 100181 |  |  | 83 | 100181 | 0
133 | Supply, Lying & testing of 3.5CX50 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/ Universal/ Glostar/ Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
| V.P 26 AB NO 02 |  |  |  |  | 40 | 722 | Rmt | 28880 |  |  | 40 | 28880 | 0
149 | Split AC unit 1.5 TR inverter type 3 Star capable of delivering 18000 BTU/hr and above with high wall mounted indoor unit and outdoor condensing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord , built-in stabilizer Voltage range 160- 264 volts and cordless remote control. Makes : Daikin / Thoshiba / O General at Gandhi Hospital
| V.P 01 MB No 03 |  |  |  |  | 2 | 43200 | Nos | 86400 |  |  | 2 | 86400 |  |  |  | 90%
124 | Batteries : Supply and fixing of 12V 65 AH SMF battery including wire leads. Makes: Quanta / Racket / Exide. At Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 32 | 18526 | Nos | 592832 |  |  | 32 | 592832 |  |  |  | 90%
125 | Supply and providing of UPS com Batteri rack for 20 batteries . At Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 6088 | Nos | 6088 |  |  | 1 | 6088 |  |  |  | 90%
123 | 20 KVA UPS: Supply and installation of 20KVA 3ph in and 3ph out on line UPS system IGBT based rectifier with input power factor correction 32 bit microprocessor based with isolation transformers double conversion, SNMP controls, LCD display, Pure sine wave output, with auto static switch three phase input / Three phase output and modular structure for better thermal technology / cooling facility, with warranty up to three years.Makes: APC / Numeric / Emerson / Fuji Electric At Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 274500 | Nos | 274500 |  |  | 1 | 274500 |  |  |  | 90%
173 | Condensing units - VRF/VRV System 16 HP: Supply, Installation, Nitrogen testing , Vacuuming and Commissioning of air cooled variable refrigerant flow modular type condensing units, each comprising of multiple scroll compressors all inverter driven, full charge of refrigerant gas R-410a including additional gas filling , lubricating oil and all accessories as per the specifications. The condensing units shall be suitable to work on cooling mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B . The COP of the system shall be greater than 4 under ARI conditions for 100percentage load . The condensing units shall be suitable for operation on 415 plus or minus 10percentage volts, 50Hz, 3 phase AC power supply and , outdoor units to be mounted on MS platform with suitable Vibration Isolation pads to avoid vibrations. All the supports and angle base frame structure to be duly black painted with synthetic epoxy paint. the condensing units shall be of following capacities: The VRF ODU should be capable of working with total capacity of connected indoor units ranging between 100percentage to 140percentage of ODU capacity . COP minimum 3.5. Make : Daikin / LG / O General / Toshiba. 16 HP At Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 292500 | Nos | 292500 |  |  | 1 | 292500 |  |  |  | 90%
174 | VRF Indoor Units : Hi wall Splits 0.8 TR: Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 0.8 TR At Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 27630 | Nos | 27630 |  |  | 1 | 27630 |  |  |  | 90%
175 | VRF Indoor Units : Hi wall Splits 1.0 TR: Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.0 TR At Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 4 | 27630 | Nos | 110520 |  |  | 4 | 110520 |  |  |  | 90%
176 | VRF Indoor Units 1.5 TR : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.5 TR At Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 5 | 31500 | Nos | 157500 |  |  | 5 | 157500 |  |  |  | 90%
177 | Cassette Units 3.0 TR : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling mode.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 3.0 TR – 4 way At Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 45000 | Nos | 45000 |  |  | 1 | 45000 |  |  |  | 90%
3 | DICOM compatible fully digital, compact, portable, Ultrasound Scan Machine Colour Doppler at Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 2 | 1228500 | Nos | 2457000 |  |  | 2 | 2457000 |  |  |  | 90%
27 | Defibrilator at Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 281250 | Nos | 281250 |  |  | 1 | 281250 |  |  |  | 90%
30 | Anesthasia work station at Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 843750 | Nos | 843750 |  |  | 1 | 843750 |  |  |  | 90%
31 | Autoclave at Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 506250 | Nos | 506250 |  |  | 1 | 506250 |  |  |  | 90%
35 | Ultrasound Examination Couch at Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 73125 | Nos | 73125 |  |  | 1 | 73125 |  |  |  | 90%
2 | IVF Test tube Warmers at Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 2 | 44550 | Nos | 89100 |  |  | 2 | 89100 |  |  |  | 90%
4 | Multipurpose Electro hydraulic with manual override mobile OT Table, with divided leg section suitable for all Gynaecological surgical procedures, complete with 5cm Mattress and corded handset at Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 2 | 507375 | Nos | 1014750 |  |  | 2 | 1014750 |  |  |  | 90%
5 | LED procedure Lights Double dome at Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 281250 | Nos | 281250 |  |  | 1 | 281250 |  |  |  | 90%
6 | LED procedure Lights Single dome at Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 168750 | Nos | 168750 |  |  | 1 | 168750 |  |  |  | 90%
14 | IVF Thermometer with Probe
| V.P AB No 03 |  |  |  |  | 1 | 55688 | Nos | 55688 |  |  | 1 | 55688 |  |  |  | 90%
15 | CO2 Cylinder with accessories
| V.P AB No 03 |  |  |  |  | 2 | 45000 | Nos | 90000 |  |  | 2 | 90000 |  |  |  | 90%
26 | Cryocane TA 26 Ltr with wheels
| V.P AB No 03 |  |  |  |  | 2 | 55688 | Nos | 111376 |  |  | 2 | 111376 |  |  |  | 90%
16 | CO2 and O2 Analyzer
| V.P AB No 03 |  |  |  |  | 1 | 340200 | Nos | 340200 |  |  | 1 | 340200 |  |  |  | 90%
17 | PH Meter
| V.P AB No 03 |  |  |  |  | 1 | 84375 | Nos | 84375 |  |  | 1 | 84375 |  |  |  | 90%
19 | Sperm Counting Chamber
| V.P AB No 03 |  |  |  |  | 1 | 68063 | Nos | 68063 |  |  | 1 | 68063 |  |  |  | 90%
20 | Binocular Microscope MLX-B Plus
| V.P AB No 03 |  |  |  |  | 1 | 37125 | Nos | 37125 |  |  | 1 | 37125 |  |  |  | 90%
22 | Clinical Centrifuge machine for Andrology with Acessories
| V.P AB No 03 |  |  |  |  | 1 | 31050 | Nos | 31050 |  |  | 1 | 31050 |  |  |  | 90%
34 | Mulitfunctional Printer
| V.P AB No 03 |  |  |  |  | 1 | 39375 | Nos | 39375 |  |  | 1 | 39375 |  |  |  | 90%
37 | Laptop
| V.P AB No 03 |  |  |  |  | 2 | 103500 | Nos | 207000 |  |  | 2 | 207000 |  |  |  | 90%
23 | DRY Incubator
| V.P AB No 03 |  |  |  |  | 1 | 507375 | Nos | 507375 |  |  | 1 | 507375 |  |  |  | 90%
9 | CO2 Incubators
| V.P AB No 03 |  |  |  |  | 2 | 742500 | Nos | 1485000 |  |  | 2 | 1485000 |  |  |  | 90%
1 | Ovum Aspiration Pumps at Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 2 | 216000 | Nos | 432000 |  |  | 2 | 432000 |  |  |  | 90%
7 | IVF Workstation with LAF at Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 618750 | Nos | 618750 |  |  | 1 | 618750 |  |  |  | 90%
8 | IVF Anti-vibration Table for Procedure
| V.P AB No 03 |  |  |  |  | 1 | 86625 | Nos | 86625 |  |  | 1 | 86625 |  |  |  | 90%
10 | Trigas Bench Top Incubators for Human Embryo culture
| V.P AB No 03 |  |  |  |  | 1 | 742500 | Nos | 742500 |  |  | 1 | 742500 |  |  |  | 90%
11 | Trinocular Stereozoom Microscope
| V.P AB No 03 |  |  |  |  | 1 | 278100 | Nos | 278100 |  |  | 1 | 278100 |  |  |  | 90%
12 | ICSI Micro Manipulator with Inverted Microscope
| V.P AB No 03 |  |  |  |  | 1 | 2362500 | Nos | 2362500 |  |  | 1 | 2362500 |  |  |  | 90%
13 | IVF Laser System
| V.P AB No 03 |  |  |  |  | 1 | 2304000 | Nos | 2304000 |  |  | 1 | 2304000 |  |  |  | 90%
18 | VOC Meter for ART Lab
| V.P AB No 03 |  |  |  |  | 1 | 658125 | Nos | 658125 |  |  | 1 | 658125 |  |  |  | 90%
21 | Laminar Flow Cabinet with Andrology Work Station
| V.P AB No 03 |  |  |  |  | 1 | 225000 | Nos | 225000 |  |  | 1 | 225000 |  |  |  | 90%
24 | Pipetter and Denudation system
| V.P AB No 03 |  |  |  |  | 1 | 92813 | Nos | 92813 |  |  | 1 | 92813 |  |  |  | 90%
25 | Pharmaceutical Refrigerator
| V.P AB No 03 |  |  |  |  | 1 | 202500 | Nos | 202500 |  |  | 1 | 202500 |  |  |  | 90%
28 | 7 Para Patient Monitor
| V.P AB No 03 |  |  |  |  | 2 | 252000 | Nos | 504000 |  |  | 2 | 504000 |  |  |  | 90%
29 | Suction Machine
| V.P AB No 03 |  |  |  |  | 1 | 44550 | Nos | 44550 |  |  | 1 | 44550 |  |  |  | 90%
32 | Operative Hysteroscopy and Resectoscope Set Machine
| V.P AB No 03 |  |  |  |  | 1 | 1912500 | Nos | 1912500 |  |  | 1 | 1912500 |  |  |  | 90%
33 | Operative Laparoscopy Set
| V.P AB No 03 |  |  |  |  | 1 | 3780000 | Nos | 3780000 |  |  | 1 | 3780000 |  |  |  | 90%
39 | Reception Chair
| V.P AB No 03 |  |  |  |  | 2 | 31050 | Nos | 62100 |  |  | 2 | 62100 |  |  |  | 90%
42 | Consultant Chair
| V.P AB No 03 |  |  |  |  | 3 | 17325 | Nos | 51975 |  |  | 3 | 51975 |  |  |  | 90%
43 | Patient Chair
| V.P AB No 03 |  |  |  |  | 6 | 12375 | Nos | 74250 |  |  | 6 | 74250 |  |  |  | 90%
44 | Small Trolley
| V.P AB No 03 |  |  |  |  | 3 | 35280 | Nos | 105840 |  |  | 3 | 105840 |  |  |  | 90%
45 | Big Trolley
| V.P AB No 03 |  |  |  |  | 3 | 56250 | Nos | 168750 |  |  | 3 | 168750 |  |  |  | 90%
46 | Wall Storage Cabinets
| V.P AB No 03 |  |  |  |  | 8 | 15750 | Nos | 126000 |  |  | 8 | 126000 |  |  |  | 90%
151 | Modular Double skin floor mounted EUROVENT Certified Air Handling Unit 3400CFM / 8.5 TR / 150mm SP made out of 45 plus or minus 2mm thick PUF insulated panels Thermal break aluminium profile frame work with 0.8mm thick pre painted / powder coated inner and outer skins comprising of mixing box with fresh air and return air dampers, pre filters with 10 and 5 microns combination filters in single frame, Interlaced/Intertwined DX Cooling Coil suitable for connecting 2 nos of 8.5TR capacity 1W plus 1S out door condensing units, SS304 drain pan with , blower section with Nicotra / Kruger make direct drive/ Plug type fan, vibration isolators, EFF1 motor and blower section with on/off switches to operate from outside, limit switch for the fan section access door with a view port, fine filter section with 3 microns filters inspection doors for all filter and fan sections and damper at the outlet of unit. Ports for differential pressure gauges across all filters and blower to measure differential pressure. AHU Make : VTS / Systemair, Make - Blower - Nicotra / Kruger ; Motor - Crompton Greaves / Siemens ; Filter - Thermodyne / Freudenberg / Ultrafil at Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 531000 | Nos | 531000 |  |  | 1 | 531000 |  |  |  | 90%
166 | SITC of Magnehelic gauges across pre and fine filter at AHUs including mounting arrangement, SS nozzles, food grade PVC tubing, etc. At Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 3 | 9450 | Nos | 28350 |  |  | 3 | 28350 |  |  |  | 90%
167 | SITC of Magnehelic gauges to measure the room differential pressures in operation theatres with SS mounting box, SS nozzles, food grade PVC tubing, etc. At Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 2 | 11610 | Nos | 23220 |  |  | 2 | 23220 |  |  |  | 90%
153 | SITC of air cooled condensing units with two scroll compressors, air cooled condenser, power panel, vibration isolating pads, stand for ODU, thermostat, etc. of the following capacities. The nominal capacity of the condensing unit shall be as under. Air cooled condensing unit shall have horizontal discharge. All refrigerant piping accessories sight glass, drier, expansion valve, etc. shall be supplied with the condensing units and suitable to connect above AHUs. Refrigerant shall be R 407C / R 410A. Necessary thermostat, control wiring, etc. shall be included. Derating of the unit shall not be more than 15percentage under 45 deg. C ambient temperature. Condensing unit shall be capable of operating up 50 deg. C ambient temperature. 8.5 TR capacity At Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 2 | 163800 | Nos | 327600 |  |  | 2 | 327600 |  |  |  | 90%
154 | SITC of Flange type, Flame proof FLP duct heaters of 5 kW capacity with Mineral Filled AISI SS304/SS321 Sheathed Tubular Heater with GI Helical fins, Tube dia 8.2mm min and Helical Finn dia 25mm min, enclosed in the frame, FLP Terminal box etc., Nickel Chromium Inner Element, Silicon Sealing to Restrict Moisture pickup, Silver brazed mounting plate etc., and heaters shall be controlled with PID thyrestor controller based on the analog output signal of 0-10 V DC of controller . And this should have saftey thermostat and cutouts and air stat etc. all safety controls. The capacities as follows and sizes of the heaters shall be as per the duct sizes and approved drawing. at Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 184500 | Nos | 184500 |  |  | 1 | 184500 |  |  |  | 90%
152 | Supply and Installation of AL-powdercoated bottom loading type HEPA filter modules with bewel gear arrangement damper with access from clean room suitable to house the following size flange type HEPA filters including GI pressure plate, GI cleats with bolts and pressure drop & Integrity testing ports into room.Supply and Installation of H14 HEPA filters with 99.995% efficiency of the following sizes 600 X 600 X 150MM - HEPA filter - Module height <=350 mm,600 x 600 x 150 mm - 1000 CFM,600 x 600 x 150 mm - 1000 CFM
| V.P AB No 03 |  |  |  |  | 6 | 37800 | Nos | 226800 |  |  | 6 | 226800 |  |  |  | 90%
140 | Supply, Installation, testing And Commissioning of 20 nos LAN points with cat 6 cable and with suitable network rack and 5 nos of telephone points with knore box to existing EPABEX. At Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 344700 | Job | 344700 |  |  | 1 | 344700 |  |  |  | 90%
141 | Supply, Installation, testing And Commissioning of 1 no of Access control system with egress switch, power cable communication cable to control panel with necessary required items etc,. At Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 111600 | Nos | 111600 |  |  | 1 | 111600 |  |  |  | 90%
142 | Supply, Installation, testing And Commissioning of Automatic Fire Alaram system which is including 30 nos of smoke detectors 1nos manual call point 1 nos hooter with fire alaram cable connected to the existing fire control panel with necessary required item etc,. At Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 459000 | Job | 459000 |  |  | 1 | 459000 |  |  |  | 90%
143 | Supply, Installation, testing And Commissioning of 5 nos IP Based CCTV camers and cat 6 cable with NVR system. At Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 163800 | Job | 163800 |  |  | 1 | 163800 |  |  |  | 90%
144 | Supply, Installation, testing And Commissioning of Audio and video recording of counseling rooms . At Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 124200 | Job | 124200 |  |  | 1 | 124200 |  |  |  | 90%
145 | Supply and Installation of fire Extinguisher of CO2 4.5 kg at Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 5 | 10103 | Nos | 50515 |  |  | 5 | 50515 |  |  |  | 90%
146 | Supply and iInstalltion of ceiling mounted Fire extinguiser of ABC MAP 90, 5.0 kg stored pressure type at Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 5 | 6917 | Nos | 34585 |  |  | 5 | 34585 |  |  |  | 90%
147 | Supply and Installtion of 2.0 kg clean agent HCFC 123 Fire Extinguiser at Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 5 | 13559 | Nos | 67795 |  |  | 5 | 67795 |  |  |  | 90%
148 | Supply and Installaion of Fire escape signage Boards at Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 50400 | Job | 50400 |  |  | 1 | 50400 |  |  |  | 90%
94 | Air Shower Supply and installation,testing and commissioning of 16 GI Power coated Suitable single person entry air shower
| V.P AB No 03 |  |  |  |  | 1 | 319500 | Job | 319500 |  |  | 1 | 319500 |  |  |  | 90%
95 | Supply and installation,testing and commissioning of Static Pass Boxes Of Size 450 x 450mm with 1.2mm thick SS 304 Mat finish, with interlock doors, UV light on When Doors Closed Condition. As per Clean room standard and requirements
| V.P AB No 03 |  |  |  |  | 3 | 54900 | Job | 164700 |  |  | 3 | 164700 |  |  |  | 90%
Copper Pipe
178 | Supply installation,Testing and Commissioning of Hard Copper REFRIGERANT PIPING of 16 swg various sizes with necessary supports,fittings, interconnecting the liquid and suction lines between the indoor units. The piping shall be carried out of hard drawn copper pipes of type K with soldered/brazed socket fittings.Isolate each compressor, stainers,sight glass and any other componenet requiring proper operation and maintanance.Both the suction and liquid lines sahll be insulated with 19mm thick closed cell insulation for above 25mm dia,13mm thick for pipes below 25mm dia. the insulation finished with treated woven glass fiber reinforced covering for inside piping and including making required holes in the wall and re finishing and water tight of holes after laying holes as per the specifications and approved drawings at Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 1 | 360000 | Job | 360000 |  |  | 1 | 360000 |  |  |  | 90%
179 | Supply, Installation, Testing and Commissioning of refnet joints to be provided in refrigerant pipe line. Maretial of construction for fittings shall be similar to refrigerant piping.At Gandhi Hospital
| V.P AB No 03 |  |  |  |  | 11 | 5572 | Nos | 61292 |  |  | 11 | 61292 |  |  |  | 90%
Electrical -2
137 | SITC of IVF Center Main Panel Indoor IP-42 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with /without detachable extension type structure with all type of suitable switching accessories & bus-bar as per load requirement of respective IVF equipment’s. (Which is including Lighting, power DBs & UPS)
[6 empty] | 1 | 355000 | Nos | 355000 |  |  |  |  | 1 | 355000
138 | SITC of IVF center AC Panel outdoor IP-54 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with / without detachable extension type structure with all type of suitable switching accessories & bus-bar as per load requirement of respective AC equipment’s. (Which is including 1nos AHU’s stater with VFD by pass, Heater, ODU & VRF system)
| V.P MB No 04 |  |  |  |  | 1 | 270000 | Nos | 270000 |  |  |  |  | 1 | 270000
139 | Supply & installation of AHUs stater on/off push button station for Remote control for inside IVF center with control wiring from AC panel to on /off push button station with necessary items.
| V.P MB No 04 |  |  |  |  | 3 | 1540 | Nos | 4620 |  |  |  |  | 3 | 4620
136 | Supply, Laying & testing of 4Cx4 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
| V.P MB No 04 |  |  |  |  | 80 | 356 | Rmt | 28480 |  |  |  |  | 80 | 28480
[5 empty] | AE | 45 | 285 | Rmt | 12825 |  |  |  |  | 45 | 12825
135 | Supply, Laying & testing of 4Cx6 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
| V.P MB No 04 |  |  |  |  | 53 | 484 | Rmt | 25652 |  |  |  |  | 53 | 25652
134 | Supply, Lying & testing of 4Cx16 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
| V.P MB No 04 |  |  |  |  | 60 | 1483 | Rmt | 88980 |  |  |  |  | 60 | 88980
130 | Supply & installation of 25x3 Copper flat for Neutral earthing of UPS & Equipment which is laid in 100mm cable tray
| V.P MB No 04 |  |  |  |  | 65.3 | 902 | Rmt | 58900.6 |  |  |  |  | 65.3 | 58900.6
129 | Supply & installation of 25x3 GI flat for body earthing of DBs & Cable tray which is laid in 100mm cable tray
| V.P MB No 04 |  |  |  |  | 52.4 | 163 | Rmt | 8541.2 |  |  |  |  | 52.4 | 8541.2
127 | Providing and Fixing maintenance free earthing which consists of copper. Earth station, with 600X600X3.15mm Copper Plate at 2500mm Depth including construction of brick pedestal, providing meshed funnel, GI cover and other civil Engineering works, spreading a homogenous mixture of salt, charcoal around the pipe etc., completely as per IS 3043, 1987 or latest revision. Earthing testing should be done as per IE Rules like Earth valve test Etc.
| V.P MB No 04 |  |  |  |  | 2 | 22283 | Nos | 44566 |  |  |  |  | 2 | 44566
126 | Providing and Fixing maintenance free earthing which consists of G.I. Earth station, with 600X600X3.15mm GI Plate at 2500mm Depth including construction of brick pedestal, providing meshed funnel, GI cover and other civil Engineering works, spreading a homogenous mixture of salt, charcoal around the pipe etc., completely as per IS 3043, 1987 or latest revision. Earthing testing should be done as per IE Rules like Earth valve test Etc.
| V.P MB No 04 |  |  |  |  | 2 | 8500 | Nos | 17000 |  |  |  |  | 2 | 17000
121 | SITC of Hot dip galvanized perforated cable tray of 100 mm Wide sizes for to run the cable from DBs to SBs & sockets and AC panel to Units units. All necessary supports & accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. ( Elec 4.10.1 d)
| V.P MB No 04 |  |  |  |  | 36.2 | 429 | Rmt | 15529.8 |  |  |  |  | 36.2 | 15529.8
120 | Supply & installation of 225mm Light duty exhaust fan with metal blades etc complete Makes: Havells Ventilair-DB
| V.P MB No 04 |  |  |  |  | 4 | 2203 | Nos | 8812 |  |  |  |  | 4 | 8812
112 | Providing and fixing of 125A 25KA TPN Thermal Magnetic Release Based MCCB & Terminal Spreaders in Existing panel board with 1 No. and 1 Set of Indication Lamps, LED type, R,Y,B and breaker 'ON' , 'OFF', 'TRIP' & spring charged lamps. and replace with above Mentioned with required Drilling Holes, removing & Making Busbar connections etc, as required. Makes: Legrand / Schneider/ABB/L&T/C&S
| V.P MB No 04 |  |  |  |  | 1 | 28883 | Nos | 28883 |  |  |  |  | 1 | 28883
108 | Supply and fixing of DP Metal Enclosure with IP 20 Protection DB Make with 1 No 20A, 10 KA DP MCB Make: Legrand / Schneider including internal connection and labour charges for Flush Mounting etc., complete. Makes: Legrand
| V.P MB No 04 |  |  |  |  | 1 | 2562 | Nos | 2562 |  |  |  |  | 1 | 2562
96 | Supply and Fixing of 25mm outer dia medium grade, FRLS with IS:9537 part 3 rigid PVC pipe with all accessories fixing on wall / ceiling with chromium plated metallic base saddles including all labour charges etc., complete Makes:- Modi
| V.P MB No 04 |  |  |  |  | 200 | 116 | Rmt | 23200 |  |  |  |  | 200 | 23200
[5 empty] | AE | 31.4 | 93 | Rmt | 2920.2 |  |  |  |  | 31.4 | 2920.2
98 | Wiring with run of 2 of 22/0.3mm (1.5 Sqmm) FRLS / HFFR PVC insulated flexible ISI mark copper cable in existing PVC conduit pipe including Supply and fixing of Jumbo Ceiling rose and 6A/10A ISI Mark 1way Modular switch with required modular box and cover frame in existing Surface or Concealed pipe wiring including cost and conveyance of all material and all labour charges etc., complete for light, Fan, Exhaust fan and bell points in N.R.B. Makes of wires : Polycab (HFFR) Makes of switches :Honeywell Blenge Plus
| V.P MB No 04 |  |  |  |  | 27 | 945 | Rmt | 25515 |  |  |  |  | 27 | 25515
101 | Supply & fixing of 16A/6A, 2 in one socket - 2 Nos with 16A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benzplus
| V.P MB No 04 |  |  |  |  | 19 | 1755 | Nos | 33345 |  |  |  |  | 19 | 33345
105 | Supply and Run of 3 of 56/0.3mm (4.00 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Million(HFFR) / KEI (HFFR) /
| V.P MB No 04 |  |  |  |  | 178.3 | 255 | Nos | 45466.5 |  |  |  |  | 178.3 | 45466.5
106 | Supply and Run of 5 of 90/0.3mm (6.0 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Million
| V.P MB No 04 |  |  |  |  | 60 | 606 | Rmt | 36360 |  |  |  |  | 60 | 36360
[5 empty] | AE | 30 | 485 | Rmt | 14550 |  |  |  |  | 30 | 14550
104 | Supply and Run of 3 of 36/0.3mm (2.50 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
| V.P MB No 04 |  |  |  |  | 96.4 | 177 | Rmt | 17062.8 |  |  |  |  | 96.4 | 17062.8
sup | Supply and Transportation 56W Clean room Light fixture, 2' x2' (600mm x600mm) LED luminaire CRCA powder coated white after phosphocreatine treatment provided as standard. with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% etc., complete. MAKE: OSRAM / Wipro / Crompton / Bajaj / Havells
| V.P MB No 04 |  |  |  |  | 12
sup | Supply and Transportation of 48" ( 1200 mm) High Speed Fan Sweep Celing Fan with all accessories etc., complete. Make Havells S S 390
| V.P MB No 04 |  |  |  |  | 14
sup | Labour Charges for fixing of 48" Celing fan
| V.P MB No 04 |  |  |  |  | 14
sup | Supply and fixing of Anchor Fastner
| V.P MB No 04 |  |  |  |  | 14
sup | Supply & fixing of 2nos6A, 2 in one socket - 2 Nos with 6A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benz Plus
| V.P MB No 04 |  |  |  |  | 30
sup | Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete
| V.P MB No 04 |  |  |  |  | 14
sup | Supply and fixing of 15" Heavy Duty Exfan Make Almonard
| V.P MB No 04 |  |  |  |  | 1
Sup | Supply and fixing of 63 Amps 4 pole MCB in metal enclouser
1
[6 empty] | Grand Total |  |  | 33699819.1 |  |  |  | 28831257 |  | 1168771.1
[6 empty] | Add GST @ 18% |  |  | 6065967 |  |  |  | 5189626 |  | 210379
[6 empty] | Grand Total |  |  | 39765786.1 |  |  |  | 34020883 |  | 1379150.1
Certificate
[6 empty] | 1 | The work is in progress in according with the specification drawing and terms and condition the agreement.
[6 empty] | 2 | No recoveries are due for recovery from the contractor other than those propsed in the bill
[6 empty] | 3 | There are no further dues to be recovery from the contractor
[6 empty] | 4 | The contractor has conveyneced the materieals for use on the work as per the lead statement approved the agreement.
[6 empty] | 5 | The leads and lifts are cveried in the contractor.
Sumited to the Exective Engineer TSMSIDC Raga Reddy Division for favor of pri audit and payment

## CC 4th & part
CC 4th & Part Bill
| Name of the work:Design, Fabriction, establishing and commissioning of In - Vitro ferility centers (IVFC) alongwith allied Services on Turnkey basis at Gandhi hospital secunderabad. | [6 empty] | Agency: M/s. Asta Vardhman Consortium | [5 empty] | Agt.No: 344/A/TSMIDC/Spl.Proj/IVFCs/2022-23,Dt.05.07.2023
S.No | Discription Of Work etc., | Measurements Upto date | [6 empty] | Per | Total Volume |  | Deduct/previous Measurements |  | Since last measurement |  |  | Remarks
|  | No | L | B | D | Content | Rs | Ps. |  | Rs. | Ps | P.No. | Qty. | Qty | Value
[15 empty] | Rs. | Ps.
49 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete (Brick Masonary)
(Brick Masonary)
[6 empty] | 31.21 | 398 | Cum | 12422 |  |  | 31.21 | 12422 | 0
Old Cement Morter
[6 empty] | 37.13 | 8 | Sqm | 297 |  |  | 37.13 | 297 | 0
Unreinforcement Cement More Than 15cm
[6 empty] | 3.89 | 2842 | Cum | 11055 |  |  | 3.89 | 11055 | 0
Reinforcement Cement
[6 empty] | 0.7 | 3115 | Cum | 2181 |  |  | 0.7 | 2181 | 0
51 | Dismantling doors, windows and clear storey windows, Ventilators etc., (wood or steel) shutters including Chowkhats, architraves,hold fasts and other attachments etc., and stacking them within 100m lead including labour charge etc., and overheads & contractors profit complete for finished item of work.
[6 empty] | 5 | 468 | Each | 2340 |  |  | 5 | 2340 | 0
[5 empty] | AE | 2 | 374 | Each | 748 |  |  | 2 | 748 | 0
53 | Masonry work in CM (1:8) prop (cement: Screened sand) in super structure with / lime solid blocks of size 290mmx225mmx140mm from approved source having minimum crushing strength of 50 Kg/Sqcm including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, including sales & other taxes on all materials, all operational, incidental and labour charges such as mixing cement mortar, constructing masonry, scaffolding charges, lift charges, curing, etc., complete but excluding seigniorage charges for finished item of work. (APSS No. 501 & 504).
[6 empty] | 9.03 | 16055 | Cum | 144977 |  |  | 9.03 | 144977 | 0
54 | Reinforced brick Masonry for Partition Walls (11.0 cm thick) in CM (1:4) prop (cement: Screened sand) in super structure with / lime solid blocks of size 290mmx225mmx140mm from approved source having minimum crushing strength of 50 Kg/Sqcm including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, including sales & other taxes on all materials, all operational, incidental and labour charges such as mixing cement mortar, constructing masonry, scaffolding charges, lift charges, curing, etc., complete but excluding seigniorage charges for finished item of work. (APSS No. 501 & 504).
[6 empty] | 191.0305 | 1952 | Sqm | 372892 |  |  | 191.0305 | 372892 | 0
55 | Providing Thermo Mechanically Treated ( TMT) ( Fe-500/500D/550D from primery producer TATA, SAIL, VSP, JSW Steel, Goel steel, Jindal panther, X- Vega & balaji Shakthi as per IS 1786-2008) of Different Diameters RCC Works , including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and sizes and typing and lap - spacing with binding wire of 18 SWG, Forming grills for reinforcement work as per approved design and drawings, including and conveyanace of steel bars, including all wastages such as overlaps, coupling, chairs, spacer bars including cost and conveyance of binding wire cover blocks and incidential, operational, labour charges such as cutting bending, placing in position, typing incliding sales and other taxes on all materials etc., and overheads & contractors profit completefor finished item of work
[6 empty] | 0.103 | 116500 | MT | 12000 |  |  | 0.103 | 12000 | 0
Sup | Supply and placing of the Design Mix Concrete M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Weight Batcher / Concrete mixer with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials, centering using Casurina Ballies, Bamboos, Wooden Reapers, Runners, Wood Posts, Steel Plates etc., including all operational, incidental and labour charges such as weigh batching, machine mixing, lifting of concrete manually, laying concrete, curing , overheads & contractors profit etc., complete but excluding cost of steel and its fabrication charges for finished item of work (APSS No. 402) (For Lintels)
[6 empty] | 0.43 | 12775 | Cum | 5493 |  |  | 0.43 | 5493 | 0
56 | Plastering 12mm thick in two coats using screened sand with base coat of 8mm thick in CM (1:6) and top coat of 4mm thick in CM (1:4) with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales & other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and overheads & contractors profit complete for finished item of work. (SS 901,903 & 904).
[6 empty] | 536.1091 | 1041 | Sqm | 558090 |  |  | 536.1091 | 558090 | 0
Sup | Flooring with 16 to 18 mm thick high polished granite stone slabs black colour as approved by the Engineer-in-Charge of length not less than 2.43 mts set over base coat of cement mortar (1:8) , 20mm thick using screened sand over CC bed already laid or RCC roof slab including neat grey cement slurry of honey like consistency spread @ 3.3 Kg per sqm and jointed neatly with white cement paste mixed with pigment of matching shade to full depth including cost and conveyance of all materials like cement , sand , water , granite slabs etc., to work site and all operational, incidental labour & lift charges, half rounding the edge , polishing charges and all other taxes on all materials, cost of base coat and overheads & contractors profit complete for finished item of work for platforms (S.S.701 & special)
[6 empty] | 10.166 | 6300 | Sqm | 64071 |  |  | 10.166 | 64071 | 0
65 | Flooring with soluble salt porcelain vitrified tiles screen printed and polished of size 600 x 600 mm and thickness between 8 to 10mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630Parts 1 to 15 of any colour and finish in all shades and designs with borders and design as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM 1:8 prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread at the rate 3.3 kgs per Sqm. and jointed neatly with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site excluding cost of C.C. bed including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in- charge etc., and complete for finished item of work. TSSS No.701 and 707. 5th Floor at Gandhi Hospital
[6 empty] | 225 | 1725 | Sqm | 388125 |  |  | 225 | 388125 | 0
[6 empty] | 149.81 | 1380 | Sqm | 206738 |  |  | 149.81 | 206738 | 0
66 | Flooring with non-skid full body ceramic floor tiles of size 300mm x 300mm and thickness between 7 - 8mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630 Part 1 to 15 of any colour and finish in all shades and designs as approved by Engineer-in-charge, set over base coat of cement mortar 1:8, 12mm thick using screened sand over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread at the rate 3.3 Kgs per Sqm and jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, screened sand , water and tiles etc., complete for finished item of work. TSSS No.701 and 707 at Gandhi Hospital
[6 empty] | 14.618 | 1525 | Sqm | 22296 |  |  | 14.618 | 22296 | 0
68 | Providing dadooing to walls with glazed full body porcelain wall tiles of size 300 x 600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. 5th Floor at Gandhi Hospital
[6 empty] | 40 | 1423 | Sqm | 56920 |  |  | 40 | 56920 | 0
[6 empty] | 63.766 | 1138 | Sqm | 72566 |  |  | 63.766 | 72566 | 0
Sup | Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707)
[6 empty] | 107.179 | 114 | Rmt | 12219 |  |  | 107.179 | 12219 | 0
Electrical-1
96 | Supply and Fixing of 25mm outer dia medium grade, FRLS with IS:9537 part 3 rigid PVC pipe Concealed in with all required PVC/ Metalic junction boxes a including masonary work and labour charges etc., complete Makes:- Sudhakar / Modi
[6 empty] | 184.1 | 116 | Rmt | 21356 |  |  | 184.1 | 21356 | 0
97 | Supply and Fixing of 25mm outer dia medium grade, FRLS with IS:9537 part 3 rigid PVC pipe with all accessories fixing on wall / ceiling with chromium plated metallic base saddles including all labour charges etc., complete Makes:- Modi
[6 empty] | 500 | 107 | Rmt | 53500 |  |  | 500 | 53500 | 0
[5 empty] | AE | 560.2 | 86 | Rmt | 48177 |  |  | 560.2 | 48177 | 0
98 | Wiring with run of 2 of 22/0.3mm (1.5 Sqmm) FRLS / HFFR PVC insulated flexible ISI mark copper cable in existing PVC conduit pipe including Supply and fixing of Jumbo Ceiling rose and 6A/10A ISI Mark 1way Modular switch with required modular box and cover frame in existing Surface or Concealed pipe wiring including cost and conveyance of all material and all labour charges etc., complete for light, Fan, Exhaust fan and bell points in N.R.B. Makes of wires : Polycab (HFFR) Makes of switches :Honeywell Blenge Plus
[6 empty] | 110 | 945 | No | 103950 |  |  | 110 | 103950 | 0
[5 empty] | AE | 9 | 756 | No | 6804 |  |  | 9 | 6804 | 0
99 | Supply and fixing of 6A/10A ISI Mark 3/2 pin Modular socket with 6A/10A 1way Modular switch, 3 Module box with cover frame a Common switch board including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B. Makes of switches : Honeywell Blenge Plus
[6 empty] | 12 | 675 | No | 8100 |  |  | 12 | 8100 | 0
[5 empty] | AE | 18 | 540 | No | 9720 |  |  | 18 | 9720 | 0
100 | Supply and fixing of 16A switches - 1Nos and 6/16A 2 in one socket - 1Nos Modular type with cover plate and GI switch box fixing on separate board including all labour charges etc., complete. Makes of switches: - Hooney well Benzplus
[6 empty] | 14 | 1040 | No | 14560 |  |  | 14 | 14560 | 0
101 | Supply & fixing of 16A/6A, 2 in one socket - 2 Nos with 16A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benzplus
[6 empty] | 34 | 1755 | No | 59670 |  |  | 34 | 59670 | 0
104 | Supply and Run of 3 of 36/0.3mm (2.50 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
[6 empty] | 540.7 | 177 | Rmt | 95704 |  |  | 540.7 | 95704 | 0
105 | Supply and Run of 3 of 56/0.3mm (4.00 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
[6 empty] | 1170.8 | 255 | Rmt | 298554 |  |  | 1170.8 | 298554 | 0
106 | Supply and Run of 5 of 90/0.3mm (6.0 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
[6 empty] | 60 | 606 | Rmt | 36360 |  |  | 60 | 36360 | 0
[5 empty] | AE | 183.3 | 485 | Rmt | 88901 |  |  | 183.3 | 88901 | 0
107 | Supply & run of 5 of 10.0 Sqmm (140/0.3 mm) (3 phases, neutral and earth) FRLS / HFFR PVC insulated flexible copper cable in the existing conduit pipe for run of mains from Power panel board to TPN DB"s with pin type lugs and connections etc., complete. [for PDBs] Makes of wires: Polycab
[6 empty] | 40 | 967 | Rmt | 38680 |  |  | 40 | 38680 | 0
[6 empty] | 105.1 | 774 | Rmt | 81347 |  |  | 105.1 | 81347 | 0
109 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand and Supply and Fixing of 1 No., of 40A FP 30mA RCCB as incomer and 12 Nos 6-32 A 10kA SP MCBs Makes: Legrand-DX3 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. (For Lighting DBs) Make Legrand
[6 empty] | 3 | 18325 | No | 54975 |  |  | 3 | 54975 | 0
[6 empty] | 5 | 14660 | No | 73300 |  |  | 5 | 73300 | 0
110 | Supply and fixing of 8 Way VTPN DB with IP 43 Protection as per IS:13032 with 1 No., of 125A 4P MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted as incomer with 8 Nos of 63A, 10KA, TP MCBs C Curve ISI Mark as Out goings including internal connections and labour charges for FLUSH Mounting etc., complete. Makes : Legrand / Schneider
[6 empty] | 1 | 28460 | No | 28460 |  |  | 1 | 28460 | 0
114 | Supply, transportation and fixing of 24W edge lit LED Down light Square Housing Made of Aluminium alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser Square with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor > 0.9, Surge protection: > 2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI >80, and THD is less than 15% etc., with BIS Certification. Makes: Crompton
[6 empty] | 44 | 2652 | No | 116688 |  |  | 44 | 116688 | 0
115 | Supply and Transportation 36W Edge lit, 2' x2' (600mm x600mm) slim panel LED luminaire Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% etc., complete. Makes: Crompton
[6 empty] | 30 | 4350 | No | 130500 |  |  | 30 | 130500 | 0
[5 empty] | AE | 10 | 3480 | No | 34800 |  |  | 10 | 34800 | 0
119 | Supply and fixing of Modular type Stepped electronic regulator Makes : GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/ Cabtree Verna/ Million logus / Gold Medal Curve for sweep AC ceiling fans of 1200mm / 1400mm complete with connections.
[6 empty] | 12 | 827 | No | 9924 |  |  | 12 | 9924 | 0
[5 empty] | AE | 2 | 662 | No | 1324 |  |  | 2 | 1324 | 0
122 | SITC of Hot dip galvanized perforated cable tray of 300 mm Wide sizes for to run the cable from Floor Panel to Lab Panel & electrical room to AC panel and AC panel to Units. All necessary supports & accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. ( Elec 4.10.1 d)
[6 empty] | 80 | 1310 | Rmt | 104800 |  |  | 80 | 104800 | 0
[5 empty] | AE | 5.4 | 1048 | Rmt | 5659 |  |  | 5.4 | 5659 | 0
128 | Supply & installation of 50x6 GI flat for body earthing of electrical panel & AC Panel which is laid in 300mm cable tray
[6 empty] | 184.9 | 329 | Rmt | 60832 |  |  | 184.9 | 60832 | 0
129 | Supply & installation of 25x3 GI flat for body earthing of DBs & Cable tray which is laid in 100mm cable tray
[6 empty] | 100 | 163 | Rmt | 16300 |  |  | 100 | 16300 | 0
[5 empty] | AE | 16.3 | 130 | Rmt | 2119 |  |  | 16.3 | 2119 | 0
131 | Supply & installation of 4 sqmm Copper wire for Earthing of DBs Equipment
[6 empty] | 80 | 83 | Rmt | 6640 |  |  | 80 | 6640 | 0
[5 empty] | AE | 206 | 66 | Rmt | 13596 |  |  | 206 | 13596 | 0
132 | Supply, Lying & testing of 3.5Cx95 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/ Glostar/ Finolex Make of gland & Lungs: HMI/ Commet /Dowell’s
[6 empty] | 83 | 1207 | Rmt | 100181 |  |  | 83 | 100181 | 0
133 | Supply, Lying & testing of 3.5CX50 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/ Universal/ Glostar/ Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
[6 empty] | 40 | 722 | Rmt | 28880 |  |  | 40 | 28880 | 0
149 | Split AC unit 1.5 TR inverter type 3 Star capable of delivering 18000 BTU/hr and above with high wall mounted indoor unit and outdoor condensing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord , built-in stabilizer Voltage range 160- 264 volts and cordless remote control. Makes : Daikin / Thoshiba / O General at Gandhi Hospital
[6 empty] | 2 | 43200 | Nos | 86400 |  |  | 2 | 86400 |  |  |  | 90%
124 | Batteries : Supply and fixing of 12V 65 AH SMF battery including wire leads. Makes: Quanta / Racket / Exide. At Gandhi Hospital
[6 empty] | 32 | 18526 | Nos | 592832 |  |  | 32 | 592832 |  |  |  | 90%
125 | Supply and providing of UPS com Batteri rack for 20 batteries . At Gandhi Hospital
[6 empty] | 1 | 6088 | Nos | 6088 |  |  | 1 | 6088 |  |  |  | 90%
123 | 20 KVA UPS: Supply and installation of 20KVA 3ph in and 3ph out on line UPS system IGBT based rectifier with input power factor correction 32 bit microprocessor based with isolation transformers double conversion, SNMP controls, LCD display, Pure sine wave output, with auto static switch three phase input / Three phase output and modular structure for better thermal technology / cooling facility, with warranty up to three years.Makes: APC / Numeric / Emerson / Fuji Electric At Gandhi Hospital
[6 empty] | 1 | 274500 | Nos | 274500 |  |  | 1 | 274500 |  |  |  | 90%
173 | Condensing units - VRF/VRV System 16 HP: Supply, Installation, Nitrogen testing , Vacuuming and Commissioning of air cooled variable refrigerant flow modular type condensing units, each comprising of multiple scroll compressors all inverter driven, full charge of refrigerant gas R-410a including additional gas filling , lubricating oil and all accessories as per the specifications. The condensing units shall be suitable to work on cooling mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B . The COP of the system shall be greater than 4 under ARI conditions for 100percentage load . The condensing units shall be suitable for operation on 415 plus or minus 10percentage volts, 50Hz, 3 phase AC power supply and , outdoor units to be mounted on MS platform with suitable Vibration Isolation pads to avoid vibrations. All the supports and angle base frame structure to be duly black painted with synthetic epoxy paint. the condensing units shall be of following capacities: The VRF ODU should be capable of working with total capacity of connected indoor units ranging between 100percentage to 140percentage of ODU capacity . COP minimum 3.5. Make : Daikin / LG / O General / Toshiba. 16 HP At Gandhi Hospital
[6 empty] | 1 | 292500 | Nos | 292500 |  |  | 1 | 292500 |  |  |  | 90%
174 | VRF Indoor Units : Hi wall Splits 0.8 TR: Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 0.8 TR At Gandhi Hospital
[6 empty] | 1 | 27630 | Nos | 27630 |  |  | 1 | 27630 |  |  |  | 90%
175 | VRF Indoor Units : Hi wall Splits 1.0 TR: Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.0 TR At Gandhi Hospital
[6 empty] | 4 | 27630 | Nos | 110520 |  |  | 4 | 110520 |  |  |  | 90%
176 | VRF Indoor Units 1.5 TR : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.5 TR At Gandhi Hospital
[6 empty] | 5 | 31500 | Nos | 157500 |  |  | 5 | 157500 |  |  |  | 90%
177 | Cassette Units 3.0 TR : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling mode.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 3.0 TR – 4 way At Gandhi Hospital
[6 empty] | 1 | 45000 | Nos | 45000 |  |  | 1 | 45000 |  |  |  | 90%
3 | DICOM compatible fully digital, compact, portable, Ultrasound Scan Machine Colour Doppler at Gandhi Hospital
[6 empty] | 2 | 1228500 | Nos | 2457000 |  |  | 2 | 2457000 |  |  |  | 90%
27 | Defibrilator at Gandhi Hospital
[6 empty] | 1 | 281250 | Nos | 281250 |  |  | 1 | 281250 |  |  |  | 90%
30 | Anesthasia work station at Gandhi Hospital
[6 empty] | 1 | 843750 | Nos | 843750 |  |  | 1 | 843750 |  |  |  | 90%
31 | Autoclave at Gandhi Hospital
[6 empty] | 1 | 506250 | Nos | 506250 |  |  | 1 | 506250 |  |  |  | 90%
35 | Ultrasound Examination Couch at Gandhi Hospital
[6 empty] | 1 | 73125 | Nos | 73125 |  |  | 1 | 73125 |  |  |  | 90%
2 | IVF Test tube Warmers at Gandhi Hospital
[6 empty] | 2 | 44550 | Nos | 89100 |  |  | 2 | 89100 |  |  |  | 90%
4 | Multipurpose Electro hydraulic with manual override mobile OT Table, with divided leg section suitable for all Gynaecological surgical procedures, complete with 5cm Mattress and corded handset at Gandhi Hospital
[6 empty] | 2 | 507375 | Nos | 1014750 |  |  | 2 | 1014750 |  |  |  | 90%
5 | LED procedure Lights Double dome at Gandhi Hospital
[6 empty] | 1 | 281250 | Nos | 281250 |  |  | 1 | 281250 |  |  |  | 90%
6 | LED procedure Lights Single dome at Gandhi Hospital
[6 empty] | 1 | 168750 | Nos | 168750 |  |  | 1 | 168750 |  |  |  | 90%
14 | IVF Thermometer with Probe
[6 empty] | 1 | 55688 | Nos | 55688 |  |  | 1 | 55688 |  |  |  | 90%
15 | CO2 Cylinder with accessories
[6 empty] | 2 | 45000 | Nos | 90000 |  |  | 2 | 90000 |  |  |  | 90%
26 | Cryocane TA 26 Ltr with wheels
[6 empty] | 2 | 55688 | Nos | 111376 |  |  | 2 | 111376 |  |  |  | 90%
16 | CO2 and O2 Analyzer
[6 empty] | 1 | 340200 | Nos | 340200 |  |  | 1 | 340200 |  |  |  | 90%
17 | PH Meter
[6 empty] | 1 | 84375 | Nos | 84375 |  |  | 1 | 84375 |  |  |  | 90%
19 | Sperm Counting Chamber
[6 empty] | 1 | 68063 | Nos | 68063 |  |  | 1 | 68063 |  |  |  | 90%
20 | Binocular Microscope MLX-B Plus
[6 empty] | 1 | 37125 | Nos | 37125 |  |  | 1 | 37125 |  |  |  | 90%
22 | Clinical Centrifuge machine for Andrology with Acessories
[6 empty] | 1 | 31050 | Nos | 31050 |  |  | 1 | 31050 |  |  |  | 90%
34 | Mulitfunctional Printer
[6 empty] | 1 | 39375 | Nos | 39375 |  |  | 1 | 39375 |  |  |  | 90%
37 | Laptop
[6 empty] | 2 | 103500 | Nos | 207000 |  |  | 2 | 207000 |  |  |  | 90%
23 | DRY Incubator
[6 empty] | 1 | 507375 | Nos | 507375 |  |  | 1 | 507375 |  |  |  | 90%
9 | CO2 Incubators
[6 empty] | 2 | 742500 | Nos | 1485000 |  |  | 2 | 1485000 |  |  |  | 90%
1 | Ovum Aspiration Pumps at Gandhi Hospital
[6 empty] | 2 | 216000 | Nos | 432000 |  |  | 2 | 432000 |  |  |  | 90%
7 | IVF Workstation with LAF at Gandhi Hospital
[6 empty] | 1 | 618750 | Nos | 618750 |  |  | 1 | 618750 |  |  |  | 90%
8 | IVF Anti-vibration Table for Procedure
[6 empty] | 1 | 86625 | Nos | 86625 |  |  | 1 | 86625 |  |  |  | 90%
10 | Trigas Bench Top Incubators for Human Embryo culture
[6 empty] | 1 | 742500 | Nos | 742500 |  |  | 1 | 742500 |  |  |  | 90%
11 | Trinocular Stereozoom Microscope
[6 empty] | 1 | 278100 | Nos | 278100 |  |  | 1 | 278100 |  |  |  | 90%
12 | ICSI Micro Manipulator with Inverted Microscope
[6 empty] | 1 | 2362500 | Nos | 2362500 |  |  | 1 | 2362500 |  |  |  | 90%
13 | IVF Laser System
[6 empty] | 1 | 2304000 | Nos | 2304000 |  |  | 1 | 2304000 |  |  |  | 90%
18 | VOC Meter for ART Lab
[6 empty] | 1 | 658125 | Nos | 658125 |  |  | 1 | 658125 |  |  |  | 90%
21 | Laminar Flow Cabinet with Andrology Work Station
[6 empty] | 1 | 225000 | Nos | 225000 |  |  | 1 | 225000 |  |  |  | 90%
24 | Pipetter and Denudation system
[6 empty] | 1 | 92813 | Nos | 92813 |  |  | 1 | 92813 |  |  |  | 90%
25 | Pharmaceutical Refrigerator
[6 empty] | 1 | 202500 | Nos | 202500 |  |  | 1 | 202500 |  |  |  | 90%
28 | 7 Para Patient Monitor
[6 empty] | 2 | 252000 | Nos | 504000 |  |  | 2 | 504000 |  |  |  | 90%
29 | Suction Machine
[6 empty] | 1 | 44550 | Nos | 44550 |  |  | 1 | 44550 |  |  |  | 90%
32 | Operative Hysteroscopy and Resectoscope Set Machine
[6 empty] | 1 | 1912500 | Nos | 1912500 |  |  | 1 | 1912500 |  |  |  | 90%
33 | Operative Laparoscopy Set
[6 empty] | 1 | 3780000 | Nos | 3780000 |  |  | 1 | 3780000 |  |  |  | 90%
39 | Reception Chair
[6 empty] | 2 | 31050 | Nos | 62100 |  |  | 2 | 62100 |  |  |  | 90%
42 | Consultant Chair
[6 empty] | 3 | 17325 | Nos | 51975 |  |  | 3 | 51975 |  |  |  | 90%
43 | Patient Chair
[6 empty] | 6 | 12375 | Nos | 74250 |  |  | 6 | 74250 |  |  |  | 90%
44 | Small Trolley
[6 empty] | 3 | 35280 | Nos | 105840 |  |  | 3 | 105840 |  |  |  | 90%
45 | Big Trolley
[6 empty] | 3 | 56250 | Nos | 168750 |  |  | 3 | 168750 |  |  |  | 90%
46 | Wall Storage Cabinets
[6 empty] | 8 | 15750 | Nos | 126000 |  |  | 8 | 126000 |  |  |  | 90%
151 | Modular Double skin floor mounted EUROVENT Certified Air Handling Unit 3400CFM / 8.5 TR / 150mm SP made out of 45 plus or minus 2mm thick PUF insulated panels Thermal break aluminium profile frame work with 0.8mm thick pre painted / powder coated inner and outer skins comprising of mixing box with fresh air and return air dampers, pre filters with 10 and 5 microns combination filters in single frame, Interlaced/Intertwined DX Cooling Coil suitable for connecting 2 nos of 8.5TR capacity 1W plus 1S out door condensing units, SS304 drain pan with , blower section with Nicotra / Kruger make direct drive/ Plug type fan, vibration isolators, EFF1 motor and blower section with on/off switches to operate from outside, limit switch for the fan section access door with a view port, fine filter section with 3 microns filters inspection doors for all filter and fan sections and damper at the outlet of unit. Ports for differential pressure gauges across all filters and blower to measure differential pressure. AHU Make : VTS / Systemair, Make - Blower - Nicotra / Kruger ; Motor - Crompton Greaves / Siemens ; Filter - Thermodyne / Freudenberg / Ultrafil at Gandhi Hospital
[6 empty] | 1 | 531000 | Nos | 531000 |  |  | 1 | 531000 |  |  |  | 90%
166 | SITC of Magnehelic gauges across pre and fine filter at AHUs including mounting arrangement, SS nozzles, food grade PVC tubing, etc. At Gandhi Hospital
[6 empty] | 3 | 9450 | Nos | 28350 |  |  | 3 | 28350 |  |  |  | 90%
167 | SITC of Magnehelic gauges to measure the room differential pressures in operation theatres with SS mounting box, SS nozzles, food grade PVC tubing, etc. At Gandhi Hospital
[6 empty] | 2 | 11610 | Nos | 23220 |  |  | 2 | 23220 |  |  |  | 90%
153 | SITC of air cooled condensing units with two scroll compressors, air cooled condenser, power panel, vibration isolating pads, stand for ODU, thermostat, etc. of the following capacities. The nominal capacity of the condensing unit shall be as under. Air cooled condensing unit shall have horizontal discharge. All refrigerant piping accessories sight glass, drier, expansion valve, etc. shall be supplied with the condensing units and suitable to connect above AHUs. Refrigerant shall be R 407C / R 410A. Necessary thermostat, control wiring, etc. shall be included. Derating of the unit shall not be more than 15percentage under 45 deg. C ambient temperature. Condensing unit shall be capable of operating up 50 deg. C ambient temperature. 8.5 TR capacity At Gandhi Hospital
[6 empty] | 2 | 163800 | Nos | 327600 |  |  | 2 | 327600 |  |  |  | 90%
154 | SITC of Flange type, Flame proof FLP duct heaters of 5 kW capacity with Mineral Filled AISI SS304/SS321 Sheathed Tubular Heater with GI Helical fins, Tube dia 8.2mm min and Helical Finn dia 25mm min, enclosed in the frame, FLP Terminal box etc., Nickel Chromium Inner Element, Silicon Sealing to Restrict Moisture pickup, Silver brazed mounting plate etc., and heaters shall be controlled with PID thyrestor controller based on the analog output signal of 0-10 V DC of controller . And this should have saftey thermostat and cutouts and air stat etc. all safety controls. The capacities as follows and sizes of the heaters shall be as per the duct sizes and approved drawing. at Gandhi Hospital
[6 empty] | 1 | 184500 | Nos | 184500 |  |  | 1 | 184500 |  |  |  | 90%
152 | Supply and Installation of AL-powdercoated bottom loading type HEPA filter modules with bewel gear arrangement damper with access from clean room suitable to house the following size flange type HEPA filters including GI pressure plate, GI cleats with bolts and pressure drop & Integrity testing ports into room.Supply and Installation of H14 HEPA filters with 99.995% efficiency of the following sizes 600 X 600 X 150MM - HEPA filter - Module height <=350 mm,600 x 600 x 150 mm - 1000 CFM,600 x 600 x 150 mm - 1000 CFM
[6 empty] | 6 | 37800 | Nos | 226800 |  |  | 6 | 226800 |  |  |  | 90%
140 | Supply, Installation, testing And Commissioning of 20 nos LAN points with cat 6 cable and with suitable network rack and 5 nos of telephone points with knore box to existing EPABEX. At Gandhi Hospital
[6 empty] | 1 | 344700 | Job | 344700 |  |  | 1 | 344700 |  |  |  | 90%
141 | Supply, Installation, testing And Commissioning of 1 no of Access control system with egress switch, power cable communication cable to control panel with necessary required items etc,. At Gandhi Hospital
[6 empty] | 1 | 111600 | Nos | 111600 |  |  | 1 | 111600 |  |  |  | 90%
142 | Supply, Installation, testing And Commissioning of Automatic Fire Alaram system which is including 30 nos of smoke detectors 1nos manual call point 1 nos hooter with fire alaram cable connected to the existing fire control panel with necessary required item etc,. At Gandhi Hospital
[6 empty] | 1 | 459000 | Job | 459000 |  |  | 1 | 459000 |  |  |  | 90%
143 | Supply, Installation, testing And Commissioning of 5 nos IP Based CCTV camers and cat 6 cable with NVR system. At Gandhi Hospital
[6 empty] | 1 | 163800 | Job | 163800 |  |  | 1 | 163800 |  |  |  | 90%
144 | Supply, Installation, testing And Commissioning of Audio and video recording of counseling rooms . At Gandhi Hospital
[6 empty] | 1 | 124200 | Job | 124200 |  |  | 1 | 124200 |  |  |  | 90%
145 | Supply and Installation of fire Extinguisher of CO2 4.5 kg at Gandhi Hospital
[6 empty] | 5 | 10103 | Nos | 50515 |  |  | 5 | 50515 |  |  |  | 90%
146 | Supply and iInstalltion of ceiling mounted Fire extinguiser of ABC MAP 90, 5.0 kg stored pressure type at Gandhi Hospital
[6 empty] | 5 | 6917 | Nos | 34585 |  |  | 5 | 34585 |  |  |  | 90%
147 | Supply and Installtion of 2.0 kg clean agent HCFC 123 Fire Extinguiser at Gandhi Hospital
[6 empty] | 5 | 13559 | Nos | 67795 |  |  | 5 | 67795 |  |  |  | 90%
148 | Supply and Installaion of Fire escape signage Boards at Gandhi Hospital
[6 empty] | 1 | 50400 | Job | 50400 |  |  | 1 | 50400 |  |  |  | 90%
94 | Air Shower Supply and installation,testing and commissioning of 16 GI Power coated Suitable single person entry air shower
| V.P07 MB No 03 |  |  |  |  | 1 | 319500 | Job | 319500 |  |  | 1 | 319500 |  |  |  | 90%
95 | Supply and installation,testing and commissioning of Static Pass Boxes Of Size 450 x 450mm with 1.2mm thick SS 304 Mat finish, with interlock doors, UV light on When Doors Closed Condition. As per Clean room standard and requirements
| V.P08 MB No 03 |  |  |  |  | 3 | 54900 | Job | 164700 |  |  | 3 | 164700 |  |  |  | 90%
Copper Pipe
178 | Supply installation,Testing and Commissioning of Hard Copper REFRIGERANT PIPING of 16 swg various sizes with necessary supports,fittings, interconnecting the liquid and suction lines between the indoor units. The piping shall be carried out of hard drawn copper pipes of type K with soldered/brazed socket fittings.Isolate each compressor, stainers,sight glass and any other componenet requiring proper operation and maintanance.Both the suction and liquid lines sahll be insulated with 19mm thick closed cell insulation for above 25mm dia,13mm thick for pipes below 25mm dia. the insulation finished with treated woven glass fiber reinforced covering for inside piping and including making required holes in the wall and re finishing and water tight of holes after laying holes as per the specifications and approved drawings at Gandhi Hospital
[6 empty] | 1 | 360000 | Job | 360000 |  |  | 1 | 360000 |  |  |  | 90%
179 | Supply, Installation, Testing and Commissioning of refnet joints to be provided in refrigerant pipe line. Maretial of construction for fittings shall be similar to refrigerant piping.At Gandhi Hospital
[6 empty] | 11 | 5572 | Nos | 61292 |  |  | 11 | 61292 |  |  |  | 90%
Electrical -2
137 | SITC of IVF Center Main Panel Indoor IP-42 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with /without detachable extension type structure with all type of suitable switching accessories & bus-bar as per load requirement of respective IVF equipment’s. (Which is including Lighting, power DBs & UPS)
[6 empty] | 1 | 355000 | Nos | 355000 |  |  |  |  | 1 | 355000
138 | SITC of IVF center AC Panel outdoor IP-54 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with / without detachable extension type structure with all type of suitable switching accessories & bus-bar as per load requirement of respective AC equipment’s. (Which is including 1nos AHU’s stater with VFD by pass, Heater, ODU & VRF system)
[6 empty] | 1 | 270000 | Nos | 270000 |  |  |  |  | 1 | 270000
139 | Supply & installation of AHUs stater on/off push button station for Remote control for inside IVF center with control wiring from AC panel to on /off push button station with necessary items.
[6 empty] | 3 | 1540 | Nos | 4620 |  |  |  |  | 3 | 4620
136 | Supply, Laying & testing of 4Cx4 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
[6 empty] | 80 | 356 | Rmt | 28480 |  |  |  |  | 80 | 28480
[5 empty] | AE | 45 | 285 | Rmt | 12825 |  |  |  |  | 45 | 12825
135 | Supply, Laying & testing of 4Cx6 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
[6 empty] | 53 | 484 | Rmt | 25652 |  |  |  |  | 53 | 25652
134 | Supply, Lying & testing of 4Cx16 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
[6 empty] | 60 | 1483 | Rmt | 88980 |  |  |  |  | 60 | 88980
130 | Supply & installation of 25x3 Copper flat for Neutral earthing of UPS & Equipment which is laid in 100mm cable tray
[6 empty] | 65.3 | 902 | Rmt | 58900.6 |  |  |  |  | 65.3 | 58900.6
129 | Supply & installation of 25x3 GI flat for body earthing of DBs & Cable tray which is laid in 100mm cable tray
[6 empty] | 52.4 | 163 | Rmt | 8541.2 |  |  |  |  | 52.4 | 8541.2
127 | Providing and Fixing maintenance free earthing which consists of copper. Earth station, with 600X600X3.15mm Copper Plate at 2500mm Depth including construction of brick pedestal, providing meshed funnel, GI cover and other civil Engineering works, spreading a homogenous mixture of salt, charcoal around the pipe etc., completely as per IS 3043, 1987 or latest revision. Earthing testing should be done as per IE Rules like Earth valve test Etc.
[6 empty] | 2 | 22283 | Nos | 44566 |  |  |  |  | 2 | 44566
126 | Providing and Fixing maintenance free earthing which consists of G.I. Earth station, with 600X600X3.15mm GI Plate at 2500mm Depth including construction of brick pedestal, providing meshed funnel, GI cover and other civil Engineering works, spreading a homogenous mixture of salt, charcoal around the pipe etc., completely as per IS 3043, 1987 or latest revision. Earthing testing should be done as per IE Rules like Earth valve test Etc.
[6 empty] | 2 | 8500 | Nos | 17000 |  |  |  |  | 2 | 17000
121 | SITC of Hot dip galvanized perforated cable tray of 100 mm Wide sizes for to run the cable from DBs to SBs & sockets and AC panel to Units units. All necessary supports & accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. ( Elec 4.10.1 d)
[6 empty] | 36.2 | 429 | Rmt | 15529.8 |  |  |  |  | 36.2 | 15529.8
120 | Supply & installation of 225mm Light duty exhaust fan with metal blades etc complete Makes: Havells Ventilair-DB
[6 empty] | 4 | 2203 | Nos | 8812 |  |  |  |  | 4 | 8812
112 | Providing and fixing of 125A 25KA TPN Thermal Magnetic Release Based MCCB & Terminal Spreaders in Existing panel board with 1 No. and 1 Set of Indication Lamps, LED type, R,Y,B and breaker 'ON' , 'OFF', 'TRIP' & spring charged lamps. and replace with above Mentioned with required Drilling Holes, removing & Making Busbar connections etc, as required. Makes: Legrand / Schneider/ABB/L&T/C&S
[6 empty] | 1 | 28883 | Nos | 28883 |  |  |  |  | 1 | 28883
108 | Supply and fixing of DP Metal Enclosure with IP 20 Protection DB Make with 1 No 20A, 10 KA DP MCB Make: Legrand / Schneider including internal connection and labour charges for Flush Mounting etc., complete. Makes: Legrand
[6 empty] | 1 | 2562 | Nos | 2562 |  |  |  |  | 1 | 2562
96 | Supply and Fixing of 25mm outer dia medium grade, FRLS with IS:9537 part 3 rigid PVC pipe with all accessories fixing on wall / ceiling with chromium plated metallic base saddles including all labour charges etc., complete Makes:- Modi
[6 empty] | 200 | 116 | Rmt | 23200 |  |  |  |  | 200 | 23200
[5 empty] | AE | 31.4 | 93 | Rmt | 2920.2 |  |  |  |  | 31.4 | 2920.2
98 | Wiring with run of 2 of 22/0.3mm (1.5 Sqmm) FRLS / HFFR PVC insulated flexible ISI mark copper cable in existing PVC conduit pipe including Supply and fixing of Jumbo Ceiling rose and 6A/10A ISI Mark 1way Modular switch with required modular box and cover frame in existing Surface or Concealed pipe wiring including cost and conveyance of all material and all labour charges etc., complete for light, Fan, Exhaust fan and bell points in N.R.B. Makes of wires : Polycab (HFFR) Makes of switches :Honeywell Blenge Plus
[6 empty] | 27 | 945 | Rmt | 25515 |  |  |  |  | 27 | 25515
101 | Supply & fixing of 16A/6A, 2 in one socket - 2 Nos with 16A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benzplus
[6 empty] | 19 | 1755 | Nos | 33345 |  |  |  |  | 19 | 33345
105 | Supply and Run of 3 of 56/0.3mm (4.00 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Million(HFFR) / KEI (HFFR) /
[6 empty] | 178.3 | 255 | Nos | 45466.5 |  |  |  |  | 178.3 | 45466.5
106 | Supply and Run of 5 of 90/0.3mm (6.0 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Million
[6 empty] | 60 | 606 | Rmt | 36360 |  |  |  |  | 60 | 36360
[5 empty] | AE | 30 | 485 | Rmt | 14550 |  |  |  |  | 30 | 14550
104 | Supply and Run of 3 of 36/0.3mm (2.50 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
[6 empty] | 96.4 | 177 | Rmt | 17062.8 |  |  |  |  | 96.4 | 17062.8
sup | Supply and Transportation 56W Clean room Light fixture, 2' x2' (600mm x600mm) LED luminaire CRCA powder coated white after phosphocreatine treatment provided as standard. with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% etc., complete. MAKE: OSRAM / Wipro / Crompton / Bajaj / Havells
12
sup | Supply and Transportation of 48" ( 1200 mm) High Speed Fan Sweep Celing Fan with all accessories etc., complete. Make Havells S S 390
14
sup | Labour Charges for fixing of 48" Celing fan
14
sup | Supply and fixing of Anchor Fastner
14
sup | Supply & fixing of 2nos6A, 2 in one socket - 2 Nos with 6A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benz Plus
30
sup | Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete
14
sup | Supply and fixing of 15" Heavy Duty Exfan Make Almonard
1
Sup | Supply and fixing of 63 Amps 4 pole MCB in metal enclouser
1
[6 empty] | Grand Total |  |  | 33699819.1 |  |  |  | 32531048 |  | 1168771.1
[6 empty] | Add GST @ 18% |  |  | 6065967 |  |  |  | 5855589 |  | 210379
[6 empty] | Grand Total |  |  | 39765786.1 |  |  |  | 38386637 |  | 1379150.1
Certificate
[6 empty] | 1 | The work is in progress in according with the specification drawing and terms and condition the agreement.
[6 empty] | 2 | No recoveries are due for recovery from the contractor other than those propsed in the bill
[6 empty] | 3 | There are no further dues to be recovery from the contractor
[6 empty] | 4 | The contractor has conveyneced the materieals for use on the work as per the lead statement approved the agreement.
[6 empty] | 5 | The leads and lifts are cveried in the contractor.
Sumited to the Exective Engineer TSMSIDC Raga Reddy Division for favor of pri audit and payment

## Bill-5
DETAILED MEASUREMENTS
| Name of the work:Design, Fabriction, establishing and commissioning of In - Vitro ferility centers (IVFC) alongwith allied Services on Turnkey basis at Gandhi hospital secunderabad. | [8 empty] | Agency: M/s. Asta vardhman Consortium | [5 empty] | Agt.No: 344/A/TSMIDC/Spl.Proj/IVFCs/2022-23, Dt. 05.07.2023
| Discription Of Work etc., | Measurements Upto date | [8 empty] | Per | Total Volume |  | Deduct/previous Measurements |  | Since last measurement |  |  | Remarks
|  | No |  | L | B | D | Content | Units | Rs | Ps. |  | Rs. | Ps | P.No. | Qty. | Qty | Value
[17 empty] | Rs. | Ps.
49 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete (Brick Masonary)
| Supply Duct | 1 | 2 | 0.75 | 0.23 | 0.4 | 0.138
| Return Duct | 1 | 2 | 0.85 | 0.23 | 0.4 | 0.1564
| Access Control Door | 1 | 1 | 3 | 0.23 | 3 | 2.07
| Door Deduction(-) | -1 | 1 | 1.5 | 0.23 | 2.6 | -0.897
[7 empty] | 1.4674 | Cum
53 | Masonry work in CM (1:6) prop (cement: Screened sand) in super structure with Aerated (Cellular) Autoclaved Concrete Blocks conforming to IS:2185 (Part-3) - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600x 230 x 200 mm from approved source having minimum crushing strength of 3 N/Sq.m including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, including sales & other taxes on all materials, all operational, incidental and labour charges such as mixing cement mortar, constructing masonry, scaffolding charges, lift charges, curing, etc., complete but excluding seigniorage charges for finished item of work. (APSS No. 501 & 504).
| AHU Brick Pedastal | 1 | 1 | 4.2 | 1.4 | 0.3 | 5.88
| RO Brick Pedastal | 1 | 1 | 0.6 | 0.6 | 0.6 | 0.36
[7 empty] | 6.24 | Cum
56 | Plastering 20mm thick in two coats using screened sand with base coat of 8mm thick in CM (1:6) and top coat of 4mm thick in CM (1:4) with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales & other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and overheads & contractors profit complete for finished item of work. (SS 901,903 & 904).
| AHU Brick Pedastal | 1 | 1 | 4.2 | 1.4 |  | 5.88
| do | 1 | 2 | 4.2 |  | 0.3 | 2.52
| do | 1 | 2 | 1.4 |  | 0.3 | 0.84
| RO Brick Pedastal | 1 | 1 | 0.6 | 0.6 |  | 0.36
| do | 1 | 2 | 0.6 |  | 0.6 | 0.72
| do | 1 | 2 | 0.6 |  | 0.6 | 0.72
[7 empty] | 11.04 | Sqm
58 | Supply and Installation change room Cubicles at Gandhi Hospital GENERAL SPECIFICATIONS: Thickness of compact Laminate:12mm Thick Colour OF HPL Boards,In Single Colour,Size of Cubicle As per DWG, Door Size For Normal Cubicles AS per DWG Overall Height of Cubicle,2105mm Including bottom gap of 100mm,Accessories , Manufacturers standard makes of aluminium , SS Accessories .a Aluminium H Top Rail b. SS Hinges c. SS privacy Thumb turn occupancy indicator d.SS coat hook e. SS Door knob f. Aluminium U Channel g.Aluminium Door Stopper Channel h. Runner lining i.SS Screw And PVC Wall Plugs
| Dr. Change Room | 1 | 1 | 1.46 |  | 2.2 | 3.212
| do | 1 | 1 | 1.42 |  | 2.2 | 3.124
| Patient Change Room | 1 | 1 | 1.5 |  | 2.2 | 3.3
| Staff Change Room 1 | 1 | 1 | 1.62 |  | 2.2 | 3.564
| Staff Change Room 2 | 1 | 1 | 1.65 |  | 2.2 | 3.63
[7 empty] | 16.83 | Sqm
69 | Providing and applying Wall putty of White Cement or Polymer or Cement based of average 1 to 2 mm thickness over plastered surface to prepare the surface even and smooth after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, applying emery paper, Sand the surface, clean & wipe off loose dust, applying knifing paste filler by putty knife / muslin pad, air dry for 2 - 3 hrs, sand with 180 and 320 No., emery paper for the surface preparation including cost and conveyance of all materials to work site and all operational, incidental, labour charges, over heads and contractors profit etc., complete for finished item of work in all floors for Internal walls.
| Main Entry Corridor | 1 | 1 | 6.3 |  | 2 | 12.6
| main Entry Access Control Door | 1 | 1 | 3 |  | 2 | 6
| Door Deduction(-) | -1 | 1 | 1.5 |  | 2 | -3
| Corridor at Reception | 1 | 1 | 3 |  | 2 | 6
| Reception area | 1 | 2 | 3.4 |  | 2 | 13.6
| Record Room Main Door Wall | 1 | 1 | 3 |  | 2 | 6
| Door Jam | 1 | 1 | 5.2 | 0.15 |  | 0.78
| Door Deduction(-) | -1 | 1 | 1 |  | 2 | -2
| Record Room Inside | 1 | 2 | 3.2 |  | 2 | 12.8
| do | 1 | 1 | 3 |  | 2 | 6
| do | 1 | 1 | 3 |  | 3.5 | 10.5
| Door deductions(-) | -1 | 1 | 1 |  | 2.1 | -2.1
| Window Deduction(-) | 1 | 1 | 1.8 |  | 1.4 | 2.52
| Wndow Jam | 1 | 1 | 5.4 | 0.15 |  | 0.81
| Ultra Sound Room Inside Long Wall | 1 | 2 | 4.47 |  | 3.5 | 31.29
| Ultra Sound Room Inside Short Wall | 1 | 2 | 2.18 |  | 3.5 | 15.26
| Door Jam | 1 | 1 | 5.812 | 0.15 |  | 0.8718
| Door Deduction(-) | -1 | 1 | 1.215 |  | 2.3 | -2.7945
| Ventilator Deduction(-) | -1 | 1 | 0.45 |  | 0.45 | -0.2025
| Ventilator jam | 1 | 1 | 1.8 | 0.15 |  | 0.27
| Autoclave Room Inside Long Wall | 1 | 2 | 2.18 |  | 3.5 | 15.26
| Autoclave Room Inside Short Wall | 1 | 2 | 1.19 |  | 3.5 | 8.33
| Door deduction(-) | -1 | 1 | 1.21 |  | 2.37 | -2.8677
| Door Jam | 1 | 1 | 5.81 | 0.15 |  | 0.8715
| Toilet at Counseling Room 2 Inside Long Wall | 1 | 2 | 1.5 |  | 2 | 6
| Toilet at Counseling Room 2 Inside Short Wall Wall | 1 | 2 | 1.2 |  | 2 | 4.8
| Door Deduction(-) | -1 | 2 | 0.8 |  | 2 | -3.2
| Door Jam | 1 | 1 | 5 | 0.15 |  | 0.75
| Counseling Room 2 Inside Long Wall | 1 | 2 | 3.24 |  | 3.5 | 22.68
| Counseling Room 2 Inside Long Wall | 1 | 2 | 2.45 |  | 3.5 | 17.15
| Door jam | 1 | 1 | 5.47 | 0.15 |  | 0.8205
| Door Deduction(-) | -1 | 1 | 1.07 |  | 2.2 | -2.354
| Window Deduction(-) | -1 | 1 | 1.8 |  | 1.8 | -3.24
| Counseling Room 1 inside Long Wall | 1 | 2 | 3.24 |  | 3.5 | 22.68
| Counseling Room 1 inside Short Wall | 1 | 2 | 2.45 |  | 3.5 | 17.15
| Door Jam | 1 | 1 | 5.49 | 0.15 |  | 0.8235
| Door Deduction(-) | -1 | 1 | 1.09 |  | 2.2 | -2.398
| Corridor at Counseling Room 1 and 2 | 1 | 2 | 5.1 |  | 3.5 | 35.7
| do | 1 | 1 | 1.2 |  | 3.5 | 4.2
| Door Deductions(-) Counseling Room 2 | -1 | 1 | 1.09 |  | 2.2 | -2.398
| Door Deductions(-) Counseling Room 1 | -1 | 1 | 1.07 |  | 2.2 | -2.354
| Door Deductions(-) Auto Clave Room | -1 | 1 | 1.2 |  | 2.3 | -2.76
| Door Deductions(-) Altra Sound Room | -1 | 1 | 1.2 |  | 2.3 | -2.76
| Corridor at prepost Operative Wards | 1 | 2 | 6.3 |  | 2 | 25.2
| Door Deduction(-) | -1 | 1 | 1.49 |  | 2 | -2.98
| Corridor Deduction(-) | -1 | 1 | 1.2 |  | 2 | -2.4
| Prepost Operative Wards Inside Long Wall | 1 | 1 | 6.48 |  | 2 | 12.96
| Prepost Operative Wards Inside Long Wall | 1 | 1 | 4.38 |  | 2 | 8.76
| Prepost Operative Wards Inside Short Wall | 1 | 1 | 6 |  | 2 | 12
| Prepost Operative Wards Inside Short Wall | 1 | 1 | 4.8 |  | 2 | 9.6
| Door Deduction(-) | -1 | 1 | 1.49 |  | 2 | -2.98
| Door Jam | 1 | 1 | 6.49 | 0.23 |  | 1.4927
| Window Deduction(-) | -1 | 1 | 1.8 |  | 1.4 | -2.52
| Window Jam | 1 | 1 | 7.2 | 0.15 |  | 1.08
| Corridor At Semi Sterile Area | 1 | 2 | 6.45 |  | 2 | 25.8
| Corridor Opening Deductions(-) | -1 | 2 | 1.2 |  | 1.5 | -3.6
| Access Control Door at Semistearail Area | 1 | 2 | 3 |  | 3.5 | 21
| Door Deduction(-) | -1 | 2 | 1.5 |  | 2.6 | -7.8
| Door Jam | 1 | 1 | 6.7 | 0.23 |  | 1.541
| Corridor at Dr Change Room Long Wall | 1 | 2 | 4.7 |  | 3.5 | 32.9
| Corridor at Dr Change Room Short Wall | 1 | 2 | 4.68 |  | 3.5 | 32.76
| Corridor Opening Deductions(-) | 1 | 1 | 1.2 |  | 3 | 3.6
| Toilet Door Deduction(-) | -1 | 1 | 1 |  | 2.1 | -2.1
| Dr Toilet Inside | 1 | 2 | 4.68 |  | 2 | 18.72
| Dr Toilet Inside | 1 | 2 | 1.85 |  | 2 | 7.4
| Door Deduction(-) | -1 | 1 | 1 |  | 2.1 | -2.1
| Ventilator Deduction(-) | -1 | 1 | 0.45 |  | 0.45 | -0.2025
| Dr Change Room Partitions | 1 | 2 | 2.61 |  | 3.5 | 18.27
| Dr Change Room Partitions | 1 | 2 | 2.2 |  | 3.5 | 15.4
| Door Deductions(-) | -1 | 1 | 1 |  | 2.1 | -2.1
| Dr Change Room Partitions | 1 | 2 | 1.45 |  | 3.5 | 10.15
| Dr Change Room Partitions | 1 | 2 | 1.45 |  | 3.5 | 10.15
| Corridor at Manifold Room | 1 | 2 | 3.3 |  | 3.5 | 23.1
| Corridor at Manifold Room | 1 | 1 | 1.2 |  | 3.5 | 4.2
| Door Deductions(-) | -1 | 1 | 1.08 |  | 2.3 | -2.484
| Door Deductions(-) | -1 | 1 | 0.986 |  | 2.2 | -2.1692
| Manifold Room Inside Long Walls | 1 | 2 | 3.185 |  | 3.5 | 22.295
| Manifold Room Inside Short Walls | 1 | 2 | 2.13 |  | 3.5 | 14.91
| Door Deductions(-) | -1 | 1 | 1.01 |  | 2.3 | -2.323
| Door Jam | 1 | 1 | 5.61 | 0.15 |  | 0.8415
| Change Room walls | 3 | 2 | 1.87 |  | 3.5 | 39.27
| Change Room wall | 1 | 1 | 5.2 |  | 2 | 10.4
| Corridor at Blood Collection Room | 1 | 1 | 5.2 |  | 3.5 | 18.2
| Door Deductions(-) | -1 | 1 | 0.998 |  | 2.1 | -2.0958
| Door Deductions(-) | -1 | 1 | 0.999 |  | 2.1 | -2.0979
| Store Room Inside Long Wall | 1 | 1 | 3.3 |  | 3.5 | 11.55
| Store Room Inside Long Wall | 1 | 1 | 3.3 |  | 2.4 | 7.92
| Store Room Inside Short Wall | 1 | 2 | 2.5 |  | 3.5 | 17.5
| Door Deductions(-) | -1 | 1 | 1 |  | 2.1 | -2.1
| Partition Wall Top | 1 | 1 | 3.3 | 0.15 |  | 0.495
| Blood Collection Room Long Wall | 1 | 2 | 3.3 |  | 2.4 | 15.84
| Blood Collection Room Short Wall | 1 | 2 | 2.5 |  | 3.5 | 17.5
| Door Deductions(-) | -1 | 1 | 1 |  | 2.1 | -2.1
| Tartition Wall Top | 1 | 1 | 3.3 | 0.15 |  | 0.495
| Sperm Collection Inside Long Wall | 1 | 1 | 3.3 |  | 2.4 | 7.92
| Sperm Collection Inside Long Wall | 1 | 1 | 3.3 |  | 3.5 | 11.55
| Sperm Collection Inside Short Wall | 1 | 2 | 3.265 |  | 3.5 | 22.855
| Door Deductions(-) | -1 | 1 | 0.8 |  | 2.1 | -1.68
| Door Deductions(-) | -1 | 1 | 1 |  | 2.1 | -2.1
| Sperm Collection Toilet inside | 1 | 2 | 1.6 |  | 2 | 6.4
| Sperm Collection Toilet inside | 1 | 2 | 1.1 |  | 2 | 4.4
| Door Deductions(-) | -1 | 1 | 0.8 |  | 2.1 | -1.68
| Ventilator Deduction(-) | -1 | 1 | 0.45 |  | 0.45 | -0.2025
| Corridor at Sterile area | 1 | 2 | 6.3 |  | 2 | 25.2
| Corridor at Sterile area | 1 | 1 | 3 |  | 2 | 6
| Door Deductions(-) Minor OT | -1 | 1 | 1.5 |  | 2 | -3
| Door Deductions(-) Major OT | -1 | 1 | 1.5 |  | 2 | -3
| Door Deductions(-) Andrology Lab | -1 | 1 | 1.5 |  | 2 | -3
| Door Deductions(-) Emergency Exit | -1 | 1 | 1.8 |  | 2 | -3.6
| Minor OT Inside Long Walls | 1 | 2 | 6.4 |  | 3.5 | 44.8
| Minor OT Inside Short Walls | 1 | 2 | 4.2 |  | 3.5 | 29.4
| Door Deductions(-) | -1 | 1 | 1.5 |  | 2.6 | -3.9
| Pass box Opening (-) | -1 | 1 | 0.6 |  | 0.6 | -0.36
| Androlry Lab Long Walls Inside | 1 | 2 | 4.25 |  | 3.5 | 29.75
| Androlry Lab Short Walls Inside | 1 | 2 | 4.08 |  | 3.5 | 28.56
| Door Deductions(-) | -1 | 1 | 1.5 |  | 2.6 | -3.9
| Door Deductions(-) | -1 | 1 | 1 |  | 2.1 | -2.1
| Cryo Room Inside | 1 | 2 | 3 |  | 3.5 | 21
| do | 1 | 2 | 1.6 |  | 3.5 | 11.2
| Door Deductions | -1 | 1 | 1 |  | 2.1 | -2.1
| Staire Case area | 1 | 1 | 4.2 |  | 2 | 8.4
| Staire Case area | 1 | 2 | 4.2 |  | 2 | 16.8
| Window Deduction(-) | -1 | 1 | 1.8 |  | 1.8 | -3.24
| Dr. Change Room | 2 | 2 | 2.2 |  | 3.45 | 30.36
| Store Room | 1 | 2 | 3.18 |  | 3.45 | 21.942
| do | 1 | 2 | 2.18 |  | 3.45 | 15.042
| Door Deduction(-) | -1 | 2 | 0.8 |  | 2.1 | -3.36
| Change Rooms | 2 | 2 | 1.87 |  | 3.45 | 25.806
[7 empty] | 1007.3989 | Sqm
71 | Supply and application of one coat water based cement primer of interior grade I and two coats of water based PU paint having anti-bacterial applications content less than 50 grams/litre for internal walls including cost and conveyance of all materials to site, sales and other taxes, incidental, operational and all labour charges etc., and complete for finished item of work in 5th floor. at Gandhi Hospital
| Main Entry Corridor | 1 | 1 | 6.3 |  | 1.5 | 9.45
| main Entry Access Control Door | 1 | 1 | 3 |  | 1.5 | 4.5
| Door Deduction(-) | -1 | 1 | 1.5 |  | 2.6 | -3.9
| Corridor at Reception | 1 | 1 | 3 |  | 1.5 | 4.5
| Reception area | 1 | 2 | 3.4 |  | 1.5 | 10.2
| Record Room Main Door Wall | 1 | 2 | 3 |  | 3.05 | 18.3
| Door Jam | 1 | 1 | 5.2 | 0.15 |  | 0.78
| Door Deduction(-) | -1 | 1 | 1 |  | 2.1 | -2.1
| Record Room Inside | 1 | 2 | 3.2 |  | 1.5 | 9.6
| do | 1 | 1 | 3 |  | 1.5 | 4.5
| Window Deduction(-) | 1 | 1 | 1.8 |  | 1.4 | 2.52
| Wndow Jam | 1 | 1 | 5.4 | 0.15 |  | 0.81
| Ultra Sound Room Inside Long Wall | 1 | 2 | 4.505 |  | 3.05 | 27.4805
| Ultra Sound Room Inside Short Wall | 1 | 2 | 2.18 |  | 3.05 | 13.298
| Door Jam | 1 | 1 | 5.812 | 0.15 |  | 0.8718
| Door Deduction(-) | -1 | 1 | 1.215 |  | 2.3 | -2.7945
| Ventilator Deduction(-) | -1 | 1 | 0.45 |  | 0.45 | -0.2025
| Ventilator jam | 1 | 1 | 1.8 | 0.15 |  | 0.27
| Autoclave Room Inside Long Wall | 1 | 2 | 2.18 |  | 3.05 | 13.298
| Autoclave Room Inside Short Wall | 1 | 2 | 1.19 |  | 3.05 | 7.259
| Door deduction(-) | -1 | 1 | 1.21 |  | 2.37 | -2.8677
| Door Jam | 1 | 1 | 5.81 | 0.15 |  | 0.8715
| Toilet at Counseling Room 2 Inside Long Wall | 1 | 2 | 1.5 |  | 1.5 | 4.5
| Toilet at Counseling Room 2 Inside Short Wall Wall | 1 | 2 | 1.2 |  | 1.5 | 3.6
| Door Deduction(-) | 1 | 2 | 0.8 |  | 2.1 | 3.36
| Door Jam | 1 | 1 | 5 | 0.15 |  | 0.75
| Counseling Room 2 Inside Long Wall | 1 | 2 | 3.24 |  | 3.05 | 19.764
| Counseling Room 2 Inside Long Wall | 1 | 2 | 2.45 |  | 3.05 | 14.945
| Door jam | 1 | 1 | 5.47 | 0.15 |  | 0.8205
| Door Deduction(-) | -1 | 1 | 1.07 |  | 2.2 | -2.354
| Window Deduction(-) | -1 | 1 | 1.8 |  | 1.8 | -3.24
| Counseling Room 1 inside Long Wall | 1 | 2 | 3.24 |  | 3.05 | 19.764
| Counseling Room 1 inside Short Wall | 1 | 2 | 2.45 |  | 3.05 | 14.945
| Door Jam | 1 | 1 | 5.49 | 0.15 |  | 0.8235
| Door Deduction(-) | -1 | 1 | 1.09 |  | 2.2 | -2.398
| Corridor at Counseling Room 1 and 2 | 1 | 2 | 5.1 |  | 3.05 | 31.11
| do | 1 | 1 | 1.2 |  | 3.05 | 3.66
| Door Deductions(-) Counseling Room 2 | -1 | 1 | 1.09 |  | 2.2 | -2.398
| Door Deductions(-) Counseling Room 1 | -1 | 1 | 1.07 |  | 2.2 | -2.354
| Door Deductions(-) Auto Clave Room | -1 | 1 | 1.2 |  | 2.3 | -2.76
| Door Deductions(-) Altra Sound Room | -1 | 1 | 1.2 |  | 2.3 | -2.76
| Corridor at prepost Operative Wards | 1 | 2 | 6.3 |  | 1.5 | 18.9
| Door Deduction(-) | -1 | 1 | 1.49 |  | 1.5 | -2.235
| Corridor Deduction(-) | -1 | 1 | 1.2 |  | 2 | -2.4
| Prepost Operative Wards Inside Long Wall | 1 | 1 | 6.48 |  | 1.5 | 9.72
| Prepost Operative Wards Inside Long Wall | 1 | 1 | 4.38 |  | 1.5 | 6.57
| Prepost Operative Wards Inside Short Wall | 1 | 1 | 6 |  | 1.5 | 9
| Prepost Operative Wards Inside Short Wall | 1 | 1 | 4.8 |  | 1.5 | 7.2
| Door Deduction(-) | -1 | 1 | 1.49 |  | 2.5 | -3.725
| Door Jam | 1 | 1 | 6.49 | 0.23 |  | 1.4927
| Window Deduction(-) | -1 | 1 | 1.8 |  | 1.4 | -2.52
| Window Jam | 1 | 1 | 7.2 | 0.15 |  | 1.08
| Corridor At Semi Sterile Area | 1 | 2 | 6.45 |  | 2 | 25.8
| Corridor Opening Deductions(-) | -1 | 2 | 1.2 |  | 1.5 | -3.6
| Access Control Door at Semistearail Area | 1 | 2 | 3 |  | 3.05 | 18.3
| Door Deduction(-) | -1 | 2 | 1.5 |  | 2.6 | -7.8
| Door Jam | 1 | 1 | 6.7 | 0.23 |  | 1.541
| Corridor at Dr Change Room Long Wall | 1 | 2 | 4.7 |  | 3.05 | 28.67
| Corridor at Dr Change Room Short Wall | 1 | 2 | 4.68 |  | 3.05 | 28.548
| Corridor Opening Deductions(-) | 1 | 1 | 1.2 |  | 3 | 3.6
| Toilet Door Deduction(-) | -1 | 1 | 1 |  | 2.1 | -2.1
| Dr Toilet Inside | 1 | 2 | 4.68 |  | 1.5 | 14.04
| Dr Toilet Inside | 1 | 2 | 1.85 |  | 1.5 | 5.55
| Door Deduction(-) | -1 | 1 | 1 |  | 1.5 | -1.5
| Ventilator Deduction(-) | -1 | 1 | 0.45 |  | 0.45 | -0.2025
| Dr Change Room Partitions | 1 | 2 | 2.61 |  | 3.05 | 15.921
| Dr Change Room Partitions | 1 | 2 | 2.2 |  | 3.05 | 13.42
| Door Deductions(-) | -1 | 1 | 1 |  | 2.1 | -2.1
| Dr Change Room Partitions | 1 | 2 | 1.45 |  | 3.05 | 8.845
| Dr Change Room Partitions | 1 | 2 | 1.45 |  | 3.05 | 8.845
| Corridor at Manifold Room | 1 | 2 | 3.3 |  | 3.05 | 20.13
| Corridor at Manifold Room | 1 | 1 | 1.2 |  | 3.05 | 3.66
| Door Deductions(-) | -1 | 1 | 1.08 |  | 2.3 | -2.484
| Door Deductions(-) | -1 | 1 | 0.986 |  | 2.2 | -2.1692
| Manifold Room Inside Long Walls | 1 | 2 | 3.185 |  | 3.05 | 19.4285
| Manifold Room Inside Short Walls | 1 | 2 | 2.13 |  | 3.05 | 12.993
| Door Deductions(-) | -1 | 1 | 1.01 |  | 2.3 | -2.323
| Door Jam | 1 | 1 | 5.61 | 0.15 |  | 0.8415
| Change Room walls | 3 | 2 | 1.87 |  | 3.05 | 34.221
| Change Room wall | 1 | 1 | 5.2 |  | 1.5 | 7.8
| Corridor at Blood Collection Room | 1 | 1 | 5.2 |  | 3.05 | 15.86
| Door Deductions(-) | -1 | 1 | 0.998 |  | 2.1 | -2.0958
| Door Deductions(-) | -1 | 1 | 0.999 |  | 2.1 | -2.0979
| Store Room Inside Long Wall | 1 | 1 | 3.3 |  | 3.05 | 10.065
| Store Room Inside Long Wall | 1 | 1 | 3.3 |  | 2.4 | 7.92
| Store Room Inside Short Wall | 1 | 2 | 2.5 |  | 3.05 | 15.25
| Door Deductions(-) | -1 | 1 | 1 |  | 2.1 | -2.1
| Partition Wall Top | 1 | 1 | 3.3 | 0.15 |  | 0.495
| Blood Collection Room Long Wall | 1 | 2 | 3.3 |  | 2.4 | 15.84
| Blood Collection Room Short Wall | 1 | 2 | 2.5 |  | 3.05 | 15.25
| Door Deductions(-) | -1 | 1 | 1 |  | 2.1 | -2.1
| Tartition Wall Top | 1 | 1 | 3.3 | 0.15 |  | 0.495
| Sperm Collection Inside Long Wall | 1 | 1 | 3.3 |  | 2.4 | 7.92
| Sperm Collection Inside Long Wall | 1 | 1 | 3.3 |  | 3.05 | 10.065
| Sperm Collection Inside Short Wall | 1 | 2 | 3.265 |  | 3.05 | 19.9165
| Door Deductions(-) | -1 | 1 | 0.8 |  | 2.1 | -1.68
| Door Deductions(-) | -1 | 1 | 1 |  | 2.1 | -2.1
| Sperm Collection Toilet inside | 1 | 2 | 1.6 |  | 1.5 | 4.8
| Sperm Collection Toilet inside | 1 | 2 | 1.1 |  | 1.5 | 3.3
| Door Deductions(-) | -1 | 1 | 0.8 |  | 1.5 | -1.2
| Ventilator Deduction(-) | -1 | 1 | 0.45 |  | 0.45 | -0.2025
| Corridor at Sterile area | 1 | 2 | 6.3 |  | 1.5 | 18.9
| Corridor at Sterile area | 1 | 1 | 3 |  | 1.5 | 4.5
| Door Deductions(-) Minor OT | -1 | 1 | 1.5 |  | 1.5 | -2.25
| Door Deductions(-) Major OT | -1 | 1 | 1.5 |  | 1.5 | -2.25
| Door Deductions(-) Andrology Lab | -1 | 1 | 1.5 |  | 1.5 | -2.25
| Door Deductions(-) Emergency Exit | -1 | 1 | 1.8 |  | 1.5 | -2.7
| Minor OT Inside Long Walls | 1 | 2 | 6.4 |  | 3.05 | 39.04
| Minor OT Inside Short Walls | 1 | 2 | 4.2 |  | 3.05 | 25.62
| Door Deductions(-) | -1 | 1 | 1.5 |  | 2.6 | -3.9
| Pass box Opening (-) | -1 | 1 | 0.6 |  | 0.6 | -0.36
| Androlry Lab Long Walls Inside | 1 | 2 | 4.25 |  | 3.05 | 25.925
| Androlry Lab Short Walls Inside | 1 | 2 | 4.08 |  | 3.05 | 24.888
| Door Deductions(-) | -1 | 1 | 1.5 |  | 2.6 | -3.9
| Door Deductions(-) | -1 | 1 | 1 |  | 2.1 | -2.1
| Cryo Room Inside | 1 | 2 | 3 |  | 3.05 | 18.3
| do | 1 | 2 | 1.6 |  | 3.05 | 9.76
| Door Deductions | -1 | 1 | 1 |  | 2.1 | -2.1
| Staire Case area | 1 | 1 | 4.2 |  | 1.5 | 6.3
| Staire Case area | 1 | 2 | 4.2 |  | 1.5 | 12.6
| Window Deduction(-) | -1 | 1 | 1.8 |  | 1.5 | -2.7
| Dr. Change Room | 2 | 2 | 2.2 |  | 3.45 | 30.36
| Store Room | 1 | 2 | 3.18 |  | 3.45 | 21.942
| do | 1 | 2 | 2.18 |  | 3.45 | 15.042
| Door Deduction(-) | -1 | 2 | 0.8 |  | 2.1 | -3.36
| Change Rooms | 2 | 2 | 1.87 |  | 3.45 | 25.806
[7 empty] | 872.0934 | Sqm
67 | Providing and fixing in true horizontal level 14 mm - Mineral Fiber sheet 595 x 595 Square / Tegular Fissura fine model edge tiles with a Humidity Resistance of 90percentage RH, Average NRC 0.50, Light Reflectance greater than80percentage, Thermal Conductivity equal to 0.052 to 0.057 w/mk, Fire Performance Class 0/Class 1 using hot dipped Galvanized Steel section exposed surface with pre-coated capping, main Tee of size 24 x 32 mm at every 1200 mm c/c maximum and rotary stitched cross tee of size 24 x 27 mm at every 600 mm c/c and sub-cross tee of size 24 mm x 25 mm at 1200 mm c/c and wall angle of size 19 x 19 mm fixed to periphery of the wall and the above grid is suspended at every 1200 mm c/c in both directions using 2.0 mm thick pre-straightened GI Wire including cost and conveyance of all materials and labour charges such as cutting , fixing of standing of frame work exposing roof making etc., complete for finished item of work in 5th floor. at Gandhi Hospital
| Main Entry Corridor | 1 | 1 | 6.3 | 2.94 |  | 18.522
| Corridor at Reception | 1 | 1 | 3 | 3 |  | 9
| Reception | 1 | 1 | 3.4 | 3 |  | 10.2
| Record Room | 1 | 1 | 3.2 | 3 |  | 9.6
| Corridor at Prepost Operative Wards | 1 | 1 | 6.3 | 3 |  | 18.9
| Corridor at Counseling Room 1 and 2 | 1 | 1 | 5.1 | 1.2 |  | 6.12
| do | 1 | 1 | 0.4 | 0.1 |  | 0.04
| Toilet | 1 | 1 | 1.5 | 1.2 |  | 1.8
| Ultra Sound Room | 1 | 1 | 3.2 | 3 |  | 9.6
| Auto Clave Room | 1 | 1 | 2.18 | 1.9 |  | 4.142
| Counseling Room 2 | 1 | 1 | 3.24 | 2.4 |  | 7.776
| Counseling Room 1 | 1 | 1 | 3.2 | 2.45 |  | 7.84
| Prepost Operative Wards | 1 | 1 | 6.48 | 6 |  | 38.88
| Toilet Area Deduction(-) | -1 | 1 | 2 | 2.1 |  | -4.2
| Column Deduction(-) | -1 | 1 | 0.53 | 0.53 |  | -0.2809
| Toilet | 1 | 1 | 1.7 | 1.2 |  | 2.04
| Corridor At Semi Sterile Area | 1 | 1 | 6.45 | 3 |  | 19.35
| Dr Chganhe Room | 1 | 1 | 4.7 | 4.68 |  | 21.996
| do | 1 | 1 | 4.8 | 0.1 |  | 0.48
| Dr Toilet | 1 | 1 | 4.68 | 1.85 |  | 8.658
| Change Room Area | 1 | 1 | 6.45 | 3.07 |  | 19.8015
| Store Room | 1 | 1 | 3.3 | 2.58 |  | 8.514
| Blood Collection Room | 1 | 1 | 3.3 | 2.58 |  | 8.514
| Sperm Collection Room | 1 | 1 | 3.3 | 3.27 |  | 10.791
| Sterm Collection Toilet | 1 | 1 | 1.6 | 1.1 |  | 1.76
| Manifold Room | 1 | 1 | 3.185 | 2.13 |  | 6.784
| Deductions Column | -1 | 1 | 0.68 | 0.68 |  | -0.4624
| Minor OT | 1 | 1 | 6.4 | 4.2 |  | 26.88
| Corridor at Sterile area | 1 | 1 | 6.3 | 3 |  | 18.9
| Scrub Area | 1 | 1 | 3.53 | 0.68 |  | 2.4004
| Andrology Lab | 1 | 1 | 4.13 | 4.1 |  | 16.933
| Cryo room | 1 | 1 | 3 | 1.6 |  | 4.8
[7 empty] | 316.0786 | Sqm
93 | Providing Laying of scratch proof PVC/vinyl flooring of 2mm thickness with proper welded joints air tight along with leveling compound to match the existing flooring levels as per the engineer in charge instructions. Sub floor preparation with self leveling compound. After the sub floor preparation, it should be suitable for ESD Flooring.Rate inclusive of sifting of material and labour charges.at Gandhi Hospital
| Minor OT | 1 | 1 | 6.4 | 4.2 |  | 26.88
| Door Mat | 1 | 1 | 1.5 | 0.23 |  | 0.345
| Corridor at Sterile area | 1 | 1 | 6.3 | 3 |  | 18.9
| Deductions Air Shower(-) | -1 | 1 | 0.5 | 1.71 |  | -0.855
| Major OT | 1 | 1 | 6.48 | 4.05 |  | 26.244
| Door mat | 1 | 1 | 1.5 | 0.23 |  | 0.345
| do | 1 | 1 | 0.39 | 1.5 |  | 0.585
| Embrology Lab | 1 | 1 | 6.48 | 4.3 |  | 27.864
| Door mat | 1 | 1 | 1.5 | 0.1 |  | 0.15
| Scrub Area | 1 | 1 | 3.53 | 0.68 |  | 2.4004
| Andrology Lab | 1 | 1 | 4.13 | 4.1 |  | 16.933
| Door Mat | 1 | 1 | 1.5 | 0.1 |  | 0.15
| Cryo room | 1 | 1 | 3 | 1.6 |  | 4.8
| Door mat | 1 | 1 | 1 | 0.1 |  | 0.1
[7 empty] | 124.8414 | Sqm
160 | SITC of Factory fabricated and boxed ducting using Aluminium Sheets / coils, should be fabricated as per SMACNA, galvanised hardware and supports, silicon sealant at all longitudinal joints, Galvanized /GI Electroplated iron angle flanges for all the joints, bracing angles and minimum 5mm thick neoprene rubber gasket.- Duct pressure testing at 75mm to be carried oubefore insulatiting the duct. pressure testing to be done as per SMACNA. Procedure to be approved by consultant. 22G - 0.8 mm Thick at Gandhi Hospital
| Supply Duct 650 x 350 mm Terrace to Out side IVF OT | 1 | 6 | 1.23 | 2 |  | 14.76
| Elbow 650 x 350 mm | 1 | 1 | 0.95 | 2 |  | 1.9
| Straight 650 x 350 mm | 1 | 1 | 0.75 | 2 |  | 1.5
| Straight 650 x 350 mm | 1 | 8 | 1.23 | 2 |  | 19.68
| Elbow 650 x 350 mm OT Entry | 1 | 1 | 0.95 | 2 |  | 1.9
| Straight 650 x 350 mm OVF OT Inside | 1 | 7 | 1.23 | 2 |  | 17.22
| Straight 650 x 350 mm OVF OT Inside | 1 | 1 | 0.75 | 2 |  | 1.5
| Straight 650 x 350 mm OVF OT Inside | 1 | 1 | 1.05 | 2 |  | 2.1
| Straight 650 x 350 mm OVF OT Inside | 1 | 2 | 0.65 | 2 |  | 2.6
| Straight 200 x 350 mm OVF OT Inside | 1 | 1 | 0.65 | 1.1 |  | 0.715
| Dummy IVF OT 300 x 475mm | 1 | 1 | 0.3 |  | 0.45 | 0.135
| Embryology Supply 475 x 350 x 475 x 300 mm Tapper | 1 | 1 | 1.1 | 1.55 |  | 1.705
| Straight 475 x 300 mm Inside | 1 | 2 | 1.23 | 1.5 |  | 3.69
| Straight 475 x 300 mm Inside | 1 | 1 | 0.9 | 1.5 |  | 1.35
| Straight 650 x 300 mm Inside | 1 | 1 | 0.65 | 1.9 |  | 1.235
| Straight 250 x 300 mm Inside | 1 | 1 | 0.65 | 1.1 |  | 0.715
| Straight 300 x 300 x 300 x 175 mm Inside | 1 | 1 | 0.9 | 1.05 |  | 0.945
| Dummy 400 x 400 mm | 1 | 1 | 0.4 |  | 0.4 | 0.16
| Straight 350 x 300 mm | 1 | 1 | 1.23 | 1.3 |  | 1.599
| Straight 350 x 300 mm | 1 | 1 | 0.65 | 1.3 |  | 0.845
| Straight 350 x 300 mm | 1 | 1 | 1.43 | 1.3 |  | 1.859
| Dummy 475 x 400mm | 1 | 1 | 0.45 |  | 0.4 | 0.18
| Return Duct Terrace to IVF OT Out side 750 x 300 mm | 1 | 4 | 1.23 | 2.1 |  | 10.332
| Elbow 750 x 300 mm Out Side | 1 | 1 | 1.05 | 2.1 |  | 2.205
| Straight 750 x 300 mm Outside | 1 | 4 | 1.23 | 2.1 |  | 10.332
| Elbow 750 x 300 mm Out Side | 1 | 1 | 1.05 | 2.1 |  | 2.205
| Straight 750 x 300 mm Outside | 1 | 8 | 1.23 | 2.1 |  | 20.664
| Elbow 750 x 300 mm Out Side | 1 | 1 | 1.05 | 2.1 |  | 2.205
| Lab Entry Straight 750 x 300 mm | 1 | 9 | 1.23 | 2.1 |  | 23.247
| Straight 750 x 300 mm Embryology Inside | 1 | 1 | 0.7 | 2.1 |  | 1.47
| Tapper 750 x 300 x 525 x 300 mm | 1 | 1 | 0.9 | 1.85 |  | 1.665
| Straight 525 x 300 mm Embryology Inside | 1 | 4 | 1.23 | 1.6 |  | 7.872
| Straight 525 x 300 mm IVF OT Inside | 1 | 1 | 0.7 | 1.6 |  | 1.12
| Elbow 525 x 300 IVF OT Inside | 1 | 1 | 0.65 | 1.6 |  | 1.04
| Straight 525 x 300 mm IVF OT Inside | 1 | 4 | 1.23 | 1.6 |  | 7.872
| Straight 525 x 300 mm IVF OT Inside | 1 | 2 | 0.7 | 1.6 |  | 2.24
| Straight 625 x 175 mm IVF OT Inside | 1 | 6 | 2.67 | 1.5 |  | 24.03
| Modular Connections Embryology Lab 650 x 250 mm | 1 | 3 | 1.9 | 1.8 |  | 10.26
| Modular Connections IVF OT 650 x 250 mm | 1 | 3 | 1.9 | 1.8 |  | 10.26
| Riser Connection Embryology Lab 800 x 175 mm | 1 | 3 | 1.13 | 1.9 |  | 6.441
| Riser Connection IVF OT 800 x 175 mm | 1 | 3 | 1.13 | 1.9 |  | 6.441
[7 empty] | 230.194 | Sqm
156 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Suction Line at Gandhi Hospital
| From AHU to Condensing Unit | 1 | 1 | 12 |  |  | 12
[7 empty] | 12 | Rmt
155 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Liquid Line at Gandhi Hospital
| From AHU to Condensing Unit | 1 | 1 | 10 |  |  | 10
[7 empty] | 10 | Rmt
158 | SITC of CPVC drain ping with supports, clamps and 9 mm thk. Nitrile rubber tube insulation of the following sizes. Insulation shall have factory laminated glass cloth. 25mm Dia at Gandhi Hospital
| AHU Drain Outlet to Near Rain Water Pipe | 1 | 1 | 12 |  |  | 12
[7 empty] | 12 | Rmt
161 | Aluminium low leakage aerofoil design volume control dampers Suitable for manual and motorised operation At Gandhi Hospital
| AHU return 800 x 400 x 200 mm | 1 | 1 | 0.2 | 2.4 |  | 0.48
| AHU Supply 700 x 400 x 200 | 1 | 1 | 0.2 | 2.2 |  | 0.44
| AHU Fresh Air 400 x 400 x 200 mm | 1 | 1 | 0.2 | 1.6 |  | 0.32
[7 empty] | 1.24 | Sqm
162 | CBRI approved 16G GI Spring return actuated fire dampers rated for 90 minutes with limit switch. At Gandhi Hospital
| AHU Return Air Damper 750 x 350 x 200mm | 1 | 1 | 0.2 | 2.2 |  | 0.44
| AHU Supply 650 x 350 x 200 mm | 1 | 1 | 0.2 | 2 |  | 0.4
[7 empty] | 0.84 | Sqm
163 | SITC of SS perforated return raiser grilles with 10 microns filters with collar dampers At Gandhi Hospital
| IVF-OT SS Perforated 740 x 740 mm (Dummy) | 1 | 3 | 0.74 |  | 0.74 | 1.6428
| Embryology SS Perforated 740 x 740 mm (Dummy) | 1 | 3 | 0.74 |  | 0.74 | 1.6428
[7 empty] | 3.2856 | Sqm
164 | Extruded Al. powder coated EXHAUST / RETURN discrete grilles At Gandhi Hospital
| IVF-OT 630 x 330 mm (Dummy) | 1 | 3 | 0.63 |  | 0.33 | 0.6237
| Embryology 630 x 330 mm (Dummy) | 1 | 3 | 0.63 |  | 0.33 | 0.6237
[7 empty] | 1.2474 | Sqm
165 | SITC of Collar Dampers made of Al. extrusions with black powder coating for Grilles / Diffusers At Gandhi Hospital
| IVF-OT 800x 175 mm (Dummy) | 1 | 3 | 0.8 |  | 0.15 | 0.36
| Embryology 800 x 175 mm (Dummy) | 1 | 3 | 0.8 |  | 0.15 | 0.36
[7 empty] | 0.72 | Sqm
168 | SITC of Aluminium powder coated Fresh air and Exhaust Louvers of nonvision type with nylon mosquito net etc. At Gandhi Hospital
| Terrace Dresh Air Exhaust Louver 350 x 350 mm | 1 | 1 | 0.35 |  | 0.35 | 0.1225 | Sqm
169 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 32mm Thick for Exposed Supply Air duct and finished with UV Protective Paint. at Gandhi Hospital
| Supply Duct 682 x 382 mm Terrace to Out side IVF OT | 1 | 6 | 1.43 | 2.252 |  | 19.3222
| Elbow 682 x 382 mm | 1 | 1 | 1.15 | 2.252 |  | 2.5898
| Straight 682 x 382 mm | 1 | 1 | 0.95 | 2.252 |  | 2.1394
| Straight 682 x 382 mm | 1 | 8 | 1.43 | 2.252 |  | 25.7629
| Elbow 682 x 382 mm OT Entry | 1 | 1 | 1.15 | 2.252 |  | 2.5898
| Straight 682 x 382 mm OVF OT Inside | 1 | 7 | 1.43 | 2.252 |  | 22.5425
| Straight 682 x 382 mm OVF OT Inside | 1 | 1 | 0.95 | 2.252 |  | 2.1394
| Straight 682 x 382 mm OVF OT Inside | 1 | 1 | 1.15 | 2.252 |  | 2.5898
| Straight 682 x 382 mm OVF OT Inside | 1 | 2 | 0.85 | 2.252 |  | 3.8284
| Straight 232 x 382 mm OVF OT Inside | 1 | 1 | 0.85 | 1.412 |  | 1.2002
| Modular Connections Embryology Lab 714 x 314 mm | 1 | 3 | 1.9 | 1.8 |  | 10.26
| Modular Connections IVF OT 714 x 314 mm | 1 | 3 | 1.9 | 1.8 |  | 10.26
| Riser Connection Embryology Lab 864 x 214 mm | 1 | 3 | 1.13 | 2.156 |  | 7.3088
| Riser Connection IVF OT 864 x 214 mm | 1 | 3 | 1.13 | 2.156 |  | 7.3088
[7 empty] | 119.842 | Sqm
170 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Exposed Return Air Duct and finished with UV Protective Paint. at Gandhi Hospital
| Return Duct Terrace to IVF OT Out side 750 x 325 mm | 1 | 4 | 1.33 | 2.3 |  | 12.236
| Elbow 750 x 325 mm Out Side | 1 | 1 | 1.15 | 2.3 |  | 2.645
| Straight 750 x 325 mm Outside | 1 | 4 | 1.33 | 2.3 |  | 12.236
| Elbow 750 x 325 mm Out Side | 1 | 1 | 1.15 | 2.3 |  | 2.645
| Straight 750 x 325 mm Outside | 1 | 8 | 1.33 | 2.3 |  | 24.472
| Elbow 750 x 325 mm Out Side | 1 | 1 | 1.15 | 2.3 |  | 2.645
| Lab Entry Straight 750 x 325 mm | 1 | 9 | 1.33 | 2.3 |  | 27.531
[7 empty] | 84.41 | Sqm
171 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Supply air duct running inside the building. at Gandhi Hospital
| Dummy IVF OT 325 x 475mm | 1 | 1 | 0.325 |  | 0.475 | 0.15437
| Embryology Supply 475 x 350 x 475 x 325 mm Tapper | 1 | 1 | 1.2 | 1.75 |  | 2.1
| Straight 475 x 325 mm Inside | 1 | 2 | 1.33 | 1.7 |  | 4.522
| Straight 475 x 325 mm Inside | 1 | 1 | 1 | 1.7 |  | 1.7
| Straight 650 x 325 mm Inside | 1 | 1 | 0.75 | 2.1 |  | 1.575
| Straight 250 x 325 mm Inside | 1 | 1 | 0.75 | 1.3 |  | 0.975
| Straight 325 x 325 x 325 x 175 mm Inside | 1 | 1 | 1 | 1.25 |  | 1.25
| Dummy 425 x 425 mm | 1 | 1 | 0.425 |  | 0.425 | 0.18062
| Straight 350 x 325 mm | 1 | 1 | 1.33 | 1.5 |  | 1.995
| Straight 350 x 325 mm | 1 | 1 | 0.75 | 1.5 |  | 1.125
| Straight 350 x 325 mm | 1 | 1 | 1.53 | 1.5 |  | 2.295
| Dummy 475 x 425mm | 1 | 1 | 0.475 |  | 0.425 | 0.20187
| Straight 750 x 325 mm Embryology Inside | 1 | 1 | 0.8 | 2.3 |  | 1.84
| Tapper 750 x 325 x 525 x 325 mm | 1 | 1 | 1 | 2.05 |  | 2.05
| Straight 525 x 325 mm Embryology Inside | 1 | 4 | 1.33 | 1.8 |  | 9.576
| Straight 525 x 325 mm IVF OT Inside | 1 | 1 | 0.8 | 1.8 |  | 1.44
| Elbow 525 x 325 IVF OT Inside | 1 | 1 | 0.75 | 1.8 |  | 1.35
| Straight 525 x 325 mm IVF OT Inside | 1 | 4 | 1.33 | 1.8 |  | 9.576
| Straight 525 x 325 mm IVF OT Inside | 1 | 2 | 0.8 | 1.8 |  | 2.88
| Straight 625 x 175 mm IVF OT Inside | 1 | 6 | 2.77 | 1.7 |  | 28.254
[7 empty] | 75.0399 | Sqm
172 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 19mm Thick for Return air running inside the building. at Gandhi Hospital
| TDF Flange Insulation at Embryology Lab | 1 | 16 | 1.5 | 0.2 |  | 4.8 | Sqm
| TDF Flange Insulation at IVF-OT | 1 | 16 | 1.9 | 0.2 |  | 6.08 | Sqm
| TDF Flange Insulation at Exposed Area | 1 | 22 | 1.9 | 0.2 |  | 8.36 | Sqm
[7 empty] | 19.24 | Sqm
87 | Supply and instalaion of Wall Panels 80mm thick double skin Modular wall panels made of .8mm Powder Coated GI on both sides, with 40 plus or minus 2 kg/cum demsity pUF as infill, GI profiles all along the periphery,flush on both sides with maximum allowable gap of 3-4mm filled with food grade silicon sealent and placed on cold rolled galvanised bottom tracks with a recess to provide floor to wall coving flush with the wall panel. This including all required hardware for completion panels to be covered with a protective film to avoid any damages during transpotation and installation at Gandhi Hispital
| IVF Ot Long Walls RHS | 1 | 1 | 6.17 |  | 2.55 | 15.7335
| Door Deduction(-) | -1 | 1 | 1.5 |  | 2.55 | -3.825
| Long Wall LHS | 1 | 1 | 6.17 |  | 2.55 | 15.7335
| Short Walls | 1 | 1 | 3.65 |  | 2.55 | 9.3075
| Short Wall Main Door Wall | 1 | 1 | 4.02 |  | 2.55 | 10.251
| Door Deduction(-) | -1 | 1 | 1.48 |  | 2.55 | -3.774
| Sides | 1 | 1 | 0.39 |  | 2.55 | 0.9945
| Door Sides | 1 | 2 | 0.32 |  | 2.55 | 1.632
| Embryology Lab Long Walls | 1 | 2 | 6.21 |  | 2.55 | 31.671
| Door Deduction(-) | -1 | 1 | 1.5 |  | 2.55 | -3.825
| Short Walls | 1 | 2 | 3.97 |  | 2.55 | 20.247
| Air Shower Sides | 1 | 2 | 0.5 |  | 2.6 | 2.6
[7 empty] | 96.746 | Sqm
88 | Supply and installtion of 50mm thick double skin cealing system made .8mm thich powder coated GI sheet on both sides, 40 plus or minus 2kg/cum density PUF ad infill, GI Profiles all along the periphery, panels flush towards room sides with maximum allowable gap of 3-4mm at panelto panel joints filled with silicon sealent ceiling panels are suspended from the RCC salb bu using concealed Aall ceiling grid with tie rod and adjestable turn bickle arrangement etc. This includes all required hardware for completition. panels to be covered with a protective film to avoid any damge during transpotation and installation at Gandhi Hospital.
| IVF OT | 1 | 1 | 6.17 | 3.65 |  | 22.5205
| do | 1 | 1 | 1.5 | 0.39 |  | 0.585
| do | 1 | 1 | 1.48 | 0.32 |  | 0.4736
| Columns Deduction(-) | -1 | 1 | 0.55 | 0.39 |  | -0.2145
| Embryology lab | 1 | 1 | 6.21 | 3.97 |  | 24.6537
[7 empty] | 48.0183 | Sqm
92 | Supply and installation of Extruded Aluminium Coving at Gndhi Hopital
| IVF Ot Long Walls RHS | 1 | 1 | 4.3 |  |  | 4.3
| do | 1 | 1 | 1.5 |  |  | 1.5
| do | 1 | 1 | 0.39 |  |  | 0.39
| Long Wall LHS | 1 | 1 | 6.16 |  |  | 6.16
| Sort Wall Main Door | 1 | 1 | 0.6 |  |  | 0.6
| do | 1 | 2 | 0.32 |  |  | 0.64
| do | 1 | 1 | 1 |  |  | 1
| do | 1 | 1 | 0.39 |  |  | 0.39
| do | 1 | 1 | 0.91 |  |  | 0.91
| Vertical Coving | 1 | 4 | 2.41 |  |  | 9.64
| Embryology Lab Long Walls | 1 | 2 | 6.21 |  |  | 12.42
| Short Walls | 1 | 2 | 3.97 |  |  | 7.94
| Vertical Coving | 1 | 4 | 2.42 |  |  | 9.68
| Pass Box Sides | 1 | 3 | 2.68 |  |  | 8.04
[7 empty] | 63.61 | Rmt
90 | Single leaf clean room door 46mm thick flush made of .8mm thick powedr coated GI sheet on both sides 90 pus or minus 2kg/cum density honeycomb with stand upto 220 deg.C temperature ,and compressible strength upto 400 kg/sqm,1.2mm thick GPSP door frames ,double glazed vision panel with necessary adhesive tapes and silicon swalent, necessary hardware like SS304 ball bearing butt hinges D- hnadles,push plates ,Dorma make door closer concealed tower bolt ,drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms,BOth sides lock and key etc,. Complete .
| UPS Room (990 x 2280mm) | 1 | 1 |  |  |  | 1
| Cryo Room(1000 x 2250mm) | 1 | 1 |  |  |  | 1
| Auto Clave Room Single Shutter(980 x 2260mm) | 1 | 1 |  |  |  | 1
[7 empty] | 3 | Nos
89 | Double leaf clean room door 46mm thick flush made of .8mm thick powedr coated GI sheet on both sides 90 pus or minus 2kg/cum density honeycomb with stand upto 220 deg.C temperature ,and compressible strength upto 400 kg/sqm,1.2mm thick GPSP door frames ,double glazed vision panel with necessary adhesive tapes and silicon swalent, necessary hardware like SS304 ball bearing butt hinges D- hnadles,push plates ,Dorma make door closer concealed tower bolt ,drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms,BOth sides lock and key etc,. Complete .
| Access Control Door (1490 x 2570mm) | 1 | 1 |  |  |  | 1
| Minor OT Door(1490 x 2570mm) | 1 | 1 |  |  |  | 1
| IVF OT Door (1450 x 2550mm) | 1 | 1 |  |  |  | 1
| Embryology lab Door(1500 x 2400mm) | 1 | 1 |  |  |  | 1
| Andrology Lab Door (1490 x 2580mm) | 1 | 1 |  |  |  | 1
[7 empty] | 5 | Nos
91 | Emergency Fire door 46mm thick flush made of .8mm thick powedr coated GI sheet on both sides 90 pus or minus 2kg/cum density honeycomb with stand upto 220 deg.C temperature ,and compressible strength upto 400 kg/sqm,1.2mm thick GPSP door frames ,double glazed vision panel with necessary adhesive tapes and silicon swalent, necessary hardware like SS304 ball bearing butt hinges D- hnadles,push plates ,Dorma make door closer concealed tower bolt ,drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms,BOth sides lock and key etc,. Complete .
| Emergency Fire Door(1730 x 2610mm) | 1 | 1 |  |  |  | 1 | Nos
61 | Supplying and fixing of Unplasticised Poly Vinyl Chloride UPVC 3 track sliding windows with mesh shutter – 2-glass shutters and 1-mesh shutter duly manufactured using UPVC reinforced profiles Composition of profile shall consists a minimum of 5.5 PHR of TiO2 and not more than 12 PHR of CaCo3 for every 100 parts of PVC resin of 94mm x 45 mm/80 mm x 52 mm x 2.20 mm for outer frames, 58 mm x 39 mm/54 mm x 38 mm x 2.20mm for sliding shutter frames capable of mounting single glazing system structurally reinforced with hot dip galvanized up to 50 microns of minimum thickness of 1.0/1.2 mm prefabricated and welded through fusion welding. The window sash shall be fitted with 5 mm thick clear float glass of reputed make and mesh shutter frame shall be 42 mm 25mm/52 mm x 21.5 mm x 2.0 mm fitted with Vinyl Coated Fiber mesh- on rollers/ pulley duly fixed with Grey colour TPV Gasket for sash and Glazing bead shall be co extruded with Grey colour soft PVC. System shall have single point locking with Touch Lock and the system is to be installed at the site using anchor fasteners, silicon rubber sealant, easy glazing/deglazing at site etc., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site includingetc., complete for finished item of work. at Gandhi Hospital
| UPS Room | 1 | 1 | 1.5 |  | 1.8 | 2.7
| Sperm Collection and Blood Collection | 1 | 1 | 3.05 |  | 0.4 | 1.22
| Blood Collection and Autoclave Room | 1 | 1 | 3.15 |  | 0.4 | 1.26
| Prepost Operative Wards | 1 | 1 | 1.5 |  | 1.8 | 2.7
[7 empty] | 7.88 | Sqm
62 | Providing, supplying and fixing of Fixed Louvered Ventilator made out of multi chambered uPVC sections with Glazing bead shall be co-extruded with Grey colour soft PVC. having isolated drainage and reinforced with Galvanized Iron profiles throughout the window. The outer frame having an overall size of 60 mm x 55 mm x 2.40 with reinforcement of 1 mm thickness and Mullion with overall size of 74 mm x 60 mm x 2.40 mm with reinforcement of 1 mm thickness. Composition of profile shall consists a minimum of 5.5 PHR of TiO2 and not more than 12 PHR of CaCo3 for every 100 parts of PVC resin. Ventilator shall be provided with 4.5 mm Pin Head glass, standard hardware. Wall thickness of frame and Mullion shall be 2.4 mm., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site etc., complete for finished item of work hinges IS:205 150mm long, 1 No. aldrop IS:2681 300mm long, 1 No. tower bolt IS:204 of 200 mm x 10 mm dia at top, 2 Nos. 150 mm at Gandhi Hospital
| Counseling Room | 1 | 1 | 0.585 |  | 0.5 | 0.2925
| Manifold Room | 1 | 1 | 0.585 |  | 0.505 | 0.29542
| Pre/post Operative Ward Toilet | 1 | 1 | 0.599 |  | 0.514 | 0.30789
| Dr. Toilet | 1 | 1 | 0.601 |  | 0.561 | 0.33716
| Cryo Room | 1 | 1 | 0.593 |  | 0.5 | 0.2965
[7 empty] | 1.5295 | Sqm
77 | Supplying and fixing of SWR PVC pipes (Prince/Sudhakar/Kisan/Supreme or any ISI brand) 4 Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, overheads & contractors profit complete for finished item of work at all floor levels. (APSS No. 1302 1319 & 1326)
110mm dia
| Prepost Operative wards | 1 | 1 | 4.5 |  |  | 4.5
| Toilet At Counseling Room2 | 1 | 1 | 4.8 |  |  | 4.8
| Dr. Toilet | 1 | 1 | 5.6 |  |  | 5.6
| Sperm Collection Room | 1 | 1 | 4.2 |  |  | 4.2
| Scrub Wastewater Line | 1 | 1 | 7.53 |  |  | 7.53
[7 empty] | 26.63 | Rmt
75 | Supply and fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings SDR 13.5 to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" to 2") for hot and cold water (IS 15778:2007) including cost and conveyance of all materials to site, labour charges for fixing, overheads & contractors profit complete for finished item of work at all floor levels.
22.20 mm OD pipe
| Prepost Operative wards | 1 | 1 | 6.8 |  |  | 6.8
| Toilet At Counseling Room2 | 1 | 1 | 5.4 |  |  | 5.4
| Dr. Toilet | 1 | 1 | 10.7 |  |  | 10.7
| Sperm Collection Room | 1 | 1 | 4.8 |  |  | 4.8
| Scrub Inlet Line | 1 | 1 | 7.9 |  |  | 7.9
| Ro Inlet | 1 | 1 | 3.9 |  |  | 3.9
| VRV Drain pipe Major OT to out Side | 1 | 1 | 5.2 |  |  | 5.2
| VRV Drain pipe Major OT to out Side | 1 | 1 | 4.9 |  |  | 4.9
| Prepost Operative 3.0 TR Drain | 1 | 1 | 20.3 |  |  | 20.3
| Andrology Lab, Cryo Room to Toilet | 1 | 1 | 11.4 |  |  | 11.4
| Sperm Collection Room To Toilet | 1 | 1 | 1.2 |  |  | 1.2
| Blood Colletin Room To Toilet | 1 | 1 | 6.2 |  |  | 6.2
| Counseling Room1 ,2 to Toilet | 1 | 1 | 8.2 |  |  | 8.2
| Ultra Sound Room to Toilet | 1 | 1 | 2.3 |  |  | 2.3
| Split AC 2.0 Tr Drain | 1 | 1 | 6.2 |  |  | 6.2
[7 empty] | 98.6 | Rmt
81 | Supply, installation and commissioning approved make floor mounted Anglo Indian wash down EWC conforming to IS: 2556 part8-2004 suit with P or S trap with dual flush porcelain cistren fixed on wash down EWC with all intenal parts of dual flush cistren. ultra solid seat cover of approved make with rubber buffer and cap and 15mm angle stop cock and 450mm long PVC iner connection pipe wall flanges all of approved make etc. Complete for finished item of work
| Prepost Operative wards | 1 | 1 |  |  |  | 1
| Toilet At Counseling Room2 | 1 | 1 |  |  |  | 1
| Dr. Toilet | 1 | 1 |  |  |  | 1
| Sperm Collection Room | 1 | 1 |  |  |  | 1
[7 empty] | 4 | Nos
80 | Supplying and fixing Indian make Flat Back Wash Hand Basin 1st quality conforming to IS:2556-Part-4:1972 of size 550mm x 400mm with 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make heavy duty complete with standard CI brackets including wooden blocks ,1 No.12.70mm PVC connection with brass union nuts CP coated , angle stop cock 12.70mm dia. first quality Indian make heavy duty, 30mm dia. PVC flexible waste pipe 914.4mm length of 1st quality including cost and conveyance of all materials to site, labour charges , overheads & contractors profit for finished item of work.
| Prepost Operative wards | 1 | 1 |  |  |  | 1
| Toilet At Counseling Room2 | 1 | 1 |  |  |  | 1
| Dr. Toilet | 1 | 1 |  |  |  | 1
| Sperm Collection Room | 1 | 1 |  |  |  | 1
[7 empty] | 4 | Nos
83 | Supplying and fixing CP finish brass soap dish of approved make ISI quality including cost and conveyance of all materials, labour charges for fixing, overheads & contractors profit for finished item of work
| Prepost Operative wards | 1 | 1 |  |  |  | 1
| Toilet At Counseling Room2 | 1 | 1 |  |  |  | 1
| Dr. Toilet | 1 | 1 |  |  |  | 1
| Sperm Collection Room | 1 | 1 |  |  |  | 1
[7 empty] | 4 | Nos
84 | Supplying and fixing TV shape mirror with plastic frame of size 609.6mm x 457.2mm , plywood back with NP screws 1st quality including cost and conveyance of all materials, labour charges , overheads & contractors profit for finished item of work
| Prepost Operative wards | 1 | 1 |  |  |  | 1
| Toilet At Counseling Room2 | 1 | 1 |  |  |  | 1
| Dr. Toilet | 1 | 1 |  |  |  | 1
| Sperm Collection Room | 1 | 1 |  |  |  | 1
[7 empty] | 4 | Nos
85 | Supplying and fixing of CP finish steel towel rods 600mm long and 20mm dia with brackets and aluminium screws including cost and conveyance of all materials, labour charges , overheads & contractors profit for finished item of work.
| Prepost Operative wards | 1 | 1 |  |  |  | 1
| Toilet At Counseling Room2 | 1 | 1 |  |  |  | 1
| Dr. Toilet | 1 | 1 |  |  |  | 1
| Sperm Collection Room | 1 | 1 |  |  |  | 1
[7 empty] | 4 | Nos
86 | Supplying and fixing 15 mm Steel body CP finish self closing tap push type conforming to IS 1711 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, overheads & contractors profit complete for finished item of work in all floors.
| Prepost Operative wards | 1 | 1 |  |  |  | 1
| Toilet At Counseling Room2 | 1 | 1 |  |  |  | 1
| Dr. Toilet | 1 | 1 |  |  |  | 1
| Sperm Collection Room | 1 | 1 |  |  |  | 1
[7 empty] | 4 | Nos
82 | Supplying and fixing Chromium plated finish brass body quarter turn Bibcock cum Health Faucet with 1m long tube and wall hook with necessary fittings etc., complete including cost and conveyance of all materials, labour charges, complete for finished item of work in all floors. at Gandhi Hospital
| Prepost Operative wards | 1 | 1 |  |  |  | 1
| Toilet At Counseling Room2 | 1 | 1 |  |  |  | 1
| Dr. Toilet | 1 | 1 |  |  |  | 1
| Sperm Collection Room | 1 | 1 |  |  |  | 1
[7 empty] | 4 | Nos
73 | Supplying and fixing 15 mm brass body CP finish bib tap of not less than 300 grams weight screw type full turn with internal/external threaded connection conforming to IS 8931 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, overheads and contractors profit complete for finished item of work in all floors. at Gandhi Hospital
| Dr. Toilet | 1 | 1 |  |  |  | 1
[7 empty] | 1 | Nos
79 | Supply and fixing of 4 inches 101.6mm multi floor trap with jali -UPVC/SWR pipe fittings as per site requirements with standard practice for all floor including cost and conveyance of all materials to site ,labour charges ,etc,. Complete for finshed item of work at handhi hospital
| Prepost Operative wards | 1 | 1 |  |  |  | 1
| Toilet At Counseling Room2 | 1 | 1 |  |  |  | 1
| Dr. Toilet | 1 | 1 |  |  |  | 1
| Sperm Collection Room | 1 | 1 |  |  |  | 1
| Scrub Wastewater Line | 1 | 1 |  |  |  | 1
[7 empty] | 5 | Nos
182 | SITC of Oxygen Manifold Emergency for 1 plus 1 Cylinders, as per technical specifications. At Gandhi Hospital
| Manifold Room | 1 | 1 |  |  |  | 1 | Set
183 | SITC of Oxygen Outlets with matching probes, as per HTM-2022/02-01 of UK/NFPA99C of USA as per enclosed technical specifications - Imported At Gandhi Hospital
| Manifold Room | 1 | 6 |  |  |  | 6 | Nos
184 | SITC of Oxygen Flow meter with Humidifier, CE Certified with four digit number as per enclosed technical specifications - Imported At Gandhi Hospital
| Manifold Room | 1 | 6 |  |  |  | 6
185 | SITC of Nitrous Oxide Manifold Emergency for 1 Cylinder, with high pressure Regulator, NRV, tailpipes etc. as per technical specifications At Gandhi Hospital
| Manifold Room | 1 | 1 |  |  |  | 1 | Set
186 | SITC of N20 Outlets with matching probes, as per HTM-2022/02-01 of UK/NFPA99C of USA as per enclosed technical specifications - Imported At Gandhi Hospital
| Manifold Room | 1 | 4 |  |  |  | 4 | Nos
187 | SITC of C02 Manifold for 2 Cylinders, with high pressure Regulator, NRV, tailpipes etc. as per technical specifications At Gandhi Hospital
| Manifold Room | 1 | 1 |  |  |  | 1 | Set
188 | SITC of C02 Outlets with matching probes, as per HTM-2022102-01ofUK/NFPA99C of USA as per enclosed technical specifications - Imported At Gandhi Hospital
| Manifold Room | 1 | 6 |  |  |  | 6 | Nos
189 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 12mm COPPER PIPE at Gandhi Hospital
| Manifold Room to Prepost Operative Wards | 1 | 1 | 38.3 |  |  | 38.3 | Rmt
190 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 15mm COPPER PIPE at Gandhi Hospital
| Manifold Room to Prepost Operative Wards | 1 | 1 | 157.7 |  |  | 157.7 | Rmt
191 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 22mm COPPER PIPE at Gandhi Hospital
| Manifold Room to Prepost Operative Wards | 1 | 1 | 79.5 |  |  | 79.5 | Rmt
192 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 28mm COPPER PIPE at Gandhi Hospital
| Manifold Room to Prepost Operative Wards | 1 | 1 | 27 |  |  | 27 | Rmt
193 | SITC of Touch type LCD Area Alarm and Zonal Valve box- as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications imported for 3 gases at Gandhi Hospital
| Manifold Room | 1 | 1 |  |  |  | 1 | Nos
194 | SITC of Touch type LCD Area Alarm and Zonal Valve box- as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications imported for Master Main Alarm including all Gases at Gandhi Hospital
| Manifold Room | 1 | 1 |  |  |  | 1 | Nos
195 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 15mm 0D at Gandhi Hospital
| Manifold Room | 1 | 8 |  |  |  | 8 | Nos
196 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 22mm 0D at Gandhi Hospital
| Manifold Room | 1 | 3 |  |  |  | 3 | Nos
197 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 28mm 0D at Gandhi Hospital
| Manifold Room | 1 | 4 |  |  |  | 4 | Nos
198 | SITC of Bed Head Panel - as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications at Gandhi Hospital
| Manifold Room | 1 | 2 |  |  |  | 2 | Nos

## Abs -5
ABSTRACT
| Name of the work:Design, Fabriction, establishing and commissioning of In - Vitro ferility centers (IVFC) alongwith allied Services on Turnkey basis at Gandhi hospital secunderabad. | [7 empty] | Agency: M/s. Asta Vardhman Consortium | [5 empty] | Agt.No: 344/A/TSMIDC/Spl.Proj/IVFCs/2022-23,Dt.05.07.2023
S.No | Discription Of Work etc., | Measurements Upto date | [7 empty] | Per | Total Volume |  | Deduct/previous Measurements |  | Since last measurement |  |  | Remarks
|  | No |  | L | B | D | Content | Rs | Ps. |  | Rs. | Ps | P.No. | Qty. | Qty | Value
[16 empty] | Rs. | Ps.
49 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete (Brick Masonary)
| (Brick Masonary) |  |  |  | 32.68
| V.P 01 ABNO 08 |  |  |  |  | 31.21 | 31.21 | 398 | Cum | 12421.58 |  |  | 31.21 | 12421.58 | 0 | 0 |  |  | 398
| V.P 01 ABNO 09 |  |  |  |  | 1.47 | 1.47 | 398 | Cum | 585.06 |  |  | 0 | 0 | 1.47 | 585.06
Old Cement Morter
| V.P 01 ABNO 08 |  |  |  |  | 37.13 | 37.13 | 8 | Sqm | 297 |  |  | 37.13 | 297 | 0
Unreinforcement Cement More Than 15cm
| V.P 01 ABNO 08 |  |  |  |  | 3.89 | 3.89 | 2842 | Cum | 11055 |  |  | 3.89 | 11055 | 0
Reinforcement Cement
| V.P 01 ABNO 02 |  |  |  |  | 0.7 | 0.7 | 3115 | Cum | 2181 |  |  | 0.7 | 2181 | 0
51 | Dismantling doors, windows and clear storey windows, Ventilators etc., (wood or steel) shutters including Chowkhats, architraves,hold fasts and other attachments etc., and stacking them within 100m lead including labour charge etc., and overheads & contractors profit complete for finished item of work. | [17 empty] | 468
| V.P 01 ABNO 10 |  |  |  |  | 7 | 5 | 468 | Each | 2340 |  |  | 5 | 2340 | 0
[6 empty] | AE | 2 |  | Each | 0 |  |  | 2 | 0 | 0
53 | Masonry work in CM (1:8) prop (cement: Screened sand) in super structure with / lime solid blocks of size 290mmx225mmx140mm from approved source having minimum crushing strength of 50 Kg/Sqcm including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, including sales & other taxes on all materials, all operational, incidental and labour charges such as mixing cement mortar, constructing masonry, scaffolding charges, lift charges, curing, etc., complete but excluding seigniorage charges for finished item of work. (APSS No. 501 & 504).
| V.P 01 ABNO 10 |  |  |  | 15.27 | 9.03 | 9.03 | 16055 | Cum | 144977 |  |  | 9.03 | 144977 | 0 | 0 |  |  | 16055
| V.P 01 ABNO 10 |  |  |  |  | 6.24 | 6.24 | 16055 | Cum | 100183 |  |  | 0 | 0 | 6.24 | 100183
54 | Reinforced brick Masonry for Partition Walls (11.0 cm thick) in CM (1:4) prop (cement: Screened sand) in super structure with / lime solid blocks of size 290mmx225mmx140mm from approved source having minimum crushing strength of 50 Kg/Sqcm including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, including sales & other taxes on all materials, all operational, incidental and labour charges such as mixing cement mortar, constructing masonry, scaffolding charges, lift charges, curing, etc., complete but excluding seigniorage charges for finished item of work. (APSS No. 501 & 504).
| V.P 01 ABNO 10 |  |  |  |  | 191.03 | 191.0305 | 1952 | Sqm | 372892 |  |  | 191.0305 | 372892 | 0 |  |  |  | 1952
55 | Providing Thermo Mechanically Treated ( TMT) ( Fe-500/500D/550D from primery producer TATA, SAIL, VSP, JSW Steel, Goel steel, Jindal panther, X- Vega & balaji Shakthi as per IS 1786-2008) of Different Diameters RCC Works , including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and sizes and typing and lap - spacing with binding wire of 18 SWG, Forming grills for reinforcement work as per approved design and drawings, including and conveyanace of steel bars, including all wastages such as overlaps, coupling, chairs, spacer bars including cost and conveyance of binding wire cover blocks and incidential, operational, labour charges such as cutting bending, placing in position, typing incliding sales and other taxes on all materials etc., and overheads & contractors profit completefor finished item of work
| V.P 01 ABNO 10 |  |  |  |  | 0.103 | 0.103 | 116500 | MT | 12000 |  |  | 0.103 | 12000 | 0 |  |  |  | 116500
Sup | Supply and placing of the Design Mix Concrete M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Weight Batcher / Concrete mixer with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials, centering using Casurina Ballies, Bamboos, Wooden Reapers, Runners, Wood Posts, Steel Plates etc., including all operational, incidental and labour charges such as weigh batching, machine mixing, lifting of concrete manually, laying concrete, curing , overheads & contractors profit etc., complete but excluding cost of steel and its fabrication charges for finished item of work (APSS No. 402) (For Lintels)
| V.P 01 ABNO 10 |  |  |  |  | 0.43 | 0.43 | 12775 | Cum | 5493 |  |  | 0.43 | 5493 | 0
56 | Plastering 12mm thick in two coats using screened sand with base coat of 8mm thick in CM (1:6) and top coat of 4mm thick in CM (1:4) with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales & other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and overheads & contractors profit complete for finished item of work. (SS 901,903 & 904).
| V.P 01 ABNO 10 |  |  |  |  | 536.11 | 536.1091 | 1041 | Sqm | 558090 |  |  | 536.1091 | 558090 | 0 |  |  |  | 1041 | 22295.5
Sup | Flooring with 16 to 18 mm thick high polished granite stone slabs black colour as approved by the Engineer-in-Charge of length not less than 2.43 mts set over base coat of cement mortar (1:8) , 20mm thick using screened sand over CC bed already laid or RCC roof slab including neat grey cement slurry of honey like consistency spread @ 3.3 Kg per sqm and jointed neatly with white cement paste mixed with pigment of matching shade to full depth including cost and conveyance of all materials like cement , sand , water , granite slabs etc., to work site and all operational, incidental labour & lift charges, half rounding the edge , polishing charges and all other taxes on all materials, cost of base coat and overheads & contractors profit complete for finished item of work for platforms (S.S.701 & special) | [18 empty] | 22295.5
| V.P 02 ABNO 10 |  |  |  |  | 10.17 | 10.166 | 6300 | Sqm | 64071 |  |  | 10.166 | 64071 | 0
65 | Flooring with soluble salt porcelain vitrified tiles screen printed and polished of size 600 x 600 mm and thickness between 8 to 10mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630Parts 1 to 15 of any colour and finish in all shades and designs with borders and design as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM 1:8 prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread at the rate 3.3 kgs per Sqm. and jointed neatly with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site excluding cost of C.C. bed including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in- charge etc., and complete for finished item of work. TSSS No.701 and 707. 5th Floor at Gandhi Hospital
| V.P 02 AB NO 10 |  |  |  |  | 374.81 | 225 | 1725 | Sqm | 388125 |  |  | 225 | 388125 | 0 |  |  |  | 1725
[6 empty] | AE | 149.81 |  | Sqm | 0 |  |  | 149.81 | 0 | 0
66 | Flooring with non-skid full body ceramic floor tiles of size 300mm x 300mm and thickness between 7 - 8mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630 Part 1 to 15 of any colour and finish in all shades and designs as approved by Engineer-in-charge, set over base coat of cement mortar 1:8, 12mm thick using screened sand over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread at the rate 3.3 Kgs per Sqm and jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, screened sand , water and tiles etc., complete for finished item of work. TSSS No.701 and 707 at Gandhi Hospital
| V.P 02 AB NO 10 |  |  |  |  | 14.62 | 14.618 | 1525 | Sqm | 22296 |  |  | 14.618 | 22296 | 0 |  |  |  | 1525
68 | Providing dadooing to walls with glazed full body porcelain wall tiles of size 300 x 600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. 5th Floor at Gandhi Hospital
| V.P 02 AB NO 10 |  |  |  |  | 103.76 | 40 | 1423 | Sqm | 56920 |  |  | 40 | 56920 | 0 |  |  |  | 1423
[6 empty] | AE | 63.766 |  | Sqm | 0 |  |  | 63.766 | 0 | 0
Sup | Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707)
| V.P 02 AB NO 10 |  |  |  |  | 107.18 | 107.179 | 114 | Rmt | 12219 |  |  | 107.179 | 12219 | 0
Electrical-1
96 | Supply and Fixing of 25mm outer dia medium grade, FRLS with IS:9537 part 3 rigid PVC pipe Concealed in with all required PVC/ Metalic junction boxes a including masonary work and labour charges etc., complete Makes:- Sudhakar / Modi
| V.P 02 AB NO 10 |  |  |  | 415.5 | 184.1 | 200 | 116 | Rmt | 23200 |  |  | 200 | 23200 | 0 |  |  |  | 116
| V.P 02 AB NO 10 |  |  |  |  | 231.4
[6 empty] | AE | 215.5
97 | Supply and Fixing of 25mm outer dia medium grade, FRLS with IS:9537 part 3 rigid PVC pipe with all accessories fixing on wall / ceiling with chromium plated metallic base saddles including all labour charges etc., complete Makes:- Modi
| V.P 02 AB NO 10 |  |  |  |  | 1060.2 | 500 | 107 | Rmt | 53500 |  |  | 500 | 53500 | 0 |  |  |  | 107
[6 empty] | AE | 560.2 |  | Rmt | 0 |  |  | 560.2 | 0 | 0
98 | Wiring with run of 2 of 22/0.3mm (1.5 Sqmm) FRLS / HFFR PVC insulated flexible ISI mark copper cable in existing PVC conduit pipe including Supply and fixing of Jumbo Ceiling rose and 6A/10A ISI Mark 1way Modular switch with required modular box and cover frame in existing Surface or Concealed pipe wiring including cost and conveyance of all material and all labour charges etc., complete for light, Fan, Exhaust fan and bell points in N.R.B. Makes of wires : Polycab (HFFR) Makes of switches :Honeywell Blenge Plus
| V.P 02 AB NO 10 |  |  |  | 146 | 119 | 110 | 945 | No | 103950 |  |  | 110 | 103950 | 0 |  |  |  | 945
| V.P 02 AB NO 10 |  |  |  |  | 27
[6 empty] | AE | 36
99 | Supply and fixing of 6A/10A ISI Mark 3/2 pin Modular socket with 6A/10A 1way Modular switch, 3 Module box with cover frame a Common switch board including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B. Makes of switches : Honeywell Blenge Plus
| V.P 03 AB NO 10 |  |  |  |  | 30 | 12 | 675 | No | 8100 |  |  | 12 | 8100 | 0 |  |  |  | 675
[6 empty] | AE | 18 |  | No | 0 |  |  | 18 | 0 | 0
100 | Supply and fixing of 16A switches - 1Nos and 6/16A 2 in one socket - 1Nos Modular type with cover plate and GI switch box fixing on separate board including all labour charges etc., complete. Makes of switches: - Hooney well Benzplus
| V.P 03 AB NO 10 |  |  |  |  | 14 | 14 | 1040 | No | 14560 |  |  | 14 | 14560 | 0 |  |  |  | 1040
101 | Supply & fixing of 16A/6A, 2 in one socket - 2 Nos with 16A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benzplus
| V.P 03 AB NO 10 |  |  |  | 53 | 34 | 53 | 1755 | No | 93015 |  |  | 53 | 93015 | 0 | 19 |  |  | 1755
| V.P 03 AB NO 10 |  |  |  |  | 19
104 | Supply and Run of 3 of 36/0.3mm (2.50 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
| V.P 03 AB NO 10 |  |  |  | 637.1 | 540.7 | 600 | 177 | Rmt | 106200 |  |  | 600 | 106200 | 0 |  |  |  | 177
| V.P 03 AB NO 10 |  |  |  |  | 96.4
[6 empty] | AE | 37.1
105 | Supply and Run of 3 of 56/0.3mm (4.00 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
| V.P 03 AB NO 10 |  |  |  | 1349.1 | 1170.8 | 1200 | 255 | Rmt | 306000 |  |  | 1200 | 306000 | 0 |  |  |  | 255
| V.P 03 AB NO 10 |  |  |  |  | 178.3 | 149.1
AE
106 | Supply and Run of 5 of 90/0.3mm (6.0 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
| V.P 03 AB NO 10 |  |  |  | 333.3 | 243.3 | 60 | 606 | Rmt | 36360 |  |  | 60 | 36360 | 0 |  |  |  | 606
| V.P 03 AB NO 10 |  |  |  |  | 90
[6 empty] | AE | 273.3 |  | Rmt | 0 |  |  | 273.3 | 0 | 0
107 | Supply & run of 5 of 10.0 Sqmm (140/0.3 mm) (3 phases, neutral and earth) FRLS / HFFR PVC insulated flexible copper cable in the existing conduit pipe for run of mains from Power panel board to TPN DB"s with pin type lugs and connections etc., complete. [for PDBs] Makes of wires: Polycab
| V.P 03 AB NO 10 |  |  |  |  | 145.1 | 40 | 967 | Rmt | 38680 |  |  | 40 | 38680 | 0 |  |  |  | 967
[6 empty] | AE | 105.1 |  | Rmt | 0 |  |  | 105.1 | 0 | 0
109 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand and Supply and Fixing of 1 No., of 40A FP 30mA RCCB as incomer and 12 Nos 6-32 A 10kA SP MCBs Makes: Legrand-DX3 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. (For Lighting DBs) Make Legrand
| V.P 03 AB NO 10 |  |  |  |  | 8 | 3 | 18325 | No | 54975 |  |  | 3 | 54975 | 0 |  |  |  | 18325
[6 empty] | AE | 5 |  | No | 0 |  |  | 5 | 0 | 0
110 | Supply and fixing of 8 Way VTPN DB with IP 43 Protection as per IS:13032 with 1 No., of 125A 4P MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted as incomer with 8 Nos of 63A, 10KA, TP MCBs C Curve ISI Mark as Out goings including internal connections and labour charges for FLUSH Mounting etc., complete. Makes : Legrand / Schneider
| V.P 04 AB NO 10 |  |  |  |  | 1 | 1 | 28460 | No | 28460 |  |  | 1 | 28460 | 0 |  |  |  | 28460
114 | Supply, transportation and fixing of 24W edge lit LED Down light Square Housing Made of Aluminium alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser Square with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor > 0.9, Surge protection: > 2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI >80, and THD is less than 15% etc., with BIS Certification. Makes: Crompton
| V.P 04 AB NO 10 |  |  |  |  | 44 | 44 | 2652 | No | 116688 |  |  | 44 | 116688 | 0 |  |  |  | 2652
115 | Supply and Transportation 36W Edge lit, 2' x2' (600mm x600mm) slim panel LED luminaire Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% etc., complete. Makes: Crompton
| V.P 04 AB NO 10 |  |  |  |  | 40 | 30 | 4350 | No | 130500 |  |  | 30 | 130500 | 0 |  |  |  | 4350
[6 empty] | AE | 10 |  | No | 0 |  |  | 10 | 0 | 0
119 | Supply and fixing of Modular type Stepped electronic regulator Makes : GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/ Cabtree Verna/ Million logus / Gold Medal Curve for sweep AC ceiling fans of 1200mm / 1400mm complete with connections.
| V.P 04 AB NO 10 |  |  |  |  | 14 | 12 | 827 | No | 9924 |  |  | 12 | 9924 | 0 |  |  |  | 827
[6 empty] | AE | 2 |  | No | 0 |  |  | 2 | 0 | 0
122 | SITC of Hot dip galvanized perforated cable tray of 300 mm Wide sizes for to run the cable from Floor Panel to Lab Panel & electrical room to AC panel and AC panel to Units. All necessary supports & accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. ( Elec 4.10.1 d)
| V.P 04 AB NO 10 |  |  |  |  | 85.4 | 80 | 1310 | Rmt | 104800 |  |  | 80 | 104800 | 0 |  |  |  | 1310
[6 empty] | AE | 5.4 |  | Rmt | 0 |  |  | 5.4 | 0 | 0
128 | Supply & installation of 50x6 GI flat for body earthing of electrical panel & AC Panel which is laid in 300mm cable tray
| V.P 04 AB NO 10 |  |  |  |  | 184.9 | 184.9 | 329 | Rmt | 60832 |  |  | 184.9 | 60832 | 0 |  |  |  | 329
129 | Supply & installation of 25x3 GI flat for body earthing of DBs & Cable tray which is laid in 100mm cable tray
| V.P 04 AB NO 10 |  |  |  |  | 116.3 | 100 | 163 | Rmt | 16300 |  |  | 100 | 16300 | 0 |  |  |  | 163
[6 empty] | AE | 16.3 |  | Rmt | 0 |  |  | 16.3 | 0 | 0
131 | Supply & installation of 4 sqmm Copper wire for Earthing of DBs Equipment
| V.P 04 AB NO 10 |  |  |  |  | 286 | 80 | 83 | Rmt | 6640 |  |  | 80 | 6640 | 0 |  |  |  | 83
[6 empty] | AE | 206 |  | Rmt | 0 |  |  | 206 | 0 | 0
132 | Supply, Lying & testing of 3.5Cx95 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/ Glostar/ Finolex Make of gland & Lungs: HMI/ Commet /Dowell’s
| V.P 05 AB NO 10 |  |  |  |  | 83 | 83 | 1207 | Rmt | 100181 |  |  | 83 | 100181 | 0 |  |  |  | 1207
133 | Supply, Lying & testing of 3.5CX50 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/ Universal/ Glostar/ Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
| V.P 05 AB NO 10 |  |  |  |  | 40 | 40 | 722 | Rmt | 28880 |  |  | 40 | 28880 | 0 |  |  |  | 722
149 | Split AC unit 1.5 TR inverter type 3 Star capable of delivering 18000 BTU/hr and above with high wall mounted indoor unit and outdoor condensing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord , built-in stabilizer Voltage range 160- 264 volts and cordless remote control. Makes : Daikin / Thoshiba / O General at Gandhi Hospital
| V.P 05 AB NO 10 |  |  |  |  | 2 | 1 | 43200 | Nos | 43200 |  |  | 1 | 43200 |  |  |  | 90% | 48000
[6 empty] | AE | 1 | 43200 |  | 43200
124 | Batteries : Supply and fixing of 12V 65 AH SMF battery including wire leads. Makes: Quanta / Racket / Exide. At Gandhi Hospital
| V.P 05 AB NO 10 |  |  |  |  | 32 | 20 | 18526 | Nos | 370520 |  |  | 20 | 370520 |  |  |  | 90% | 20584
[6 empty] | AE | 12 | 18526 |  | 222312
125 | Supply and providing of UPS com Batteri rack for 20 batteries . At Gandhi Hospital
| V.P 05 AB NO 10 |  |  |  |  | 1 | 1 | 6088 | Nos | 6088 |  |  | 1 | 6088 |  |  |  | 90% | 6764
123 | 20 KVA UPS: Supply and installation of 20KVA 3ph in and 3ph out on line UPS system IGBT based rectifier with input power factor correction 32 bit microprocessor based with isolation transformers double conversion, SNMP controls, LCD display, Pure sine wave output, with auto static switch three phase input / Three phase output and modular structure for better thermal technology / cooling facility, with warranty up to three years.Makes: APC / Numeric / Emerson / Fuji Electric At Gandhi Hospital
| V.P 05 AB NO 10 |  |  |  |  | 1 | 1 | 274500 | Nos | 274500 |  |  | 1 | 274500 |  |  |  | 90% | 305000
173 | Condensing units - VRF/VRV System 16 HP: Supply, Installation, Nitrogen testing , Vacuuming and Commissioning of air cooled variable refrigerant flow modular type condensing units, each comprising of multiple scroll compressors all inverter driven, full charge of refrigerant gas R-410a including additional gas filling , lubricating oil and all accessories as per the specifications. The condensing units shall be suitable to work on cooling mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B . The COP of the system shall be greater than 4 under ARI conditions for 100percentage load . The condensing units shall be suitable for operation on 415 plus or minus 10percentage volts, 50Hz, 3 phase AC power supply and , outdoor units to be mounted on MS platform with suitable Vibration Isolation pads to avoid vibrations. All the supports and angle base frame structure to be duly black painted with synthetic epoxy paint. the condensing units shall be of following capacities: The VRF ODU should be capable of working with total capacity of connected indoor units ranging between 100percentage to 140percentage of ODU capacity . COP minimum 3.5. Make : Daikin / LG / O General / Toshiba. 16 HP At Gandhi Hospital
| V.P 05 AB NO 10 |  |  |  |  | 1 | 1 | 292500 | Nos | 292500 |  |  | 1 | 292500 |  |  |  | 90% | 325000
174 | VRF Indoor Units : Hi wall Splits 0.8 TR: Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 0.8 TR At Gandhi Hospital
| V.P 05 AB NO 10 |  |  |  |  | 1 | 1 | 27630 | Nos | 27630 |  |  | 1 | 27630 |  |  |  | 90% | 30700
175 | VRF Indoor Units : Hi wall Splits 1.0 TR: Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.0 TR At Gandhi Hospital
| V.P 06 AB NO 10 |  |  |  |  | 4 | 4 | 27630 | Nos | 110520 |  |  | 4 | 110520 |  |  |  | 90% | 30700
176 | VRF Indoor Units 1.5 TR : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.5 TR At Gandhi Hospital
| V.P 06 AB NO 10 |  |  |  |  | 5 | 4 | 31500 | Nos | 126000 |  |  | 4 | 126000 |  |  |  | 90% | 35000
[6 empty] | AE | 1 | 31500 |  | 31500
177 | Cassette Units 3.0 TR : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling mode.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 3.0 TR – 4 way At Gandhi Hospital
| V.P 06 AB NO 10 |  |  |  |  | 1 | 1 | 45000 | Nos | 45000 |  |  | 1 | 45000 |  |  |  | 90% | 50000
3 | DICOM compatible fully digital, compact, portable, Ultrasound Scan Machine Colour Doppler at Gandhi Hospital
| V.P 06 AB NO 10 |  |  |  |  | 2 | 2 | 1228500 | Nos | 2457000 |  |  | 2 | 2457000 |  |  |  | 90% | 1365000
27 | Defibrilator at Gandhi Hospital
| V.P 06 AB NO 10 |  |  |  |  | 1 | 1 | 281250 | Nos | 281250 |  |  | 1 | 281250 |  |  |  | 90% | 312500
30 | Anesthasia work station at Gandhi Hospital
| V.P 06 AB NO 10 |  |  |  |  | 1 | 1 | 843750 | Nos | 843750 |  |  | 1 | 843750 |  |  |  | 90% | 937500
31 | Autoclave at Gandhi Hospital
| V.P 06 AB NO 10 |  |  |  |  | 1 | 1 | 506250 | Nos | 506250 |  |  | 1 | 506250 |  |  |  | 90% | 562500
35 | Ultrasound Examination Couch at Gandhi Hospital
| V.P 06 AB NO 10 |  |  |  |  | 1 | 1 | 73125 | Nos | 73125 |  |  | 1 | 73125 |  |  |  | 90% | 81250
2 | IVF Test tube Warmers at Gandhi Hospital
| V.P 06 AB NO 10 |  |  |  |  | 2 | 2 | 44550 | Nos | 89100 |  |  | 2 | 89100 |  |  |  | 90% | 49500
4 | Multipurpose Electro hydraulic with manual override mobile OT Table, with divided leg section suitable for all Gynaecological surgical procedures, complete with 5cm Mattress and corded handset at Gandhi Hospital
| V.P 07 AB No 10 |  |  |  |  | 2 | 1 | 507375 | Nos | 507375 |  |  | 1 | 507375 |  |  |  | 90% | 563750
[6 empty] | AE | 1 | 507375 |  | 507375
5 | LED procedure Lights Double dome at Gandhi Hospital
| V.P 07 AB No 10 |  |  |  |  | 1 | 1 | 281250 | Nos | 281250 |  |  | 1 | 281250 |  |  |  | 90% | 312500
6 | LED procedure Lights Single dome at Gandhi Hospital
| V.P 07 AB No 10 |  |  |  |  | 1 | 1 | 168750 | Nos | 168750 |  |  | 1 | 168750 |  |  |  | 90% | 187500
14 | IVF Thermometer with Probe
| V.P 07 AB No 10 |  |  |  |  | 1 | 1 | 55688 | Nos | 55688 |  |  | 1 | 55688 |  |  |  | 90% | 61875
15 | CO2 Cylinder with accessories
| V.P 07 AB No 10 |  |  |  |  | 2 | 2 | 45000 | Nos | 90000 |  |  | 2 | 90000 |  |  |  | 90% | 50000
26 | Cryocane TA 26 Ltr with wheels
| V.P 07 AB No 10 |  |  |  |  | 2 | 2 | 55688 | Nos | 111376 |  |  | 2 | 111376 |  |  |  | 90% | 61875
16 | CO2 and O2 Analyzer
| V.P 07 AB No 10 |  |  |  |  | 1 | 1 | 340200 | Nos | 340200 |  |  | 1 | 340200 |  |  |  | 90% | 378000
17 | PH Meter
| V.P 07 AB No 10 |  |  |  |  | 1 | 1 | 84375 | Nos | 84375 |  |  | 1 | 84375 |  |  |  | 90% | 93750
19 | Sperm Counting Chamber
| V.P 07 AB No 10 |  |  |  |  | 1 | 1 | 68063 | Nos | 68063 |  |  | 1 | 68063 |  |  |  | 90% | 75625
20 | Binocular Microscope MLX-B Plus
| V.P 07 AB No 10 |  |  |  |  | 1 | 1 | 37125 | Nos | 37125 |  |  | 1 | 37125 |  |  |  | 90% | 41250
22 | Clinical Centrifuge machine for Andrology with Acessories
| V.P 07 AB No 10 |  |  |  |  | 1 | 1 | 31050 | Nos | 31050 |  |  | 1 | 31050 |  |  |  | 90% | 34500
34 | Mulitfunctional Printer
| V.P 08 AB No 010 |  |  |  |  | 1 | 1 | 39375 | Nos | 39375 |  |  | 1 | 39375 |  |  |  | 90% | 43750
37 | Laptop
| V.P 08 AB No 010 |  |  |  |  | 2 | 2 | 103500 | Nos | 207000 |  |  | 2 | 207000 |  |  |  | 90% | 115000
23 | DRY Incubator
| V.P 08 AB No 010 |  |  |  |  | 1 | 1 | 507375 | Nos | 507375 |  |  | 1 | 507375 |  |  |  | 90% | 563750
9 | CO2 Incubators
| V.P 08 AB No 010 |  |  |  |  | 2 | 2 | 742500 | Nos | 1485000 |  |  | 2 | 1485000 |  |  |  | 90% | 825000
1 | Ovum Aspiration Pumps at Gandhi Hospital
| V.P 08 AB No 010 |  |  |  |  | 2 | 2 | 216000 | Nos | 432000 |  |  | 2 | 432000 |  |  |  | 90% | 240000
7 | IVF Workstation with LAF at Gandhi Hospital
| V.P 08 AB No 010 |  |  |  |  | 1 | 1 | 618750 | Nos | 618750 |  |  | 1 | 618750 |  |  |  | 90% | 687500
8 | IVF Anti-vibration Table for Procedure
| V.P 08 AB No 010 |  |  |  |  | 1 | 1 | 86625 | Nos | 86625 |  |  | 1 | 86625 |  |  |  | 90% | 96250
10 | Trigas Bench Top Incubators for Human Embryo culture
| V.P 08 AB No 010 |  |  |  |  | 1 | 1 | 742500 | Nos | 742500 |  |  | 1 | 742500 |  |  |  | 90% | 825000
11 | Trinocular Stereozoom Microscope
| V.P 08 AB No 010 |  |  |  |  | 1 | 1 | 278100 | Nos | 278100 |  |  | 1 | 278100 |  |  |  | 90% | 309000
12 | ICSI Micro Manipulator with Inverted Microscope
| V.P 08 AB No 010 |  |  |  |  | 1 | 1 | 2362500 | Nos | 2362500 |  |  | 1 | 2362500 |  |  |  | 90% | 2625000
13 | IVF Laser System
| V.P 08 AB No 010 |  |  |  |  | 1 | 1 | 2304000 | Nos | 2304000 |  |  | 1 | 2304000 |  |  |  | 90% | 2560000
18 | VOC Meter for ART Lab
| V.P 09 AB No 010 |  |  |  |  | 1 | 1 | 658125 | Nos | 658125 |  |  | 1 | 658125 |  |  |  | 90% | 731250
21 | Laminar Flow Cabinet with Andrology Work Station
| V.P 09 AB No 010 |  |  |  |  | 1 | 1 | 225000 | Nos | 225000 |  |  | 1 | 225000 |  |  |  | 90% | 250000
24 | Pipetter and Denudation system
| V.P 09 AB No 010 |  |  |  |  | 1 | 1 | 92813 | Nos | 92813 |  |  | 1 | 92813 |  |  |  | 90% | 103125
25 | Pharmaceutical Refrigerator
| V.P 09 AB No 010 |  |  |  |  | 1 | 1 | 202500 | Nos | 202500 |  |  | 1 | 202500 |  |  |  | 90% | 225000
28 | 7 Para Patient Monitor
| V.P 09 AB No 010 |  |  |  |  | 2 | 2 | 252000 | Nos | 504000 |  |  | 2 | 504000 |  |  |  | 90% | 280000
29 | Suction Machine
| V.P 09 AB No 010 |  |  |  |  | 1 | 1 | 44550 | Nos | 44550 |  |  | 1 | 44550 |  |  |  | 90% | 49500
32 | Operative Hysteroscopy and Resectoscope Set Machine
| V.P 09 AB No 010 |  |  |  |  | 1 | 1 | 1912500 | Nos | 1912500 |  |  | 1 | 1912500 |  |  |  | 90% | 2125000
33 | Operative Laparoscopy Set
| V.P 09 AB No 010 |  |  |  |  | 1 | 1 | 3780000 | Nos | 3780000 |  |  | 1 | 3780000 |  |  |  | 90% | 4200000
39 | Reception Chair
| V.P 09 AB No 010 |  |  |  |  | 2 | 2 | 31050 | Nos | 62100 |  |  | 2 | 62100 |  |  |  | 90% | 34500
42 | Consultant Chair
| V.P 09 AB No 010 |  |  |  |  | 3 | 3 | 17325 | Nos | 51975 |  |  | 3 | 51975 |  |  |  | 90% | 19250
43 | Patient Chair
| V.P 09 AB No 010 |  |  |  |  | 6 | 6 | 12375 | Nos | 74250 |  |  | 6 | 74250 |  |  |  | 90% | 13750
44 | Small Trolley
| V.P 09 AB No 010 |  |  |  |  | 3 | 3 | 35280 | Nos | 105840 |  |  | 3 | 105840 |  |  |  | 90% | 39200
45 | Big Trolley
| V.P 10 AB No 010 |  |  |  |  | 3 | 3 | 56250 | Nos | 168750 |  |  | 3 | 168750 |  |  |  | 90% | 62500
46 | Wall Storage Cabinets
| V.P 10 AB No 010 |  |  |  |  | 8 | 8 | 15750 | Nos | 126000 |  |  | 8 | 126000 |  |  |  | 90% | 17500
151 | Modular Double skin floor mounted EUROVENT Certified Air Handling Unit 3400CFM / 8.5 TR / 150mm SP made out of 45 plus or minus 2mm thick PUF insulated panels Thermal break aluminium profile frame work with 0.8mm thick pre painted / powder coated inner and outer skins comprising of mixing box with fresh air and return air dampers, pre filters with 10 and 5 microns combination filters in single frame, Interlaced/Intertwined DX Cooling Coil suitable for connecting 2 nos of 8.5TR capacity 1W plus 1S out door condensing units, SS304 drain pan with , blower section with Nicotra / Kruger make direct drive/ Plug type fan, vibration isolators, EFF1 motor and blower section with on/off switches to operate from outside, limit switch for the fan section access door with a view port, fine filter section with 3 microns filters inspection doors for all filter and fan sections and damper at the outlet of unit. Ports for differential pressure gauges across all filters and blower to measure differential pressure. AHU Make : VTS / Systemair, Make - Blower - Nicotra / Kruger ; Motor - Crompton Greaves / Siemens ; Filter - Thermodyne / Freudenberg / Ultrafil at Gandhi Hospital
| V.P 10 AB No 010 |  |  |  |  | 1 | 1 | 531000 | Nos | 531000 |  |  | 1 | 531000 |  |  |  | 90% | 590000
166 | SITC of Magnehelic gauges across pre and fine filter at AHUs including mounting arrangement, SS nozzles, food grade PVC tubing, etc. At Gandhi Hospital
| V.P 10 AB No 010 |  |  |  |  | 3 | 2 | 9450 | Nos | 18900 |  |  | 2 | 18900 |  |  |  | 90% | 10500
[6 empty] | AE | 1
167 | SITC of Magnehelic gauges to measure the room differential pressures in operation theatres with SS mounting box, SS nozzles, food grade PVC tubing, etc. At Gandhi Hospital
| V.P 10 AB No 010 |  |  |  |  | 2 | 2 | 11610 | Nos | 23220 |  |  | 2 | 23220 |  |  |  | 90% | 12900
153 | SITC of air cooled condensing units with two scroll compressors, air cooled condenser, power panel, vibration isolating pads, stand for ODU, thermostat, etc. of the following capacities. The nominal capacity of the condensing unit shall be as under. Air cooled condensing unit shall have horizontal discharge. All refrigerant piping accessories sight glass, drier, expansion valve, etc. shall be supplied with the condensing units and suitable to connect above AHUs. Refrigerant shall be R 407C / R 410A. Necessary thermostat, control wiring, etc. shall be included. Derating of the unit shall not be more than 15percentage under 45 deg. C ambient temperature. Condensing unit shall be capable of operating up 50 deg. C ambient temperature. 8.5 TR capacity At Gandhi Hospital
| V.P 10 AB No 010 |  |  |  |  | 2 | 1 | 163800 | Nos | 163800 |  |  | 1 | 163800 |  |  |  | 90% | 182000
[6 empty] | AE | 1
154 | SITC of Flange type, Flame proof FLP duct heaters of 5 kW capacity with Mineral Filled AISI SS304/SS321 Sheathed Tubular Heater with GI Helical fins, Tube dia 8.2mm min and Helical Finn dia 25mm min, enclosed in the frame, FLP Terminal box etc., Nickel Chromium Inner Element, Silicon Sealing to Restrict Moisture pickup, Silver brazed mounting plate etc., and heaters shall be controlled with PID thyrestor controller based on the analog output signal of 0-10 V DC of controller . And this should have saftey thermostat and cutouts and air stat etc. all safety controls. The capacities as follows and sizes of the heaters shall be as per the duct sizes and approved drawing. at Gandhi Hospital
| V.P 10 AB No 010 |  |  |  |  | 1 | 1 | 184500 | Nos | 184500 |  |  | 1 | 184500 |  |  |  | 90% | 205000
152 | Supply and Installation of AL-powdercoated bottom loading type HEPA filter modules with bewel gear arrangement damper with access from clean room suitable to house the following size flange type HEPA filters including GI pressure plate, GI cleats with bolts and pressure drop & Integrity testing ports into room.Supply and Installation of H14 HEPA filters with 99.995% efficiency of the following sizes 600 X 600 X 150MM - HEPA filter - Module height <=350 mm,600 x 600 x 150 mm - 1000 CFM,600 x 600 x 150 mm - 1000 CFM
| V.P 10 AB No 010 |  |  |  |  | 6 | 6 | 37800 | Nos | 226800 |  |  | 6 | 226800 |  |  |  | 90% | 42000
140 | Supply, Installation, testing And Commissioning of 20 nos LAN points with cat 6 cable and with suitable network rack and 5 nos of telephone points with knore box to existing EPABEX. At Gandhi Hospital
| V.P 11 AB No 010 |  |  |  |  | 1 | 1 | 344700 | Job | 344700 |  |  | 1 | 344700 |  |  |  | 90% | 383000
141 | Supply, Installation, testing And Commissioning of 1 no of Access control system with egress switch, power cable communication cable to control panel with necessary required items etc,. At Gandhi Hospital
| V.P 11 AB No 010 |  |  |  |  | 1 | 1 | 111600 | Nos | 111600 |  |  | 1 | 111600 |  |  |  | 90% | 124000
142 | Supply, Installation, testing And Commissioning of Automatic Fire Alaram system which is including 30 nos of smoke detectors 1nos manual call point 1 nos hooter with fire alaram cable connected to the existing fire control panel with necessary required item etc,. At Gandhi Hospital
| V.P 11 AB No 010 |  |  |  |  | 1 | 1 | 459000 | Job | 459000 |  |  | 1 | 459000 |  |  |  | 90% | 510000
143 | Supply, Installation, testing And Commissioning of 5 nos IP Based CCTV camers and cat 6 cable with NVR system. At Gandhi Hospital
| V.P 11 AB No 010 |  |  |  |  | 1 | 1 | 163800 | Job | 163800 |  |  | 1 | 163800 |  |  |  | 90% | 182000
144 | Supply, Installation, testing And Commissioning of Audio and video recording of counseling rooms . At Gandhi Hospital
| V.P 11 AB No 010 |  |  |  |  | 1 | 1 | 124200 | Job | 124200 |  |  | 1 | 124200 |  |  |  | 90% | 138000
145 | Supply and Installation of fire Extinguisher of CO2 4.5 kg at Gandhi Hospital
| V.P 11 AB No 010 |  |  |  |  | 5 | 5 | 10103 | Nos | 50515 |  |  | 5 | 50515 |  |  |  | 90% | 11225
146 | Supply and iInstalltion of ceiling mounted Fire extinguiser of ABC MAP 90, 5.0 kg stored pressure type at Gandhi Hospital
| V.P 11 AB No 010 |  |  |  |  | 5 | 5 | 6917 | Nos | 34585 |  |  | 5 | 34585 |  |  |  | 90% | 7686
147 | Supply and Installtion of 2.0 kg clean agent HCFC 123 Fire Extinguiser at Gandhi Hospital
| V.P 12 AB No 010 |  |  |  |  | 5 | 5 | 13559 | Nos | 67795 |  |  | 5 | 67795 |  |  |  | 90% | 15065
148 | Supply and Installaion of Fire escape signage Boards at Gandhi Hospital
| V.P 12 AB No 010 |  |  |  |  | 1 | 1 | 50400 | Job | 50400 |  |  | 1 | 50400 |  |  |  | 90% | 56000
94 | Air Shower Supply and installation,testing and commissioning of 16 GI Power coated Suitable single person entry air shower
| V.P 12 AB No 010 |  |  |  |  | 1 | 1 | 319500 | Job | 319500 |  |  | 1 | 319500 |  |  |  | 90% | 355000
95 | Supply and installation,testing and commissioning of Static Pass Boxes Of Size 450 x 450mm with 1.2mm thick SS 304 Mat finish, with interlock doors, UV light on When Doors Closed Condition. As per Clean room standard and requirements
| V.P 12 AB No 010 |  |  |  |  | 3 | 3 | 54900 | Job | 164700 |  |  | 3 | 164700 |  |  |  | 90% | 61000
Copper Pipe
178 | Supply installation,Testing and Commissioning of Hard Copper REFRIGERANT PIPING of 16 swg various sizes with necessary supports,fittings, interconnecting the liquid and suction lines between the indoor units. The piping shall be carried out of hard drawn copper pipes of type K with soldered/brazed socket fittings.Isolate each compressor, stainers,sight glass and any other componenet requiring proper operation and maintanance.Both the suction and liquid lines sahll be insulated with 19mm thick closed cell insulation for above 25mm dia,13mm thick for pipes below 25mm dia. the insulation finished with treated woven glass fiber reinforced covering for inside piping and including making required holes in the wall and re finishing and water tight of holes after laying holes as per the specifications and approved drawings at Gandhi Hospital
| V.P 12 AB No 010 |  |  |  |  | 1 | 1 | 360000 | Job | 360000 |  |  | 1 | 360000 |  |  |  | 90% | 400000
179 | Supply, Installation, Testing and Commissioning of refnet joints to be provided in refrigerant pipe line. Maretial of construction for fittings shall be similar to refrigerant piping.At Gandhi Hospital
| V.P 12 AB No 010 |  |  |  |  | 11 | 10 | 5572 | Nos | 55720 |  |  | 10 | 55720 |  |  |  | 90% | 6191
[6 empty] | AE | 1
Electrical -2
137 | SITC of IVF Center Main Panel Indoor IP-42 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with /without detachable extension type structure with all type of suitable switching accessories & bus-bar as per load requirement of respective IVF equipment’s. (Which is including Lighting, power DBs & UPS)
| V.P 13 AB No 010 |  |  |  |  | 1 | 1 | 355000 | Nos | 355000 |  |  | 1 | 355000 |  |  |  |  | 355000
138 | SITC of IVF center AC Panel outdoor IP-54 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with / without detachable extension type structure with all type of suitable switching accessories & bus-bar as per load requirement of respective AC equipment’s. (Which is including 1nos AHU’s stater with VFD by pass, Heater, ODU & VRF system)
| V.P 13 AB No 010 |  |  |  |  | 1 | 1 | 270000 | Nos | 270000 |  |  | 1 | 270000 |  |  |  |  | 270000
139 | Supply & installation of AHUs stater on/off push button station for Remote control for inside IVF center with control wiring from AC panel to on /off push button station with necessary items.
| V.P 13 AB No 010 |  |  |  |  | 3 | 3 | 1540 | Nos | 4620 |  |  | 3 | 4620 |  |  |  |  | 1540
136 | Supply, Laying & testing of 4Cx4 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
| V.P 13 AB No 010 |  |  |  |  | 125 | 80 | 356 | Rmt | 28480 |  |  | 80 | 28480 |  |  |  |  | 356
[6 empty] | AE | 45 |  | Rmt | 0 |  |  | 45 | 0
135 | Supply, Laying & testing of 4Cx6 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
| V.P 14 AB No 010 |  |  |  |  | 53 | 53 | 484 | Rmt | 25652 |  |  | 53 | 25652 |  |  |  |  | 484
134 | Supply, Lying & testing of 4Cx16 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
| V.P 14 AB No 010 |  |  |  |  | 60 | 60 | 1483 | Rmt | 88980 |  |  | 60 | 88980 |  |  |  |  | 1483
130 | Supply & installation of 25x3 Copper flat for Neutral earthing of UPS & Equipment which is laid in 100mm cable tray
| V.P 14 AB No 010 |  |  |  |  | 65.3 | 65.3 | 902 | Rmt | 58900.6 |  |  | 65.3 | 58900.6 |  |  |  |  | 902
129 | Supply & installation of 25x3 GI flat for body earthing of DBs & Cable tray which is laid in 100mm cable tray
| V.P 14 AB No 010 |  |  |  |  | 52.4 | 52.4 | 163 | Rmt | 8541.2 |  |  | 52.4 | 8541.2 |  |  |  |  | 163
127 | Providing and Fixing maintenance free earthing which consists of copper. Earth station, with 600X600X3.15mm Copper Plate at 2500mm Depth including construction of brick pedestal, providing meshed funnel, GI cover and other civil Engineering works, spreading a homogenous mixture of salt, charcoal around the pipe etc., completely as per IS 3043, 1987 or latest revision. Earthing testing should be done as per IE Rules like Earth valve test Etc.
| V.P 14 AB No 010 |  |  |  |  | 2 | 2 | 22283 | Nos | 44566 |  |  | 2 | 44566 |  |  |  |  | 22283
126 | Providing and Fixing maintenance free earthing which consists of G.I. Earth station, with 600X600X3.15mm GI Plate at 2500mm Depth including construction of brick pedestal, providing meshed funnel, GI cover and other civil Engineering works, spreading a homogenous mixture of salt, charcoal around the pipe etc., completely as per IS 3043, 1987 or latest revision. Earthing testing should be done as per IE Rules like Earth valve test Etc.
| V.P 14 AB No 010 |  |  |  |  | 2 | 2 | 8500 | Nos | 17000 |  |  | 2 | 17000 |  |  |  |  | 8500
121 | SITC of Hot dip galvanized perforated cable tray of 100 mm Wide sizes for to run the cable from DBs to SBs & sockets and AC panel to Units units. All necessary supports & accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. ( Elec 4.10.1 d)
| V.P 15 AB No 010 |  |  |  |  | 36.2 | 36.2 | 429 | Rmt | 15529.8 |  |  | 36.2 | 15529.8 |  |  |  |  | 429
120 | Supply & installation of 225mm Light duty exhaust fan with metal blades etc complete Makes: Havells Ventilair-DB
| V.P 15 AB No 010 |  |  |  |  | 4 | 4 | 2203 | Nos | 8812 |  |  | 4 | 8812 |  |  |  |  | 2203
112 | Providing and fixing of 125A 25KA TPN Thermal Magnetic Release Based MCCB & Terminal Spreaders in Existing panel board with 1 No. and 1 Set of Indication Lamps, LED type, R,Y,B and breaker 'ON' , 'OFF', 'TRIP' & spring charged lamps. and replace with above Mentioned with required Drilling Holes, removing & Making Busbar connections etc, as required. Makes: Legrand / Schneider/ABB/L&T/C&S
| V.P 15 AB No 010 |  |  |  |  | 1 | 1 | 28883 | Nos | 28883 |  |  | 1 | 28883 |  |  |  |  | 28883
108 | Supply and fixing of DP Metal Enclosure with IP 20 Protection DB Make with 1 No 20A, 10 KA DP MCB Make: Legrand / Schneider including internal connection and labour charges for Flush Mounting etc., complete. Makes: Legrand
| V.P 15 AB No 010 |  |  |  |  | 1 | 1 | 2562 | Nos | 2562 |  |  | 1 | 2562 |  |  |  |  | 2562
sup | Supply and Transportation 56W Clean room Light fixture, 2' x2' (600mm x600mm) LED luminaire CRCA powder coated white after phosphocreatine treatment provided as standard. with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% etc., complete. MAKE: OSRAM / Wipro / Crompton / Bajaj / Havells
| V.P 16 AB No 010 |  |  |  |  | 12 | 12
sup | Supply and Transportation of 48" ( 1200 mm) High Speed Fan Sweep Celing Fan with all accessories etc., complete. Make Havells S S 390
| V.P 16 AB No 010 |  |  |  |  | 14 | 14
sup | Labour Charges for fixing of 48" Celing fan
| V.P 16 AB No 010 |  |  |  |  | 14 | 14
sup | Supply and fixing of Anchor Fastner
| V.P 16 AB No 010 |  |  |  |  | 14 | 14
sup | Supply & fixing of 2nos6A, 2 in one socket - 2 Nos with 6A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benz Plus
| V.P 17 AB No 010 |  |  |  |  | 30 | 30
sup | Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete
| V.P 17 AB No 010 |  |  |  |  | 14 | 14
sup | Supply and fixing of 15" Heavy Duty Exfan Make Almonard
| V.P 17 AB No 010 |  |  |  |  | 1 | 1
Sup | Supply and fixing of 63 Amps 4 pole MCB in metal enclouser
| V.P 17 AB No 010 |  |  |  |  | 1 | 1
Civil -2
56 | Plastering 20mm thick in two coats using screened sand with base coat of 8mm thick in CM (1:6) and top coat of 4mm thick in CM (1:4) with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales & other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and overheads & contractors profit complete for finished item of work. (SS 901,903 & 904).
| V.P 18 MB No 010 |  |  |  |  | 11.04 | 11.04 | 969 | Sqm | 10697.76 |  |  |  |  | 11.04 | 10697.76 |  | 90% | 1077
77 | Supplying and fixing of SWR PVC pipes (Prince/Sudhakar/Kisan/Supreme or any ISI brand) 4 Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, overheads & contractors profit complete for finished item of work at all floor levels. (APSS No. 1302 1319 & 1326)
| V.P 18 MB No 010 |  |  |  |  | 26.63 | 26.63 | 400 | Rmt | 10652 |  |  |  |  | 26.63 | 10652 |  | 90% | 444
75 | Supply and fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings SDR 13.5 to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" to 2") for hot and cold water (IS 15778:2007) including cost and conveyance of all materials to site, labour charges for fixing, overheads & contractors profit complete for finished item of work at all floor levels.
| V.P 18 MB No 010 |  |  |  |  | 105.4 | 75 | 206 | Rmt | 15450 |  |  |  |  | 75 | 15450 |  | 90% | 229
[7 empty] | 30.4 |  | Rmt | 0 |  |  |  |  | 30.4 | 0
81 | Supply, installation and commissioning approved make floor mounted Anglo Indian wash down EWC conforming to IS: 2556 part8-2004 suit with P or S trap with dual flush porcelain cistren fixed on wash down EWC with all intenal parts of dual flush cistren. ultra solid seat cover of approved make with rubber buffer and cap and 15mm angle stop cock and 450mm long PVC iner connection pipe wall flanges all of approved make etc. Complete for finished item of work
| V.P 18 MB No 010 |  |  |  |  | 4 | 4 | 6831 | Nos | 27324 |  |  |  |  | 4 | 27324 |  | 90% | 7590
80 | Supplying and fixing Indian make Flat Back Wash Hand Basin 1st quality conforming to IS:2556-Part-4:1972 of size 550mm x 400mm with 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make heavy duty complete with standard CI brackets including wooden blocks ,1 No.12.70mm PVC connection with brass union nuts CP coated , angle stop cock 12.70mm dia. first quality Indian make heavy duty, 30mm dia. PVC flexible waste pipe 914.4mm length of 1st quality including cost and conveyance of all materials to site, labour charges , overheads & contractors profit for finished item of work.
| V.P 18 MB No 010 |  |  |  |  | 4 | 4 | 3420 | Nos | 13680 |  |  |  |  | 4 | 13680 |  | 90% | 3800
83 | Supplying and fixing CP finish brass soap dish of approved make ISI quality including cost and conveyance of all materials, labour charges for fixing, overheads & contractors profit for finished item of work
| V.P 18 MB No 010 |  |  |  |  | 4 | 4 | 785 | Nos | 3140 |  |  |  |  | 4 | 3140 |  | 90% | 872
84 | Supplying and fixing TV shape mirror with plastic frame of size 609.6mm x 457.2mm , plywood back with NP screws 1st quality including cost and conveyance of all materials, labour charges , overheads & contractors profit for finished item of work
| V.P 19 MB No 010 |  |  |  |  | 4 | 4 | 654 | Nos | 2616 |  |  |  |  | 4 | 2616 |  | 90% | 727
85 | Supplying and fixing of CP finish steel towel rods 600mm long and 20mm dia with brackets and aluminium screws including cost and conveyance of all materials, labour charges , overheads & contractors profit for finished item of work.
| V.P 19 MB No 010 |  |  |  |  | 4 | 4 | 785 | Nos | 3140 |  |  |  |  | 4 | 3140 |  | 90% | 872
86 | Supplying and fixing 15 mm Steel body CP finish self closing tap push type conforming to IS 1711 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, overheads & contractors profit complete for finished item of work in all floors.
| V.P 19 MB No 010 |  |  |  |  | 4 | 4 | 376 | Nos | 1504 |  |  |  |  | 4 | 1504 |  | 90% | 418
82 | Supplying and fixing Chromium plated finish brass body quarter turn Bibcock cum Health Faucet with 1m long tube and wall hook with necessary fittings etc., complete including cost and conveyance of all materials, labour charges, complete for finished item of work in all floors. at Gandhi Hospital
| V.P 19 MB No 010 |  |  |  |  | 4 | 4 | 4122 | Nos | 16488 |  |  |  |  | 4 | 16488 |  | 90% | 4580
73 | Supplying and fixing 15 mm brass body CP finish bib tap of not less than 300 grams weight screw type full turn with internal/external threaded connection conforming to IS 8931 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, overheads and contractors profit complete for finished item of work in all floors. at Gandhi Hospital
| V.P 19 MB No 010 |  |  |  |  | 1 | 1 | 793 | Nos | 793 |  |  |  |  | 1 | 793 |  | 90% | 881
79 | Supply and fixing of 4 inches 101.6mm multi floor trap with jali -UPVC/SWR pipe fittings as per site requirements with standard practice for all floor including cost and conveyance of all materials to site ,labour charges ,etc,. Complete for finshed item of work at handhi hospital
| V.P 19 MB No 010 |  |  |  |  | 5 | 5 | 198 | Nos | 990 |  |  |  |  | 5 | 990 |  | 90% | 220
58 | Supply and Installation change room Cubicles at Gandhi Hospital GENERAL SPECIFICATIONS: Thickness of compact Laminate:12mm Thick Colour OF HPL Boards,In Single Colour,Size of Cubicle As per DWG, Door Size For Normal Cubicles AS per DWG Overall Height of Cubicle,2105mm Including bottom gap of 100mm,Accessories , Manufacturers standard makes of aluminium , SS Accessories .a Aluminium H Top Rail b. SS Hinges c. SS privacy Thumb turn occupancy indicator d.SS coat hook e. SS Door knob f. Aluminium U Channel g.Aluminium Door Stopper Channel h. Runner lining i.SS Screw And PVC Wall Plugs
| V.P 19 MB No 010 |  |  |  |  | 16.83 | 16.83 | 8150 | Sqm | 137164.5 |  |  |  |  | 16.83 | 137164.5 |  | 90% | 9055
69 | Providing and applying Wall putty of White Cement or Polymer or Cement based of average 1 to 2 mm thickness over plastered surface to prepare the surface even and smooth after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, applying emery paper, Sand the surface, clean & wipe off loose dust, applying knifing paste filler by putty knife / muslin pad, air dry for 2 - 3 hrs, sand with 180 and 320 No., emery paper for the surface preparation including cost and conveyance of all materials to work site and all operational, incidental, labour charges, over heads and contractors profit etc., complete for finished item of work in all floors for Internal walls.
| V.P 20 MB No 010 |  |  |  |  | 1007.4 | 1007.4 | 284 | Sqm | 286101.6 |  |  |  |  | 1007.4 | 286101.6 |  | 90% | 315
71 | Supply and application of one coat water based cement primer of interior grade I and two coats of water based PU paint having anti-bacterial applications content less than 50 grams/litre for internal walls including cost and conveyance of all materials to site, sales and other taxes, incidental, operational and all labour charges etc., and complete for finished item of work in 5th floor. at Gandhi Hospital
| V.P 20 MB No 010 |  |  |  |  | 872.13 | 872.13 | 234 | Sqm | 204078.42 |  |  |  |  | 872.13 | 204078.42 |  | 90% | 260
67 | Providing and fixing in true horizontal level 14 mm - Mineral Fiber sheet 595 x 595 Square / Tegular Fissura fine model edge tiles with a Humidity Resistance of 90percentage RH, Average NRC 0.50, Light Reflectance greater than80percentage, Thermal Conductivity equal to 0.052 to 0.057 w/mk, Fire Performance Class 0/Class 1 using hot dipped Galvanized Steel section exposed surface with pre-coated capping, main Tee of size 24 x 32 mm at every 1200 mm c/c maximum and rotary stitched cross tee of size 24 x 27 mm at every 600 mm c/c and sub-cross tee of size 24 mm x 25 mm at 1200 mm c/c and wall angle of size 19 x 19 mm fixed to periphery of the wall and the above grid is suspended at every 1200 mm c/c in both directions using 2.0 mm thick pre-straightened GI Wire including cost and conveyance of all materials and labour charges such as cutting , fixing of standing of frame work exposing roof making etc., complete for finished item of work in 5th floor. at Gandhi Hospital
| V.P 20 MB No 010 |  |  |  |  | 316.08 | 316.08 | 1472 | Sqm | 465269.76 |  |  |  |  | 316.08 | 465269.76 |  | 90% | 1636
93 | Providing Laying of scratch proof PVC/vinyl flooring of 2mm thickness with proper welded joints air tight along with leveling compound to match the existing flooring levels as per the engineer in charge instructions. Sub floor preparation with self leveling compound. After the sub floor preparation, it should be suitable for ESD Flooring.Rate inclusive of sifting of material and labour charges.at Gandhi Hospital
| V.P 20 MB No 010 |  |  |  |  | 124.84 | 124.84 | 3663 | Sqm | 457288.92 |  |  |  |  | 124.84 | 457288.92 |  | 90% | 4070
160 | SITC of Factory fabricated and boxed ducting using Aluminium Sheets / coils, should be fabricated as per SMACNA, galvanised hardware and supports, silicon sealant at all longitudinal joints, Galvanized /GI Electroplated iron angle flanges for all the joints, bracing angles and minimum 5mm thick neoprene rubber gasket.- Duct pressure testing at 75mm to be carried oubefore insulatiting the duct. pressure testing to be done as per SMACNA. Procedure to be approved by consultant. 22G - 0.8 mm Thick at Gandhi Hospital
| V.P 20 MB No 010 |  |  |  |  | 230.24 | 230.24 | 2093 | Sqm | 481892.32 |  |  |  |  | 230.24 | 481892.32 |  | 90% | 2325
156 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Suction Line at Gandhi Hospital
| V.P 21 MB No 010 |  |  |  |  | 12 | 12 | 1071 | Rmt | 12852 |  |  |  |  | 12 | 12852 |  | 90% | 1190
155 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Liquid Line at Gandhi Hospital
| V.P 21 MB No 010 |  |  |  |  | 10 | 10 | 918 | Rmt | 9180 |  |  |  |  | 10 | 9180 |  | 90% | 1020
158 | SITC of CPVC drain ping with supports, clamps and 9 mm thk. Nitrile rubber tube insulation of the following sizes. Insulation shall have factory laminated glass cloth. 25mm Dia at Gandhi Hospital
| V.P 21 MB No 010 |  |  |  |  | 12 | 12 | 464 | Rmt | 5568 |  |  |  |  | 12 | 5568 |  | 90% | 515
161 | Aluminium low leakage aerofoil design volume control dampers Suitable for manual and motorised operation At Gandhi Hospital
| V.P 21 MB No 010 |  |  |  |  | 1.24 | 1.24 | 14220 | Sqm | 17632.8 |  |  |  |  | 1.24 | 17632.8 |  | 90% | 15800
162 | CBRI approved 16G GI Spring return actuated fire dampers rated for 90 minutes with limit switch. At Gandhi Hospital
| V.P 21 MB No 010 |  |  |  |  | 0.84 | 0.84 | 23310 | Sqm | 19580.4 |  |  |  |  | 0.84 | 19580.4 |  | 90% | 25900
163 | SITC of SS perforated return raiser grilles with 10 microns filters with collar dampers At Gandhi Hospital
| V.P 21 MB No 010 |  |  |  |  | 3.29 | 2 | 23670 | Sqm | 47340 |  |  |  |  | 2 | 47340 |  | 90% | 26300
[7 empty] | 1.29 |  | Sqm | 0 |  |  |  |  | 1.29 | 0
164 | Extruded Al. powder coated EXHAUST / RETURN discrete grilles At Gandhi Hospital
| V.P 22 MB No 010 |  |  |  |  | 1.25 | 1 | 7313 | Sqm | 7313 |  |  |  |  | 1 | 7313 |  | 90% | 8125
[7 empty] | 0.25 |  | Sqm | 0 |  |  |  |  | 0.25 | 0
165 | SITC of Collar Dampers made of Al. extrusions with black powder coating for Grilles / Diffusers At Gandhi Hospital
| V.P 22 MB No 010 |  |  |  |  | 0.72 | 0.72 | 6750 | Sqm | 4860 |  |  |  |  | 0.72 | 4860 |  | 90% | 7550
168 | SITC of Aluminium powder coated Fresh air and Exhaust Louvers of nonvision type with nylon mosquito net etc. At Gandhi Hospital
| V.P 22 MB No 010 |  |  |  |  | 0.12 | 0.12 | 9270 | Sqm | 1112.4 |  |  |  |  | 0.12 | 1112.4 |  | 90% | 10300
169 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 32mm Thick for Exposed Supply Air duct and finished with UV Protective Paint. at Gandhi Hospital
| V.P 22 MB No 010 |  |  |  |  | 119.84 | 119.84 | 1103 | Sqm | 132183.52 |  |  |  |  | 119.84 | 132183.52 |  | 90% | 1225
170 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Exposed Return Air Duct and finished with UV Protective Paint. at Gandhi Hospital
| V.P 22 MB No 010 |  |  |  |  | 84.41 | 84.41 | 968 | sqm | 81708.88 |  |  |  |  | 84.41 | 81708.88 |  | 90% | 1075
171 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Supply air duct running inside the building. at Gandhi Hospital
| V.P 22 MB No 010 |  |  |  |  | 75.04 | 40 | 707 | Sqm | 28280 |  |  |  |  | 40 | 28280 |  | 90% | 785
[6 empty] | AE | 35 |  | Sqm | 0 |  |  |  |  | 35 | 0
172 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 19mm Thick for Return air running inside the building. at Gandhi Hospital
| V.P 22 MB No 010 |  |  |  |  | 19.24 | 19.24 | 594 | Sqm | 11428.56 |  |  |  |  | 19.24 | 11428.56 |  | 90% | 660
87 | Supply and instalaion of Wall Panels 80mm thick double skin Modular wall panels made of .8mm Powder Coated GI on both sides, with 40 plus or minus 2 kg/cum demsity pUF as infill, GI profiles all along the periphery,flush on both sides with maximum allowable gap of 3-4mm filled with food grade silicon sealent and placed on cold rolled galvanised bottom tracks with a recess to provide floor to wall coving flush with the wall panel. This including all required hardware for completion panels to be covered with a protective film to avoid any damages during transpotation and installation at Gandhi Hispital
| V.P 23 MB No 010 |  |  |  |  | 96.75 | 96.75 | 5058 | Sqm | 489361.5 |  |  |  |  | 96.75 | 489361.5 |  | 90% | 5620
88 | Supply and installtion of 50mm thick double skin cealing system made .8mm thich powder coated GI sheet on both sides, 40 plus or minus 2kg/cum density PUF ad infill, GI Profiles all along the periphery, panels flush towards room sides with maximum allowable gap of 3-4mm at panelto panel joints filled with silicon sealent ceiling panels are suspended from the RCC salb bu using concealed Aall ceiling grid with tie rod and adjestable turn bickle arrangement etc. This includes all required hardware for completition. panels to be covered with a protective film to avoid any damge during transpotation and installation at Gandhi Hospital.
| V.P 23 MB No 010 |  |  |  |  | 48.02 | 48.02 | 4622 | Sqm | 221948.44 |  |  |  |  | 48.02 | 221948.44 |  | 90% | 5135
92 | Supply and installation of Extruded Aluminium Coving at Gndhi Hopital
| V.P 23 MB No 010 |  |  |  |  | 63.61 | 63.61 | 527 | Rmt | 33522.47 |  |  |  |  | 63.61 | 33522.47 |  | 90% | 585
90 | Single leaf clean room door 46mm thick flush made of .8mm thick powedr coated GI sheet on both sides 90 pus or minus 2kg/cum density honeycomb with stand upto 220 deg.C temperature ,and compressible strength upto 400 kg/sqm,1.2mm thick GPSP door frames ,double glazed vision panel with necessary adhesive tapes and silicon swalent, necessary hardware like SS304 ball bearing butt hinges D- hnadles,push plates ,Dorma make door closer concealed tower bolt ,drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms,BOth sides lock and key etc,. Complete .
| V.P 23 MB No 010 |  |  |  |  | 3 | 1 | 25830 | Nos | 25830 |  |  |  |  | 1 | 25830 |  | 90% | 28700
[6 empty] | AE | 2 |  | Nos | 0 |  |  |  |  | 2 | 0
89 | Double leaf clean room door 46mm thick flush made of .8mm thick powedr coated GI sheet on both sides 90 pus or minus 2kg/cum density honeycomb with stand upto 220 deg.C temperature ,and compressible strength upto 400 kg/sqm,1.2mm thick GPSP door frames ,double glazed vision panel with necessary adhesive tapes and silicon swalent, necessary hardware like SS304 ball bearing butt hinges D- hnadles,push plates ,Dorma make door closer concealed tower bolt ,drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms,BOth sides lock and key etc,. Complete .
| V.P 23 MB No 010 |  |  |  |  | 5 | 5 | 41400 | Nos | 207000 |  |  |  |  | 5 | 207000 |  | 90% | 46000
91 | Emergency Fire door 46mm thick flush made of .8mm thick powedr coated GI sheet on both sides 90 pus or minus 2kg/cum density honeycomb with stand upto 220 deg.C temperature ,and compressible strength upto 400 kg/sqm,1.2mm thick GPSP door frames ,double glazed vision panel with necessary adhesive tapes and silicon swalent, necessary hardware like SS304 ball bearing butt hinges D- hnadles,push plates ,Dorma make door closer concealed tower bolt ,drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms,BOth sides lock and key etc,. Complete .
| V.P 24 MB No 010 |  |  |  |  | 1 | 1 | 49500 | Nos | 49500 |  |  |  |  | 1 | 49500 |  | 90% | 55000
61 | Supplying and fixing of Unplasticised Poly Vinyl Chloride UPVC 3 track sliding windows with mesh shutter – 2-glass shutters and 1-mesh shutter duly manufactured using UPVC reinforced profiles Composition of profile shall consists a minimum of 5.5 PHR of TiO2 and not more than 12 PHR of CaCo3 for every 100 parts of PVC resin of 94mm x 45 mm/80 mm x 52 mm x 2.20 mm for outer frames, 58 mm x 39 mm/54 mm x 38 mm x 2.20mm for sliding shutter frames capable of mounting single glazing system structurally reinforced with hot dip galvanized up to 50 microns of minimum thickness of 1.0/1.2 mm prefabricated and welded through fusion welding. The window sash shall be fitted with 5 mm thick clear float glass of reputed make and mesh shutter frame shall be 42 mm x 25mm/52 mm x 21.5 mm x 2.0 mm fitted with Vinyl Coated Fiber mesh- on rollers/ pulley duly fixed with Grey colour TPV Gasket for sash and Glazing bead shall be co extruded with Grey colour soft PVC. System shall have single point locking with Touch Lock and the system is to be installed at the site using anchor fasteners, silicon rubber sealant, easy glazing/deglazing at site etc., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site includingetc., complete for finished item of work. at Gandhi Hospital
| V.P 24 MB No 010 |  |  |  |  | 7.88 | 7.88 | 8565 | Sqm | 67492.2 |  |  |  |  | 7.88 | 67492.2 |  | 90% | 9517
62 | Providing, supplying and fixing of Fixed Louvered Ventilator made out of multi chambered uPVC sections with Glazing bead shall be co-extruded with Grey colour soft PVC. having isolated drainage and reinforced with Galvanized Iron profiles throughout the window. The outer frame having an overall size of 60 mm x 55 mm x 2.40 with reinforcement of 1 mm thickness and Mullion with overall size of 74 mm x 60 mm x 2.40 mm with reinforcement of 1 mm thickness. Composition of profile shall consists a minimum of 5.5 PHR of TiO2 and not more than 12 PHR of CaCo3 for every 100 parts of PVC resin. Ventilator shall be provided with 4.5 mm Pin Head glass, standard hardware. Wall thickness of frame and Mullion shall be 2.4 mm., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site etc., complete for finished item of work hinges IS:205 150mm long, 1 No. aldrop IS:2681 300mm long, 1 No. tower bolt IS:204 of 200 mm x 10 mm dia at top, 2 Nos. 150 mm at Gandhi Hospital
| V.P 24 MB No 010 |  |  |  |  | 1.53 | 1.53 | 7708 | Sqm | 11793.24 |  |  |  |  | 1.53 | 11793.24 |  | 90% | 8564
182 | SITC of Oxygen Manifold Emergency for 1 plus 1 Cylinders, as per technical specifications. At Gandhi Hospital
| V.P 24 MB No 010 |  |  |  |  | 1 | 1 | 18675 | Set | 18675 |  |  |  |  | 1 | 18675 |  | 90% | 20750
183 | SITC of Oxygen Outlets with matching probes, as per HTM-2022/02-01 of UK/NFPA99C of USA as per enclosed technical specifications - Imported At Gandhi Hospital
| V.P 24 MB No 010 |  |  |  |  | 6 | 4 | 2255 | Nos | 9020 |  |  |  |  | 4 | 9020 |  | 90% | 2506
[6 empty] | AE | 2 |  | Nos | 0 |  |  |  |  | 2 | 0
184 | SITC of Oxygen Flow meter with Humidifier, CE Certified with four digit number as per enclosed technical specifications - Imported At Gandhi Hospital
| V.P 25 MB No 010 |  |  |  |  | 6 | 4 | 1625 | Nos | 6500 |  |  |  |  | 4 | 6500 |  | 90% | 1805
[6 empty] | AE | 2 |  | Nos | 0 |  |  |  |  | 2 | 0
185 | SITC of Nitrous Oxide Manifold Emergency for 1 Cylinder, with high pressure Regulator, NRV, tailpipes etc. as per technical specifications At Gandhi Hospital
| V.P 25 MB No 010 |  |  |  |  | 1 | 1 | 11925 | Set | 11925 |  |  |  |  | 1 | 11925 |  | 90% | 13250
186 | SITC of N20 Outlets with matching probes, as per HTM-2022/02-01 of UK/NFPA99C of USA as per enclosed technical specifications - Imported At Gandhi Hospital
| V.P 25 MB No 010 |  |  |  |  | 4 | 4 | 2255 | Nos | 9020 |  |  |  |  | 4 | 9020 |  | 90% | 2506
187 | SITC of C02 Manifold for 2 Cylinders, with high pressure Regulator, NRV, tailpipes etc. as per technical specifications At Gandhi Hospital
| V.P 25 MB No 010 |  |  |  |  | 1 | 1 | 18675 | Set | 18675 |  |  |  |  | 1 | 18675 |  | 90% | 20750
188 | SITC of C02 Outlets with matching probes, as per HTM-2022102-01ofUK/NFPA99C of USA as per enclosed technical specifications - Imported At Gandhi Hospital
| V.P 25 MB No 010 |  |  |  |  | 6 | 4 | 2255 | Nos | 9020 |  |  |  |  | 4 | 9020 |  | 90% | 2506
[6 empty] | AE | 2 |  | Nos | 0 |  |  |  |  | 2 | 0
189 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 12mm COPPER PIPE at Gandhi Hospital
| V.P 25 MB No 010 |  |  |  |  | 38.3 | 24 | 578 | Rmt | 13872 |  |  |  |  | 24 | 13872 |  | 90% | 642
[6 empty] | AE | 14.3 |  | Rmt | 0 |  |  |  |  | 14.3 | 0
190 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 15mm COPPER PIPE at Gandhi Hospital
| V.P 25 MB No 010 |  |  |  |  | 157.7 | 114 | 742 | Rmt | 84588 |  |  |  |  | 114 | 84588 |  | 90% | 824
[6 empty] | AE | 43.7 |  | Rmt | 0 |  |  |  |  | 43.7 | 0
191 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 22mm COPPER PIPE at Gandhi Hospital
| V.P 25 MB No 010 |  |  |  |  | 79.5 | 36 | 1072 | Rmt | 38592 |  |  |  |  | 36 | 38592 |  | 90% | 1191
[6 empty] | AE | 43.5 |  | Rmt | 0 |  |  |  |  | 43.5 | 0
192 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 28mm COPPER PIPE at Gandhi Hospital
| V.P 26 MB No 010 |  |  |  |  | 27 | 18 | 1326 | Rmt | 23868 |  |  |  |  | 18 | 23868 |  | 90% | 1473
[6 empty] | AE | 9 |  | Rmt | 0 |  |  |  |  | 9 | 0
193 | SITC of Touch type LCD Area Alarm and Zonal Valve box- as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications imported for 3 gases at Gandhi Hospital
| V.P 26 MB No 010 |  |  |  |  | 1 | 1 | 247500 | Nos | 247500 |  |  |  |  | 1 | 247500 |  | 90% | 275000
194 | SITC of Touch type LCD Area Alarm and Zonal Valve box- as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications imported for Master Main Alarm including all Gases at Gandhi Hospital
| V.P 26 MB No 010 |  |  |  |  | 1 | 1 | 337500 | Nos | 337500 |  |  |  |  | 1 | 337500 |  | 90% | 375000
195 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 15mm 0D at Gandhi Hospital
| V.P 26 MB No 010 |  |  |  |  | 8 | 3 | 1744 | Nos | 5232 |  |  |  |  | 3 | 5232 |  | 90% | 1938
[6 empty] | AE | 5 |  | Nos | 0 |  |  |  |  | 5 | 0
196 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 22mm 0D at Gandhi Hospital
| V.P 26 MB No 010 |  |  |  |  | 3 | 3 | 2466 | Nos | 7398 |  |  |  |  | 3 | 7398 |  | 90% | 2740
197 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 28mm 0D at Gandhi Hospital
| V.P 26 MB No 010 |  |  |  |  | 4 | 4 | 3940 | Nos | 15760 |  |  |  |  | 4 | 15760 |  | 90% | 4378
198 | SITC of Bed Head Panel - as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications at Gandhi Hospital
| V.P 26 MB No 010 |  |  |  |  | 2 | 2 | 33075 | Nos | 66150 |  |  |  |  | 2 | 66150 |  | 90% | 36750
[7 empty] | Grand Total |  |  | 37364904.93 |  |  |  | 31912697.18 |  | 4647839.75
[7 empty] | Add GST @ 18% |  |  | 6725683 |  |  |  | 5744285 |  | 836611
[7 empty] | Grand Total |  |  | 44090587.93 |  |  |  | 37656982 |  | 5484450.75
Seignoirage Charges
Certificate
|  | Qty | Sand | Metal | Brick
1 | Brick work | 6.24 |  |  | 540 |  | 1 | The work is in progress in according with the specification drawing and terms and condition the agreement.
5 | Plastering 12mm | 11.04 | 1.14 |  |  |  | 2 | No recoveries are due for recovery from the contractor other than those propsed in the bill
|  |  | 1.14 | 0 | 540 |  | 3 | There are no further dues to be recovery from the contractor
|  |  | @ | @ | @ |  | 4 | The contractor has conveyneced the materieals for use on the work as per the lead statement approved the agreement.
|  |  | 44 | 75 | 60/1000 |  | 5 | The leads and lifts are cveried in the contractor.
|  |  | 50 | 0 | 32 |  |  | Sumited to the Exective Engineer TSMSIDC Raga Reddy Division for favor of pri audit and payment
| Total:- | 82
| Previous | 11134
| Grand Total | 11216
| Net | 82

## Abs -5cc
CC 5th & Part Bill
| Name of the work:Design, Fabriction, establishing and commissioning of In - Vitro ferility centers (IVFC) alongwith allied Services on Turnkey basis at Gandhi hospital secunderabad. | [6 empty] | Agency: M/s. Asta Vardhman Consortium | [5 empty] | Agt.No: 344/A/TSMIDC/Spl.Proj/IVFCs/2022-23,Dt.05.07.2023
S.No | Discription Of Work etc., | Measurements Upto date | [6 empty] | Per | Total Volume |  | Deduct/previous Measurements |  | Since last measurement |  |  | Remarks
|  | No | L | B | D | Content | Rs | Ps. |  | Rs. | Ps | P.No. | Qty. | Qty | Value
[15 empty] | Rs. | Ps.
49 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete (Brick Masonary)
(Brick Masonary)
[6 empty] | 31.21 | 398 | Cum | 12422 |  |  | 31.21 | 12422 | 0
Old Cement Morter
[6 empty] | 37.13 | 8 | Sqm | 297 |  |  | 37.13 | 297 | 0
Unreinforcement Cement More Than 15cm
[6 empty] | 3.89 | 2842 | Cum | 11055 |  |  | 3.89 | 11055 | 0
Reinforcement Cement
[6 empty] | 0.7 | 3115 | Cum | 2181 |  |  | 0.7 | 2181 | 0
51 | Dismantling doors, windows and clear storey windows, Ventilators etc., (wood or steel) shutters including Chowkhats, architraves,hold fasts and other attachments etc., and stacking them within 100m lead including labour charge etc., and overheads & contractors profit complete for finished item of work.
[6 empty] | 5 | 468 | Each | 2340 |  |  | 5 | 2340 | 0
[5 empty] | AE | 2 |  | Each | 0 |  |  | 2 | 0 | 0
53 | Masonry work in CM (1:8) prop (cement: Screened sand) in super structure with / lime solid blocks of size 290mmx225mmx140mm from approved source having minimum crushing strength of 50 Kg/Sqcm including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, including sales & other taxes on all materials, all operational, incidental and labour charges such as mixing cement mortar, constructing masonry, scaffolding charges, lift charges, curing, etc., complete but excluding seigniorage charges for finished item of work. (APSS No. 501 & 504).
[6 empty] | 9.03 | 16055 | Cum | 144977 |  |  | 9.03 | 144977 | 0
54 | Reinforced brick Masonry for Partition Walls (11.0 cm thick) in CM (1:4) prop (cement: Screened sand) in super structure with / lime solid blocks of size 290mmx225mmx140mm from approved source having minimum crushing strength of 50 Kg/Sqcm including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, including sales & other taxes on all materials, all operational, incidental and labour charges such as mixing cement mortar, constructing masonry, scaffolding charges, lift charges, curing, etc., complete but excluding seigniorage charges for finished item of work. (APSS No. 501 & 504).
[6 empty] | 191.0305 | 1952 | Sqm | 372892 |  |  | 191.0305 | 372892 | 0
55 | Providing Thermo Mechanically Treated ( TMT) ( Fe-500/500D/550D from primery producer TATA, SAIL, VSP, JSW Steel, Goel steel, Jindal panther, X- Vega & balaji Shakthi as per IS 1786-2008) of Different Diameters RCC Works , including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and sizes and typing and lap - spacing with binding wire of 18 SWG, Forming grills for reinforcement work as per approved design and drawings, including and conveyanace of steel bars, including all wastages such as overlaps, coupling, chairs, spacer bars including cost and conveyance of binding wire cover blocks and incidential, operational, labour charges such as cutting bending, placing in position, typing incliding sales and other taxes on all materials etc., and overheads & contractors profit completefor finished item of work
[6 empty] | 0.103 | 116500 | MT | 12000 |  |  | 0.103 | 12000 | 0
Sup | Supply and placing of the Design Mix Concrete M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Weight Batcher / Concrete mixer with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials, centering using Casurina Ballies, Bamboos, Wooden Reapers, Runners, Wood Posts, Steel Plates etc., including all operational, incidental and labour charges such as weigh batching, machine mixing, lifting of concrete manually, laying concrete, curing , overheads & contractors profit etc., complete but excluding cost of steel and its fabrication charges for finished item of work (APSS No. 402) (For Lintels)
[6 empty] | 0.43 | 12775 | Cum | 5493 |  |  | 0.43 | 5493 | 0
56 | Plastering 12mm thick in two coats using screened sand with base coat of 8mm thick in CM (1:6) and top coat of 4mm thick in CM (1:4) with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales & other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and overheads & contractors profit complete for finished item of work. (SS 901,903 & 904).
[6 empty] | 536.1091 | 1041 | Sqm | 558090 |  |  | 536.1091 | 558090 | 0 |  |  |  |  | 22295.5
Sup | Flooring with 16 to 18 mm thick high polished granite stone slabs black colour as approved by the Engineer-in-Charge of length not less than 2.43 mts set over base coat of cement mortar (1:8) , 20mm thick using screened sand over CC bed already laid or RCC roof slab including neat grey cement slurry of honey like consistency spread @ 3.3 Kg per sqm and jointed neatly with white cement paste mixed with pigment of matching shade to full depth including cost and conveyance of all materials like cement , sand , water , granite slabs etc., to work site and all operational, incidental labour & lift charges, half rounding the edge , polishing charges and all other taxes on all materials, cost of base coat and overheads & contractors profit complete for finished item of work for platforms (S.S.701 & special) | [17 empty] | 22295.5
[6 empty] | 10.166 | 6300 | Sqm | 64071 |  |  | 10.166 | 64071 | 0
65 | Flooring with soluble salt porcelain vitrified tiles screen printed and polished of size 600 x 600 mm and thickness between 8 to 10mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630Parts 1 to 15 of any colour and finish in all shades and designs with borders and design as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM 1:8 prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread at the rate 3.3 kgs per Sqm. and jointed neatly with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site excluding cost of C.C. bed including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in- charge etc., and complete for finished item of work. TSSS No.701 and 707. 5th Floor at Gandhi Hospital
[6 empty] | 225 | 1725 | Sqm | 388125 |  |  | 225 | 388125 | 0
[5 empty] | AE | 149.81 |  | Sqm | 0 |  |  | 149.81 | 0 | 0
66 | Flooring with non-skid full body ceramic floor tiles of size 300mm x 300mm and thickness between 7 - 8mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630 Part 1 to 15 of any colour and finish in all shades and designs as approved by Engineer-in-charge, set over base coat of cement mortar 1:8, 12mm thick using screened sand over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread at the rate 3.3 Kgs per Sqm and jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, screened sand , water and tiles etc., complete for finished item of work. TSSS No.701 and 707 at Gandhi Hospital
[6 empty] | 14.618 | 1525 | Sqm | 22296 |  |  | 14.618 | 22296 | 0
68 | Providing dadooing to walls with glazed full body porcelain wall tiles of size 300 x 600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. 5th Floor at Gandhi Hospital
[6 empty] | 40 | 1423 | Sqm | 56920 |  |  | 40 | 56920 | 0
[5 empty] | AE | 63.766 |  | Sqm | 0 |  |  | 63.766 | 0 | 0
Sup | Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707)
[6 empty] | 107.179 | 114 | Rmt | 12219 |  |  | 107.179 | 12219 | 0
Electrical-1
96 | Supply and Fixing of 25mm outer dia medium grade, FRLS with IS:9537 part 3 rigid PVC pipe Concealed in with all required PVC/ Metalic junction boxes a including masonary work and labour charges etc., complete Makes:- Sudhakar / Modi
[6 empty] | 184.1 | 116 | Rmt | 21356 |  |  | 184.1 | 21356 | 0
97 | Supply and Fixing of 25mm outer dia medium grade, FRLS with IS:9537 part 3 rigid PVC pipe with all accessories fixing on wall / ceiling with chromium plated metallic base saddles including all labour charges etc., complete Makes:- Modi
[6 empty] | 500 | 107 | Rmt | 53500 |  |  | 500 | 53500 | 0
[5 empty] | AE | 560.2 |  | Rmt | 0 |  |  | 560.2 | 0 | 0
98 | Wiring with run of 2 of 22/0.3mm (1.5 Sqmm) FRLS / HFFR PVC insulated flexible ISI mark copper cable in existing PVC conduit pipe including Supply and fixing of Jumbo Ceiling rose and 6A/10A ISI Mark 1way Modular switch with required modular box and cover frame in existing Surface or Concealed pipe wiring including cost and conveyance of all material and all labour charges etc., complete for light, Fan, Exhaust fan and bell points in N.R.B. Makes of wires : Polycab (HFFR) Makes of switches :Honeywell Blenge Plus
[6 empty] | 110 | 945 | No | 103950 |  |  | 110 | 103950 | 0
[5 empty] | AE | 9 |  | No | 0 |  |  | 9 | 0 | 0
99 | Supply and fixing of 6A/10A ISI Mark 3/2 pin Modular socket with 6A/10A 1way Modular switch, 3 Module box with cover frame a Common switch board including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B. Makes of switches : Honeywell Blenge Plus
[6 empty] | 12 | 675 | No | 8100 |  |  | 12 | 8100 | 0
[5 empty] | AE | 18 |  | No | 0 |  |  | 18 | 0 | 0
100 | Supply and fixing of 16A switches - 1Nos and 6/16A 2 in one socket - 1Nos Modular type with cover plate and GI switch box fixing on separate board including all labour charges etc., complete. Makes of switches: - Hooney well Benzplus
[6 empty] | 14 | 1040 | No | 14560 |  |  | 14 | 14560 | 0
101 | Supply & fixing of 16A/6A, 2 in one socket - 2 Nos with 16A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benzplus
[6 empty] | 34 | 1755 | No | 59670 |  |  | 34 | 59670 | 0
104 | Supply and Run of 3 of 36/0.3mm (2.50 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
[6 empty] | 540.7 | 177 | Rmt | 95704 |  |  | 540.7 | 95704 | 0
105 | Supply and Run of 3 of 56/0.3mm (4.00 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
[6 empty] | 1170.8 | 255 | Rmt | 298554 |  |  | 1170.8 | 298554 | 0
106 | Supply and Run of 5 of 90/0.3mm (6.0 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
[6 empty] | 60 | 606 | Rmt | 36360 |  |  | 60 | 36360 | 0
[5 empty] | AE | 183.3 |  | Rmt | 0 |  |  | 183.3 | 0 | 0
107 | Supply & run of 5 of 10.0 Sqmm (140/0.3 mm) (3 phases, neutral and earth) FRLS / HFFR PVC insulated flexible copper cable in the existing conduit pipe for run of mains from Power panel board to TPN DB"s with pin type lugs and connections etc., complete. [for PDBs] Makes of wires: Polycab
[6 empty] | 40 | 967 | Rmt | 38680 |  |  | 40 | 38680 | 0
[5 empty] | AE | 105.1 |  | Rmt | 0 |  |  | 105.1 | 0 | 0
109 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand and Supply and Fixing of 1 No., of 40A FP 30mA RCCB as incomer and 12 Nos 6-32 A 10kA SP MCBs Makes: Legrand-DX3 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. (For Lighting DBs) Make Legrand
[6 empty] | 3 | 18325 | No | 54975 |  |  | 3 | 54975 | 0
[5 empty] | AE | 5 |  | No | 0 |  |  | 5 | 0 | 0
110 | Supply and fixing of 8 Way VTPN DB with IP 43 Protection as per IS:13032 with 1 No., of 125A 4P MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted as incomer with 8 Nos of 63A, 10KA, TP MCBs C Curve ISI Mark as Out goings including internal connections and labour charges for FLUSH Mounting etc., complete. Makes : Legrand / Schneider
[6 empty] | 1 | 28460 | No | 28460 |  |  | 1 | 28460 | 0
114 | Supply, transportation and fixing of 24W edge lit LED Down light Square Housing Made of Aluminium alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser Square with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor > 0.9, Surge protection: > 2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI >80, and THD is less than 15% etc., with BIS Certification. Makes: Crompton
[6 empty] | 44 | 2652 | No | 116688 |  |  | 44 | 116688 | 0
115 | Supply and Transportation 36W Edge lit, 2' x2' (600mm x600mm) slim panel LED luminaire Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% etc., complete. Makes: Crompton
[6 empty] | 30 | 4350 | No | 130500 |  |  | 30 | 130500 | 0
[5 empty] | AE | 10 |  | No | 0 |  |  | 10 | 0 | 0
119 | Supply and fixing of Modular type Stepped electronic regulator Makes : GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/ Cabtree Verna/ Million logus / Gold Medal Curve for sweep AC ceiling fans of 1200mm / 1400mm complete with connections.
[6 empty] | 12 | 827 | No | 9924 |  |  | 12 | 9924 | 0
[5 empty] | AE | 2 |  | No | 0 |  |  | 2 | 0 | 0
122 | SITC of Hot dip galvanized perforated cable tray of 300 mm Wide sizes for to run the cable from Floor Panel to Lab Panel & electrical room to AC panel and AC panel to Units. All necessary supports & accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. ( Elec 4.10.1 d)
[6 empty] | 80 | 1310 | Rmt | 104800 |  |  | 80 | 104800 | 0
[5 empty] | AE | 5.4 |  | Rmt | 0 |  |  | 5.4 | 0 | 0
128 | Supply & installation of 50x6 GI flat for body earthing of electrical panel & AC Panel which is laid in 300mm cable tray
[6 empty] | 184.9 | 329 | Rmt | 60832 |  |  | 184.9 | 60832 | 0
129 | Supply & installation of 25x3 GI flat for body earthing of DBs & Cable tray which is laid in 100mm cable tray
[6 empty] | 100 | 163 | Rmt | 16300 |  |  | 100 | 16300 | 0
[5 empty] | AE | 16.3 |  | Rmt | 0 |  |  | 16.3 | 0 | 0
131 | Supply & installation of 4 sqmm Copper wire for Earthing of DBs Equipment
[6 empty] | 80 | 83 | Rmt | 6640 |  |  | 80 | 6640 | 0
[5 empty] | AE | 206 |  | Rmt | 0 |  |  | 206 | 0 | 0
132 | Supply, Lying & testing of 3.5Cx95 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/ Glostar/ Finolex Make of gland & Lungs: HMI/ Commet /Dowell’s
[6 empty] | 83 | 1207 | Rmt | 100181 |  |  | 83 | 100181 | 0
133 | Supply, Lying & testing of 3.5CX50 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/ Universal/ Glostar/ Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
[6 empty] | 40 | 722 | Rmt | 28880 |  |  | 40 | 28880 | 0
149 | Split AC unit 1.5 TR inverter type 3 Star capable of delivering 18000 BTU/hr and above with high wall mounted indoor unit and outdoor condensing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord , built-in stabilizer Voltage range 160- 264 volts and cordless remote control. Makes : Daikin / Thoshiba / O General at Gandhi Hospital
[6 empty] | 2 | 43200 | Nos | 86400 |  |  | 2 | 86400 |  |  |  | 90%
124 | Batteries : Supply and fixing of 12V 65 AH SMF battery including wire leads. Makes: Quanta / Racket / Exide. At Gandhi Hospital
[6 empty] | 32 | 18526 | Nos | 592832 |  |  | 32 | 592832 |  |  |  | 90%
125 | Supply and providing of UPS com Batteri rack for 20 batteries . At Gandhi Hospital
[6 empty] | 1 | 6088 | Nos | 6088 |  |  | 1 | 6088 |  |  |  | 90%
123 | 20 KVA UPS: Supply and installation of 20KVA 3ph in and 3ph out on line UPS system IGBT based rectifier with input power factor correction 32 bit microprocessor based with isolation transformers double conversion, SNMP controls, LCD display, Pure sine wave output, with auto static switch three phase input / Three phase output and modular structure for better thermal technology / cooling facility, with warranty up to three years.Makes: APC / Numeric / Emerson / Fuji Electric At Gandhi Hospital
[6 empty] | 1 | 274500 | Nos | 274500 |  |  | 1 | 274500 |  |  |  | 90%
173 | Condensing units - VRF/VRV System 16 HP: Supply, Installation, Nitrogen testing , Vacuuming and Commissioning of air cooled variable refrigerant flow modular type condensing units, each comprising of multiple scroll compressors all inverter driven, full charge of refrigerant gas R-410a including additional gas filling , lubricating oil and all accessories as per the specifications. The condensing units shall be suitable to work on cooling mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B . The COP of the system shall be greater than 4 under ARI conditions for 100percentage load . The condensing units shall be suitable for operation on 415 plus or minus 10percentage volts, 50Hz, 3 phase AC power supply and , outdoor units to be mounted on MS platform with suitable Vibration Isolation pads to avoid vibrations. All the supports and angle base frame structure to be duly black painted with synthetic epoxy paint. the condensing units shall be of following capacities: The VRF ODU should be capable of working with total capacity of connected indoor units ranging between 100percentage to 140percentage of ODU capacity . COP minimum 3.5. Make : Daikin / LG / O General / Toshiba. 16 HP At Gandhi Hospital
[6 empty] | 1 | 292500 | Nos | 292500 |  |  | 1 | 292500 |  |  |  | 90%
174 | VRF Indoor Units : Hi wall Splits 0.8 TR: Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 0.8 TR At Gandhi Hospital
[6 empty] | 1 | 27630 | Nos | 27630 |  |  | 1 | 27630 |  |  |  | 90%
175 | VRF Indoor Units : Hi wall Splits 1.0 TR: Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.0 TR At Gandhi Hospital
[6 empty] | 4 | 27630 | Nos | 110520 |  |  | 4 | 110520 |  |  |  | 90%
176 | VRF Indoor Units 1.5 TR : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.5 TR At Gandhi Hospital
[6 empty] | 5 | 31500 | Nos | 157500 |  |  | 5 | 157500 |  |  |  | 90%
177 | Cassette Units 3.0 TR : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling mode.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 3.0 TR – 4 way At Gandhi Hospital
[6 empty] | 1 | 45000 | Nos | 45000 |  |  | 1 | 45000 |  |  |  | 90%
3 | DICOM compatible fully digital, compact, portable, Ultrasound Scan Machine Colour Doppler at Gandhi Hospital
[6 empty] | 2 | 1228500 | Nos | 2457000 |  |  | 2 | 2457000 |  |  |  | 90%
27 | Defibrilator at Gandhi Hospital
[6 empty] | 1 | 281250 | Nos | 281250 |  |  | 1 | 281250 |  |  |  | 90%
30 | Anesthasia work station at Gandhi Hospital
[6 empty] | 1 | 843750 | Nos | 843750 |  |  | 1 | 843750 |  |  |  | 90%
31 | Autoclave at Gandhi Hospital
[6 empty] | 1 | 506250 | Nos | 506250 |  |  | 1 | 506250 |  |  |  | 90%
35 | Ultrasound Examination Couch at Gandhi Hospital
[6 empty] | 1 | 73125 | Nos | 73125 |  |  | 1 | 73125 |  |  |  | 90%
2 | IVF Test tube Warmers at Gandhi Hospital
[6 empty] | 2 | 44550 | Nos | 89100 |  |  | 2 | 89100 |  |  |  | 90%
4 | Multipurpose Electro hydraulic with manual override mobile OT Table, with divided leg section suitable for all Gynaecological surgical procedures, complete with 5cm Mattress and corded handset at Gandhi Hospital
[6 empty] | 2 | 507375 | Nos | 1014750 |  |  | 2 | 1014750 |  |  |  | 90%
5 | LED procedure Lights Double dome at Gandhi Hospital
[6 empty] | 1 | 281250 | Nos | 281250 |  |  | 1 | 281250 |  |  |  | 90%
6 | LED procedure Lights Single dome at Gandhi Hospital
[6 empty] | 1 | 168750 | Nos | 168750 |  |  | 1 | 168750 |  |  |  | 90%
14 | IVF Thermometer with Probe
[6 empty] | 1 | 55688 | Nos | 55688 |  |  | 1 | 55688 |  |  |  | 90%
15 | CO2 Cylinder with accessories
[6 empty] | 2 | 45000 | Nos | 90000 |  |  | 2 | 90000 |  |  |  | 90%
26 | Cryocane TA 26 Ltr with wheels
[6 empty] | 2 | 55688 | Nos | 111376 |  |  | 2 | 111376 |  |  |  | 90%
16 | CO2 and O2 Analyzer
[6 empty] | 1 | 340200 | Nos | 340200 |  |  | 1 | 340200 |  |  |  | 90%
17 | PH Meter
[6 empty] | 1 | 84375 | Nos | 84375 |  |  | 1 | 84375 |  |  |  | 90%
19 | Sperm Counting Chamber
[6 empty] | 1 | 68063 | Nos | 68063 |  |  | 1 | 68063 |  |  |  | 90%
20 | Binocular Microscope MLX-B Plus
[6 empty] | 1 | 37125 | Nos | 37125 |  |  | 1 | 37125 |  |  |  | 90%
22 | Clinical Centrifuge machine for Andrology with Acessories
[6 empty] | 1 | 31050 | Nos | 31050 |  |  | 1 | 31050 |  |  |  | 90%
34 | Mulitfunctional Printer
[6 empty] | 1 | 39375 | Nos | 39375 |  |  | 1 | 39375 |  |  |  | 90%
37 | Laptop
[6 empty] | 2 | 103500 | Nos | 207000 |  |  | 2 | 207000 |  |  |  | 90%
23 | DRY Incubator
[6 empty] | 1 | 507375 | Nos | 507375 |  |  | 1 | 507375 |  |  |  | 90%
9 | CO2 Incubators
[6 empty] | 2 | 742500 | Nos | 1485000 |  |  | 2 | 1485000 |  |  |  | 90%
1 | Ovum Aspiration Pumps at Gandhi Hospital
[6 empty] | 2 | 216000 | Nos | 432000 |  |  | 2 | 432000 |  |  |  | 90%
7 | IVF Workstation with LAF at Gandhi Hospital
[6 empty] | 1 | 618750 | Nos | 618750 |  |  | 1 | 618750 |  |  |  | 90%
8 | IVF Anti-vibration Table for Procedure
[6 empty] | 1 | 86625 | Nos | 86625 |  |  | 1 | 86625 |  |  |  | 90%
10 | Trigas Bench Top Incubators for Human Embryo culture
[6 empty] | 1 | 742500 | Nos | 742500 |  |  | 1 | 742500 |  |  |  | 90%
11 | Trinocular Stereozoom Microscope
[6 empty] | 1 | 278100 | Nos | 278100 |  |  | 1 | 278100 |  |  |  | 90%
12 | ICSI Micro Manipulator with Inverted Microscope
[6 empty] | 1 | 2362500 | Nos | 2362500 |  |  | 1 | 2362500 |  |  |  | 90%
13 | IVF Laser System
[6 empty] | 1 | 2304000 | Nos | 2304000 |  |  | 1 | 2304000 |  |  |  | 90%
18 | VOC Meter for ART Lab
[6 empty] | 1 | 658125 | Nos | 658125 |  |  | 1 | 658125 |  |  |  | 90%
21 | Laminar Flow Cabinet with Andrology Work Station
[6 empty] | 1 | 225000 | Nos | 225000 |  |  | 1 | 225000 |  |  |  | 90%
24 | Pipetter and Denudation system
[6 empty] | 1 | 92813 | Nos | 92813 |  |  | 1 | 92813 |  |  |  | 90%
25 | Pharmaceutical Refrigerator
[6 empty] | 1 | 202500 | Nos | 202500 |  |  | 1 | 202500 |  |  |  | 90%
28 | 7 Para Patient Monitor
[6 empty] | 2 | 252000 | Nos | 504000 |  |  | 2 | 504000 |  |  |  | 90%
29 | Suction Machine
[6 empty] | 1 | 44550 | Nos | 44550 |  |  | 1 | 44550 |  |  |  | 90%
32 | Operative Hysteroscopy and Resectoscope Set Machine
[6 empty] | 1 | 1912500 | Nos | 1912500 |  |  | 1 | 1912500 |  |  |  | 90%
33 | Operative Laparoscopy Set
[6 empty] | 1 | 3780000 | Nos | 3780000 |  |  | 1 | 3780000 |  |  |  | 90%
39 | Reception Chair
[6 empty] | 2 | 31050 | Nos | 62100 |  |  | 2 | 62100 |  |  |  | 90%
42 | Consultant Chair
[6 empty] | 3 | 17325 | Nos | 51975 |  |  | 3 | 51975 |  |  |  | 90%
43 | Patient Chair
[6 empty] | 6 | 12375 | Nos | 74250 |  |  | 6 | 74250 |  |  |  | 90%
44 | Small Trolley
[6 empty] | 3 | 35280 | Nos | 105840 |  |  | 3 | 105840 |  |  |  | 90%
45 | Big Trolley
[6 empty] | 3 | 56250 | Nos | 168750 |  |  | 3 | 168750 |  |  |  | 90%
46 | Wall Storage Cabinets
[6 empty] | 8 | 15750 | Nos | 126000 |  |  | 8 | 126000 |  |  |  | 90%
151 | Modular Double skin floor mounted EUROVENT Certified Air Handling Unit 3400CFM / 8.5 TR / 150mm SP made out of 45 plus or minus 2mm thick PUF insulated panels Thermal break aluminium profile frame work with 0.8mm thick pre painted / powder coated inner and outer skins comprising of mixing box with fresh air and return air dampers, pre filters with 10 and 5 microns combination filters in single frame, Interlaced/Intertwined DX Cooling Coil suitable for connecting 2 nos of 8.5TR capacity 1W plus 1S out door condensing units, SS304 drain pan with , blower section with Nicotra / Kruger make direct drive/ Plug type fan, vibration isolators, EFF1 motor and blower section with on/off switches to operate from outside, limit switch for the fan section access door with a view port, fine filter section with 3 microns filters inspection doors for all filter and fan sections and damper at the outlet of unit. Ports for differential pressure gauges across all filters and blower to measure differential pressure. AHU Make : VTS / Systemair, Make - Blower - Nicotra / Kruger ; Motor - Crompton Greaves / Siemens ; Filter - Thermodyne / Freudenberg / Ultrafil at Gandhi Hospital
[6 empty] | 1 | 531000 | Nos | 531000 |  |  | 1 | 531000 |  |  |  | 90%
166 | SITC of Magnehelic gauges across pre and fine filter at AHUs including mounting arrangement, SS nozzles, food grade PVC tubing, etc. At Gandhi Hospital
[6 empty] | 3 | 9450 | Nos | 28350 |  |  | 3 | 28350 |  |  |  | 90%
167 | SITC of Magnehelic gauges to measure the room differential pressures in operation theatres with SS mounting box, SS nozzles, food grade PVC tubing, etc. At Gandhi Hospital
[6 empty] | 2 | 11610 | Nos | 23220 |  |  | 2 | 23220 |  |  |  | 90%
153 | SITC of air cooled condensing units with two scroll compressors, air cooled condenser, power panel, vibration isolating pads, stand for ODU, thermostat, etc. of the following capacities. The nominal capacity of the condensing unit shall be as under. Air cooled condensing unit shall have horizontal discharge. All refrigerant piping accessories sight glass, drier, expansion valve, etc. shall be supplied with the condensing units and suitable to connect above AHUs. Refrigerant shall be R 407C / R 410A. Necessary thermostat, control wiring, etc. shall be included. Derating of the unit shall not be more than 15percentage under 45 deg. C ambient temperature. Condensing unit shall be capable of operating up 50 deg. C ambient temperature. 8.5 TR capacity At Gandhi Hospital
[6 empty] | 2 | 163800 | Nos | 327600 |  |  | 2 | 327600 |  |  |  | 90%
154 | SITC of Flange type, Flame proof FLP duct heaters of 5 kW capacity with Mineral Filled AISI SS304/SS321 Sheathed Tubular Heater with GI Helical fins, Tube dia 8.2mm min and Helical Finn dia 25mm min, enclosed in the frame, FLP Terminal box etc., Nickel Chromium Inner Element, Silicon Sealing to Restrict Moisture pickup, Silver brazed mounting plate etc., and heaters shall be controlled with PID thyrestor controller based on the analog output signal of 0-10 V DC of controller . And this should have saftey thermostat and cutouts and air stat etc. all safety controls. The capacities as follows and sizes of the heaters shall be as per the duct sizes and approved drawing. at Gandhi Hospital
[6 empty] | 1 | 184500 | Nos | 184500 |  |  | 1 | 184500 |  |  |  | 90%
152 | Supply and Installation of AL-powdercoated bottom loading type HEPA filter modules with bewel gear arrangement damper with access from clean room suitable to house the following size flange type HEPA filters including GI pressure plate, GI cleats with bolts and pressure drop & Integrity testing ports into room.Supply and Installation of H14 HEPA filters with 99.995% efficiency of the following sizes 600 X 600 X 150MM - HEPA filter - Module height <=350 mm,600 x 600 x 150 mm - 1000 CFM,600 x 600 x 150 mm - 1000 CFM
[6 empty] | 6 | 37800 | Nos | 226800 |  |  | 6 | 226800 |  |  |  | 90%
140 | Supply, Installation, testing And Commissioning of 20 nos LAN points with cat 6 cable and with suitable network rack and 5 nos of telephone points with knore box to existing EPABEX. At Gandhi Hospital
[6 empty] | 1 | 344700 | Job | 344700 |  |  | 1 | 344700 |  |  |  | 90%
141 | Supply, Installation, testing And Commissioning of 1 no of Access control system with egress switch, power cable communication cable to control panel with necessary required items etc,. At Gandhi Hospital
[6 empty] | 1 | 111600 | Nos | 111600 |  |  | 1 | 111600 |  |  |  | 90%
142 | Supply, Installation, testing And Commissioning of Automatic Fire Alaram system which is including 30 nos of smoke detectors 1nos manual call point 1 nos hooter with fire alaram cable connected to the existing fire control panel with necessary required item etc,. At Gandhi Hospital
[6 empty] | 1 | 459000 | Job | 459000 |  |  | 1 | 459000 |  |  |  | 90%
143 | Supply, Installation, testing And Commissioning of 5 nos IP Based CCTV camers and cat 6 cable with NVR system. At Gandhi Hospital
[6 empty] | 1 | 163800 | Job | 163800 |  |  | 1 | 163800 |  |  |  | 90%
144 | Supply, Installation, testing And Commissioning of Audio and video recording of counseling rooms . At Gandhi Hospital
[6 empty] | 1 | 124200 | Job | 124200 |  |  | 1 | 124200 |  |  |  | 90%
145 | Supply and Installation of fire Extinguisher of CO2 4.5 kg at Gandhi Hospital
[6 empty] | 5 | 10103 | Nos | 50515 |  |  | 5 | 50515 |  |  |  | 90%
146 | Supply and iInstalltion of ceiling mounted Fire extinguiser of ABC MAP 90, 5.0 kg stored pressure type at Gandhi Hospital
[6 empty] | 5 | 6917 | Nos | 34585 |  |  | 5 | 34585 |  |  |  | 90%
147 | Supply and Installtion of 2.0 kg clean agent HCFC 123 Fire Extinguiser at Gandhi Hospital
[6 empty] | 5 | 13559 | Nos | 67795 |  |  | 5 | 67795 |  |  |  | 90%
148 | Supply and Installaion of Fire escape signage Boards at Gandhi Hospital
[6 empty] | 1 | 50400 | Job | 50400 |  |  | 1 | 50400 |  |  |  | 90%
94 | Air Shower Supply and installation,testing and commissioning of 16 GI Power coated Suitable single person entry air shower
[6 empty] | 1 | 319500 | Job | 319500 |  |  | 1 | 319500 |  |  |  | 90%
95 | Supply and installation,testing and commissioning of Static Pass Boxes Of Size 450 x 450mm with 1.2mm thick SS 304 Mat finish, with interlock doors, UV light on When Doors Closed Condition. As per Clean room standard and requirements
[6 empty] | 3 | 54900 | Job | 164700 |  |  | 3 | 164700 |  |  |  | 90%
Copper Pipe
178 | Supply installation,Testing and Commissioning of Hard Copper REFRIGERANT PIPING of 16 swg various sizes with necessary supports,fittings, interconnecting the liquid and suction lines between the indoor units. The piping shall be carried out of hard drawn copper pipes of type K with soldered/brazed socket fittings.Isolate each compressor, stainers,sight glass and any other componenet requiring proper operation and maintanance.Both the suction and liquid lines sahll be insulated with 19mm thick closed cell insulation for above 25mm dia,13mm thick for pipes below 25mm dia. the insulation finished with treated woven glass fiber reinforced covering for inside piping and including making required holes in the wall and re finishing and water tight of holes after laying holes as per the specifications and approved drawings at Gandhi Hospital
[6 empty] | 1 | 360000 | Job | 360000 |  |  | 1 | 360000 |  |  |  | 90%
179 | Supply, Installation, Testing and Commissioning of refnet joints to be provided in refrigerant pipe line. Maretial of construction for fittings shall be similar to refrigerant piping.At Gandhi Hospital
[6 empty] | 11 | 5572 | Nos | 61292 |  |  | 11 | 61292 |  |  |  | 90%
Electrical -2
137 | SITC of IVF Center Main Panel Indoor IP-42 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with /without detachable extension type structure with all type of suitable switching accessories & bus-bar as per load requirement of respective IVF equipment’s. (Which is including Lighting, power DBs & UPS)
[6 empty] | 1 | 355000 | Nos | 355000 |  |  | 1 | 355000
138 | SITC of IVF center AC Panel outdoor IP-54 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with / without detachable extension type structure with all type of suitable switching accessories & bus-bar as per load requirement of respective AC equipment’s. (Which is including 1nos AHU’s stater with VFD by pass, Heater, ODU & VRF system)
[6 empty] | 1 | 270000 | Nos | 270000 |  |  | 1 | 270000
139 | Supply & installation of AHUs stater on/off push button station for Remote control for inside IVF center with control wiring from AC panel to on /off push button station with necessary items.
[6 empty] | 3 | 1540 | Nos | 4620 |  |  | 3 | 4620
136 | Supply, Laying & testing of 4Cx4 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
[6 empty] | 80 | 356 | Rmt | 28480 |  |  | 80 | 28480
[5 empty] | AE | 45 |  | Rmt | 0 |  |  | 45 | 0
135 | Supply, Laying & testing of 4Cx6 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
[6 empty] | 53 | 484 | Rmt | 25652 |  |  | 53 | 25652
134 | Supply, Lying & testing of 4Cx16 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
[6 empty] | 60 | 1483 | Rmt | 88980 |  |  | 60 | 88980
130 | Supply & installation of 25x3 Copper flat for Neutral earthing of UPS & Equipment which is laid in 100mm cable tray
[6 empty] | 65.3 | 902 | Rmt | 58900.6 |  |  | 65.3 | 58900.6
129 | Supply & installation of 25x3 GI flat for body earthing of DBs & Cable tray which is laid in 100mm cable tray
[6 empty] | 52.4 | 163 | Rmt | 8541.2 |  |  | 52.4 | 8541.2
127 | Providing and Fixing maintenance free earthing which consists of copper. Earth station, with 600X600X3.15mm Copper Plate at 2500mm Depth including construction of brick pedestal, providing meshed funnel, GI cover and other civil Engineering works, spreading a homogenous mixture of salt, charcoal around the pipe etc., completely as per IS 3043, 1987 or latest revision. Earthing testing should be done as per IE Rules like Earth valve test Etc.
[6 empty] | 2 | 22283 | Nos | 44566 |  |  | 2 | 44566
126 | Providing and Fixing maintenance free earthing which consists of G.I. Earth station, with 600X600X3.15mm GI Plate at 2500mm Depth including construction of brick pedestal, providing meshed funnel, GI cover and other civil Engineering works, spreading a homogenous mixture of salt, charcoal around the pipe etc., completely as per IS 3043, 1987 or latest revision. Earthing testing should be done as per IE Rules like Earth valve test Etc.
[6 empty] | 2 | 8500 | Nos | 17000 |  |  | 2 | 17000
121 | SITC of Hot dip galvanized perforated cable tray of 100 mm Wide sizes for to run the cable from DBs to SBs & sockets and AC panel to Units units. All necessary supports & accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. ( Elec 4.10.1 d)
[6 empty] | 36.2 | 429 | Rmt | 15529.8 |  |  | 36.2 | 15529.8
120 | Supply & installation of 225mm Light duty exhaust fan with metal blades etc complete Makes: Havells Ventilair-DB
[6 empty] | 4 | 2203 | Nos | 8812 |  |  | 4 | 8812
112 | Providing and fixing of 125A 25KA TPN Thermal Magnetic Release Based MCCB & Terminal Spreaders in Existing panel board with 1 No. and 1 Set of Indication Lamps, LED type, R,Y,B and breaker 'ON' , 'OFF', 'TRIP' & spring charged lamps. and replace with above Mentioned with required Drilling Holes, removing & Making Busbar connections etc, as required. Makes: Legrand / Schneider/ABB/L&T/C&S
[6 empty] | 1 | 28883 | Nos | 28883 |  |  | 1 | 28883
108 | Supply and fixing of DP Metal Enclosure with IP 20 Protection DB Make with 1 No 20A, 10 KA DP MCB Make: Legrand / Schneider including internal connection and labour charges for Flush Mounting etc., complete. Makes: Legrand
[6 empty] | 1 | 2562 | Nos | 2562 |  |  | 1 | 2562
96 | Supply and Fixing of 25mm outer dia medium grade, FRLS with IS:9537 part 3 rigid PVC pipe with all accessories fixing on wall / ceiling with chromium plated metallic base saddles including all labour charges etc., complete Makes:- Modi
[6 empty] | 200 | 116 | Rmt | 23200 |  |  | 200 | 23200
[5 empty] | AE | 31.4 |  | Rmt | 0 |  |  | 31.4 | 0
98 | Wiring with run of 2 of 22/0.3mm (1.5 Sqmm) FRLS / HFFR PVC insulated flexible ISI mark copper cable in existing PVC conduit pipe including Supply and fixing of Jumbo Ceiling rose and 6A/10A ISI Mark 1way Modular switch with required modular box and cover frame in existing Surface or Concealed pipe wiring including cost and conveyance of all material and all labour charges etc., complete for light, Fan, Exhaust fan and bell points in N.R.B. Makes of wires : Polycab (HFFR) Makes of switches :Honeywell Blenge Plus
[6 empty] | 27 | 945 | Rmt | 25515 |  |  | 27 | 25515
101 | Supply & fixing of 16A/6A, 2 in one socket - 2 Nos with 16A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benzplus
[6 empty] | 19 | 1755 | Nos | 33345 |  |  | 19 | 33345
105 | Supply and Run of 3 of 56/0.3mm (4.00 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Million(HFFR) / KEI (HFFR) /
[6 empty] | 178.3 | 255 | Nos | 45466.5 |  |  | 178.3 | 45466.5
106 | Supply and Run of 5 of 90/0.3mm (6.0 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Million
[6 empty] | 60 | 606 | Rmt | 36360 |  |  | 60 | 36360
[5 empty] | AE | 30 |  | Rmt | 0 |  |  | 30 | 0
104 | Supply and Run of 3 of 36/0.3mm (2.50 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
[6 empty] | 96.4 | 177 | Rmt | 17062.8 |  |  | 96.4 | 17062.8
sup | Supply and Transportation 56W Clean room Light fixture, 2' x2' (600mm x600mm) LED luminaire CRCA powder coated white after phosphocreatine treatment provided as standard. with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% etc., complete. MAKE: OSRAM / Wipro / Crompton / Bajaj / Havells
12
sup | Supply and Transportation of 48" ( 1200 mm) High Speed Fan Sweep Celing Fan with all accessories etc., complete. Make Havells S S 390
14
sup | Labour Charges for fixing of 48" Celing fan
14
sup | Supply and fixing of Anchor Fastner
14
sup | Supply & fixing of 2nos6A, 2 in one socket - 2 Nos with 6A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benz Plus
30
sup | Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete
14
sup | Supply and fixing of 15" Heavy Duty Exfan Make Almonard
1
Sup | Supply and fixing of 63 Amps 4 pole MCB in metal enclouser
1
Civil -2
49 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete (Brick Masonary)
[6 empty] | 1.47 | 358 | Cum | 526.26 |  |  |  |  | 1.47 | 526.26 |  | 90%
53 | Masonry work in CM (1:6) prop (cement: Screened sand) in super structure with Aerated (Cellular) Autoclaved Concrete Blocks conforming to IS:2185 (Part-3) - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600x 230 x 200 mm from approved source having minimum crushing strength of 3 N/Sq.m including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, including sales & other taxes on all materials, all operational, incidental and labour charges such as mixing cement mortar, constructing masonry, scaffolding charges, lift charges, curing, etc., complete but excluding seigniorage charges for finished item of work. (APSS No. 501 & 504).
[6 empty] | 6.24 | 14450 | Cum | 90168 |  |  |  |  | 6.24 | 90168 |  | 90%
56 | Plastering 20mm thick in two coats using screened sand with base coat of 8mm thick in CM (1:6) and top coat of 4mm thick in CM (1:4) with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales & other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and overheads & contractors profit complete for finished item of work. (SS 901,903 & 904).
[6 empty] | 11.04 | 969 | Sqm | 10697.76 |  |  |  |  | 11.04 | 10697.76 |  | 90%
77 | Supplying and fixing of SWR PVC pipes (Prince/Sudhakar/Kisan/Supreme or any ISI brand) 4 Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, overheads & contractors profit complete for finished item of work at all floor levels. (APSS No. 1302 1319 & 1326)
[6 empty] | 26.63 | 400 | Rmt | 10652 |  |  |  |  | 26.63 | 10652 |  | 90%
75 | Supply and fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings SDR 13.5 to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" to 2") for hot and cold water (IS 15778:2007) including cost and conveyance of all materials to site, labour charges for fixing, overheads & contractors profit complete for finished item of work at all floor levels.
[6 empty] | 75 | 206 | Rmt | 15450 |  |  |  |  | 75 | 15450 |  | 90%
[6 empty] | 23 |  | Rmt | 0 |  |  |  |  | 23 | 0
81 | Supply, installation and commissioning approved make floor mounted Anglo Indian wash down EWC conforming to IS: 2556 part8-2004 suit with P or S trap with dual flush porcelain cistren fixed on wash down EWC with all intenal parts of dual flush cistren. ultra solid seat cover of approved make with rubber buffer and cap and 15mm angle stop cock and 450mm long PVC iner connection pipe wall flanges all of approved make etc. Complete for finished item of work
[6 empty] | 4 | 6831 | Nos | 27324 |  |  |  |  | 4 | 27324 |  | 90%
80 | Supplying and fixing Indian make Flat Back Wash Hand Basin 1st quality conforming to IS:2556-Part-4:1972 of size 550mm x 400mm with 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make heavy duty complete with standard CI brackets including wooden blocks ,1 No.12.70mm PVC connection with brass union nuts CP coated , angle stop cock 12.70mm dia. first quality Indian make heavy duty, 30mm dia. PVC flexible waste pipe 914.4mm length of 1st quality including cost and conveyance of all materials to site, labour charges , overheads & contractors profit for finished item of work.
[6 empty] | 4 | 3420 | Nos | 13680 |  |  |  |  | 4 | 13680 |  | 90%
83 | Supplying and fixing CP finish brass soap dish of approved make ISI quality including cost and conveyance of all materials, labour charges for fixing, overheads & contractors profit for finished item of work
[6 empty] | 4 | 785 | Nos | 3140 |  |  |  |  | 4 | 3140 |  | 90%
84 | Supplying and fixing TV shape mirror with plastic frame of size 609.6mm x 457.2mm , plywood back with NP screws 1st quality including cost and conveyance of all materials, labour charges , overheads & contractors profit for finished item of work
[6 empty] | 4 | 654 | Nos | 2616 |  |  |  |  | 4 | 2616 |  | 90%
85 | Supplying and fixing of CP finish steel towel rods 600mm long and 20mm dia with brackets and aluminium screws including cost and conveyance of all materials, labour charges , overheads & contractors profit for finished item of work.
[6 empty] | 4 | 785 | Nos | 3140 |  |  |  |  | 4 | 3140 |  | 90%
86 | Supplying and fixing 15 mm Steel body CP finish self closing tap push type conforming to IS 1711 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, overheads & contractors profit complete for finished item of work in all floors.
[6 empty] | 4 | 376 | Nos | 1504 |  |  |  |  | 4 | 1504 |  | 90%
82 | Supplying and fixing Chromium plated finish brass body quarter turn Bibcock cum Health Faucet with 1m long tube and wall hook with necessary fittings etc., complete including cost and conveyance of all materials, labour charges, complete for finished item of work in all floors. at Gandhi Hospital
[6 empty] | 4 | 4122 | Nos | 16488 |  |  |  |  | 4 | 16488 |  | 90%
73 | Supplying and fixing 15 mm brass body CP finish bib tap of not less than 300 grams weight screw type full turn with internal/external threaded connection conforming to IS 8931 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, overheads and contractors profit complete for finished item of work in all floors. at Gandhi Hospital
[6 empty] | 1 | 793 | Nos | 793 |  |  |  |  | 1 | 793 |  | 90%
79 | Supply and fixing of 4 inches 101.6mm multi floor trap with jali -UPVC/SWR pipe fittings as per site requirements with standard practice for all floor including cost and conveyance of all materials to site ,labour charges ,etc,. Complete for finshed item of work at handhi hospital
[6 empty] | 5 | 198 | Nos | 990 |  |  |  |  | 5 | 990 |  | 90%
58 | Supply and Installation change room Cubicles at Gandhi Hospital GENERAL SPECIFICATIONS: Thickness of compact Laminate:12mm Thick Colour OF HPL Boards,In Single Colour,Size of Cubicle As per DWG, Door Size For Normal Cubicles AS per DWG Overall Height of Cubicle,2105mm Including bottom gap of 100mm,Accessories , Manufacturers standard makes of aluminium , SS Accessories .a Aluminium H Top Rail b. SS Hinges c. SS privacy Thumb turn occupancy indicator d.SS coat hook e. SS Door knob f. Aluminium U Channel g.Aluminium Door Stopper Channel h. Runner lining i.SS Screw And PVC Wall Plugs
[6 empty] | 16.83 | 8150 | Sqm | 137164.5 |  |  |  |  | 16.83 | 137164.5 |  | 90%
69 | Providing and applying Wall putty of White Cement or Polymer or Cement based of average 1 to 2 mm thickness over plastered surface to prepare the surface even and smooth after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, applying emery paper, Sand the surface, clean & wipe off loose dust, applying knifing paste filler by putty knife / muslin pad, air dry for 2 - 3 hrs, sand with 180 and 320 No., emery paper for the surface preparation including cost and conveyance of all materials to work site and all operational, incidental, labour charges, over heads and contractors profit etc., complete for finished item of work in all floors for Internal walls.
[6 empty] | 1007.4 | 284 | Sqm | 286101.6 |  |  |  |  | 1007.4 | 286101.6 |  | 90%
71 | Supply and application of one coat water based cement primer of interior grade I and two coats of water based PU paint having anti-bacterial applications content less than 50 grams/litre for internal walls including cost and conveyance of all materials to site, sales and other taxes, incidental, operational and all labour charges etc., and complete for finished item of work in 5th floor. at Gandhi Hospital
[6 empty] | 872.09 | 234 | Sqm | 204069.06 |  |  |  |  | 872.09 | 204069.06 |  | 90%
67 | Providing and fixing in true horizontal level 14 mm - Mineral Fiber sheet 595 x 595 Square / Tegular Fissura fine model edge tiles with a Humidity Resistance of 90percentage RH, Average NRC 0.50, Light Reflectance greater than80percentage, Thermal Conductivity equal to 0.052 to 0.057 w/mk, Fire Performance Class 0/Class 1 using hot dipped Galvanized Steel section exposed surface with pre-coated capping, main Tee of size 24 x 32 mm at every 1200 mm c/c maximum and rotary stitched cross tee of size 24 x 27 mm at every 600 mm c/c and sub-cross tee of size 24 mm x 25 mm at 1200 mm c/c and wall angle of size 19 x 19 mm fixed to periphery of the wall and the above grid is suspended at every 1200 mm c/c in both directions using 2.0 mm thick pre-straightened GI Wire including cost and conveyance of all materials and labour charges such as cutting , fixing of standing of frame work exposing roof making etc., complete for finished item of work in 5th floor. at Gandhi Hospital
[6 empty] | 316.08 | 1472 | Sqm | 465269.76 |  |  |  |  | 316.08 | 465269.76 |  | 90%
93 | Providing Laying of scratch proof PVC/vinyl flooring of 2mm thickness with proper welded joints air tight along with leveling compound to match the existing flooring levels as per the engineer in charge instructions. Sub floor preparation with self leveling compound. After the sub floor preparation, it should be suitable for ESD Flooring.Rate inclusive of sifting of material and labour charges.at Gandhi Hospital
[6 empty] | 124.84 | 3663 | Sqm | 457288.92 |  |  |  |  | 124.84 | 457288.92 |  | 90%
52 | Conveyance of un- useful excavated earth to a distance of 21 km for disposal including hire charges of T and P, labour charges etc,. Complete for finished item of work Dismantled Brick Masonary at Gandhi Hospital
[6 empty] | 72.93 | 409 | Sqm | 29828.37 |  |  |  |  | 72.93 | 29828.37 |  | 90%
160 | SITC of Factory fabricated and boxed ducting using Aluminium Sheets / coils, should be fabricated as per SMACNA, galvanised hardware and supports, silicon sealant at all longitudinal joints, Galvanized /GI Electroplated iron angle flanges for all the joints, bracing angles and minimum 5mm thick neoprene rubber gasket.- Duct pressure testing at 75mm to be carried oubefore insulatiting the duct. pressure testing to be done as per SMACNA. Procedure to be approved by consultant. 22G - 0.8 mm Thick at Gandhi Hospital
[6 empty] | 230.19 | 2093 | Sqm | 481787.67 |  |  |  |  | 230.19 | 481787.67 |  | 90%
156 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Suction Line at Gandhi Hospital
[6 empty] | 12 | 1071 | Rmt | 12852 |  |  |  |  | 12 | 12852 |  | 90%
155 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Liquid Line at Gandhi Hospital
[6 empty] | 10 | 918 | Rmt | 9180 |  |  |  |  | 10 | 9180 |  | 90%
158 | SITC of CPVC drain ping with supports, clamps and 9 mm thk. Nitrile rubber tube insulation of the following sizes. Insulation shall have factory laminated glass cloth. 25mm Dia at Gandhi Hospital
[6 empty] | 12 | 464 | Rmt | 5568 |  |  |  |  | 12 | 5568 |  | 90%
161 | Aluminium low leakage aerofoil design volume control dampers Suitable for manual and motorised operation At Gandhi Hospital
[6 empty] | 1.24 | 14220 | Sqm | 17632.8 |  |  |  |  | 1.24 | 17632.8 |  | 90%
162 | CBRI approved 16G GI Spring return actuated fire dampers rated for 90 minutes with limit switch. At Gandhi Hospital
[6 empty] | 0.84 | 23310 | Sqm | 19580.4 |  |  |  |  | 0.84 | 19580.4 |  | 90%
163 | SITC of SS perforated return raiser grilles with 10 microns filters with collar dampers At Gandhi Hospital
[6 empty] | 2 | 23670 | Sqm | 47340 |  |  |  |  | 2 | 47340 |  | 90% | 3.29
[6 empty] | 1.29 |  | Sqm | 0 |  |  |  |  | 1.29 | 0
164 | Extruded Al. powder coated EXHAUST / RETURN discrete grilles At Gandhi Hospital
[6 empty] | 1 | 7313 | Sqm | 7313 |  |  |  |  | 1 | 7313 |  | 90% | 1.25
[6 empty] | 0.25 |  | Sqm | 0 |  |  |  |  | 0.25 | 0
165 | SITC of Collar Dampers made of Al. extrusions with black powder coating for Grilles / Diffusers At Gandhi Hospital
[6 empty] | 0.72 | 6750 | Sqm | 4860 |  |  |  |  | 0.72 | 4860 |  | 90%
168 | SITC of Aluminium powder coated Fresh air and Exhaust Louvers of nonvision type with nylon mosquito net etc. At Gandhi Hospital
[6 empty] | 0.12 | 9270 | Sqm | 1112.4 |  |  |  |  | 0.12 | 1112.4 |  | 90%
169 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 32mm Thick for Exposed Supply Air duct and finished with UV Protective Paint. at Gandhi Hospital
[6 empty] | 119.84 | 1103 | Sqm | 132183.52 |  |  |  |  | 119.84 | 132183.52 |  | 90%
170 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Exposed Return Air Duct and finished with UV Protective Paint. at Gandhi Hospital
[6 empty] | 84.41 | 968 | sqm | 81708.88 |  |  |  |  | 84.41 | 81708.88 |  | 90%
171 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Supply air duct running inside the building. at Gandhi Hospital
[6 empty] | 40 | 707 | Sqm | 28280 |  |  |  |  | 40 | 28280 |  | 90% | 75.04
[5 empty] | AE | 35 |  | Sqm | 0 |  |  |  |  | 35 | 0
172 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 19mm Thick for Return air running inside the building. at Gandhi Hospital
[6 empty] | 19.24 | 594 | Sqm | 11428.56 |  |  |  |  | 19.24 | 11428.56 |  | 90%
87 | Supply and instalaion of Wall Panels 80mm thick double skin Modular wall panels made of .8mm Powder Coated GI on both sides, with 40 plus or minus 2 kg/cum demsity pUF as infill, GI profiles all along the periphery,flush on both sides with maximum allowable gap of 3-4mm filled with food grade silicon sealent and placed on cold rolled galvanised bottom tracks with a recess to provide floor to wall coving flush with the wall panel. This including all required hardware for completion panels to be covered with a protective film to avoid any damages during transpotation and installation at Gandhi Hispital
[6 empty] | 96.75 | 5058 | Sqm | 489361.5 |  |  |  |  | 96.75 | 489361.5 |  | 90%
88 | Supply and installtion of 50mm thick double skin cealing system made .8mm thich powder coated GI sheet on both sides, 40 plus or minus 2kg/cum density PUF ad infill, GI Profiles all along the periphery, panels flush towards room sides with maximum allowable gap of 3-4mm at panelto panel joints filled with silicon sealent ceiling panels are suspended from the RCC salb bu using concealed Aall ceiling grid with tie rod and adjestable turn bickle arrangement etc. This includes all required hardware for completition. panels to be covered with a protective film to avoid any damge during transpotation and installation at Gandhi Hospital.
[6 empty] | 48.02 | 4622 | Sqm | 221948.44 |  |  |  |  | 48.02 | 221948.44 |  | 90%
92 | Supply and installation of Extruded Aluminium Coving at Gndhi Hopital
[6 empty] | 63.61 | 527 | Rmt | 33522.47 |  |  |  |  | 63.61 | 33522.47 |  | 90%
90 | Single leaf clean room door 46mm thick flush made of .8mm thick powedr coated GI sheet on both sides 90 pus or minus 2kg/cum density honeycomb with stand upto 220 deg.C temperature ,and compressible strength upto 400 kg/sqm,1.2mm thick GPSP door frames ,double glazed vision panel with necessary adhesive tapes and silicon swalent, necessary hardware like SS304 ball bearing butt hinges D- hnadles,push plates ,Dorma make door closer concealed tower bolt ,drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms,BOth sides lock and key etc,. Complete .
[6 empty] | 1 | 25830 | Nos | 25830 |  |  |  |  | 1 | 25830 |  | 90% | 3
[5 empty] | AE | 2 |  | Nos | 0 |  |  |  |  | 2 | 0
89 | Double leaf clean room door 46mm thick flush made of .8mm thick powedr coated GI sheet on both sides 90 pus or minus 2kg/cum density honeycomb with stand upto 220 deg.C temperature ,and compressible strength upto 400 kg/sqm,1.2mm thick GPSP door frames ,double glazed vision panel with necessary adhesive tapes and silicon swalent, necessary hardware like SS304 ball bearing butt hinges D- hnadles,push plates ,Dorma make door closer concealed tower bolt ,drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms,BOth sides lock and key etc,. Complete .
[6 empty] | 5 | 41400 | Nos | 207000 |  |  |  |  | 5 | 207000 |  | 90%
91 | Emergency Fire door 46mm thick flush made of .8mm thick powedr coated GI sheet on both sides 90 pus or minus 2kg/cum density honeycomb with stand upto 220 deg.C temperature ,and compressible strength upto 400 kg/sqm,1.2mm thick GPSP door frames ,double glazed vision panel with necessary adhesive tapes and silicon swalent, necessary hardware like SS304 ball bearing butt hinges D- hnadles,push plates ,Dorma make door closer concealed tower bolt ,drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms,BOth sides lock and key etc,. Complete .
[6 empty] | 1 | 49500 | Nos | 49500 |  |  |  |  | 1 | 49500 |  | 90%
61 | Supplying and fixing of Unplasticised Poly Vinyl Chloride UPVC 3 track sliding windows with mesh shutter – 2-glass shutters and 1-mesh shutter duly manufactured using UPVC reinforced profiles Composition of profile shall consists a minimum of 5.5 PHR of TiO2 and not more than 12 PHR of CaCo3 for every 100 parts of PVC resin of 94mm x 45 mm/80 mm x 52 mm x 2.20 mm for outer frames, 58 mm x 39 mm/54 mm x 38 mm x 2.20mm for sliding shutter frames capable of mounting single glazing system structurally reinforced with hot dip galvanized up to 50 microns of minimum thickness of 1.0/1.2 mm prefabricated and welded through fusion welding. The window sash shall be fitted with 5 mm thick clear float glass of reputed make and mesh shutter frame shall be 42 mm x 25mm/52 mm x 21.5 mm x 2.0 mm fitted with Vinyl Coated Fiber mesh- on rollers/ pulley duly fixed with Grey colour TPV Gasket for sash and Glazing bead shall be co extruded with Grey colour soft PVC. System shall have single point locking with Touch Lock and the system is to be installed at the site using anchor fasteners, silicon rubber sealant, easy glazing/deglazing at site etc., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site includingetc., complete for finished item of work. at Gandhi Hospital
[6 empty] | 7.88 | 8565 | Sqm | 67492.2 |  |  |  |  | 7.88 | 67492.2 |  | 90%
62 | Providing, supplying and fixing of Fixed Louvered Ventilator made out of multi chambered uPVC sections with Glazing bead shall be co-extruded with Grey colour soft PVC. having isolated drainage and reinforced with Galvanized Iron profiles throughout the window. The outer frame having an overall size of 60 mm x 55 mm x 2.40 with reinforcement of 1 mm thickness and Mullion with overall size of 74 mm x 60 mm x 2.40 mm with reinforcement of 1 mm thickness. Composition of profile shall consists a minimum of 5.5 PHR of TiO2 and not more than 12 PHR of CaCo3 for every 100 parts of PVC resin. Ventilator shall be provided with 4.5 mm Pin Head glass, standard hardware. Wall thickness of frame and Mullion shall be 2.4 mm., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site etc., complete for finished item of work hinges IS:205 150mm long, 1 No. aldrop IS:2681 300mm long, 1 No. tower bolt IS:204 of 200 mm x 10 mm dia at top, 2 Nos. 150 mm at Gandhi Hospital
[6 empty] | 1.53 | 7708 | Sqm | 11793.24 |  |  |  |  | 1.53 | 11793.24 |  | 90%
182 | SITC of Oxygen Manifold Emergency for 1 plus 1 Cylinders, as per technical specifications. At Gandhi Hospital
[6 empty] | 1 | 18675 | Set | 18675 |  |  |  |  | 1 | 18675 |  | 90%
183 | SITC of Oxygen Outlets with matching probes, as per HTM-2022/02-01 of UK/NFPA99C of USA as per enclosed technical specifications - Imported At Gandhi Hospital
[6 empty] | 4 | 7480 | Nos | 29920 |  |  |  |  | 4 | 29920 |  | 90%
[5 empty] | AE | 2 |  | Nos | 0 |  |  |  |  | 2 | 0
184 | SITC of Oxygen Flow meter with Humidifier, CE Certified with four digit number as per enclosed technical specifications - Imported At Gandhi Hospital
[6 empty] | 4 | 1625 | Nos | 6500 |  |  |  |  | 4 | 6500 |  | 90%
[5 empty] | AE | 2 |  | Nos | 0 |  |  |  |  | 2 | 0
185 | SITC of Nitrous Oxide Manifold Emergency for 1 Cylinder, with high pressure Regulator, NRV, tailpipes etc. as per technical specifications At Gandhi Hospital
[6 empty] | 1 | 11925 | Set | 11925 |  |  |  |  | 1 | 11925 |  | 90%
186 | SITC of N20 Outlets with matching probes, as per HTM-2022/02-01 of UK/NFPA99C of USA as per enclosed technical specifications - Imported At Gandhi Hospital
[6 empty] | 4 | 2255 | Nos | 9020 |  |  |  |  | 4 | 9020 |  | 90%
187 | SITC of C02 Manifold for 2 Cylinders, with high pressure Regulator, NRV, tailpipes etc. as per technical specifications At Gandhi Hospital
[6 empty] | 1 | 18675 | Set | 18675 |  |  |  |  | 1 | 18675 |  | 90%
188 | SITC of C02 Outlets with matching probes, as per HTM-2022102-01ofUK/NFPA99C of USA as per enclosed technical specifications - Imported At Gandhi Hospital
[6 empty] | 4 | 2255 | Nos | 9020 |  |  |  |  | 4 | 9020 |  | 90%
[5 empty] | AE | 2 |  | Nos | 0 |  |  |  |  | 2 | 0
189 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 12mm COPPER PIPE at Gandhi Hospital
[6 empty] | 24 | 578 | Rmt | 13872 |  |  |  |  | 24 | 13872 |  | 90%
[5 empty] | AE | 14.3 |  | Rmt | 0 |  |  |  |  | 14.3 | 0
190 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 15mm COPPER PIPE at Gandhi Hospital
[6 empty] | 114 | 742 | Rmt | 84588 |  |  |  |  | 114 | 84588 |  | 90%
[5 empty] | AE | 43.7 |  | Rmt | 0 |  |  |  |  | 43.7 | 0
191 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 22mm COPPER PIPE at Gandhi Hospital
[6 empty] | 36 | 1072 | Rmt | 38592 |  |  |  |  | 36 | 38592 |  | 90%
[5 empty] | AE | 43.5 |  | Rmt | 0 |  |  |  |  | 43.5 | 0
192 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 28mm COPPER PIPE at Gandhi Hospital
[6 empty] | 18 | 1326 | Rmt | 23868 |  |  |  |  | 18 | 23868 |  | 90%
[5 empty] | AE | 9 |  | Rmt | 0 |  |  |  |  | 9 | 0
193 | SITC of Touch type LCD Area Alarm and Zonal Valve box- as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications imported for 3 gases at Gandhi Hospital
[6 empty] | 1 | 247500 | Nos | 247500 |  |  |  |  | 1 | 247500 |  | 90%
194 | SITC of Touch type LCD Area Alarm and Zonal Valve box- as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications imported for Master Main Alarm including all Gases at Gandhi Hospital
[6 empty] | 1 | 337500 | Nos | 337500 |  |  |  |  | 1 | 337500 |  | 90%
195 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 15mm 0D at Gandhi Hospital
[6 empty] | 3 | 1744 | Nos | 5232 |  |  |  |  | 3 | 5232 |  | 90%
[5 empty] | AE | 5 |  | Nos | 0 |  |  |  |  | 5 | 0
196 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 22mm 0D at Gandhi Hospital
[6 empty] | 3 | 2466 | Nos | 7398 |  |  |  |  | 3 | 7398 |  | 90%
197 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 28mm 0D at Gandhi Hospital
[6 empty] | 4 | 3940 | Nos | 15760 |  |  |  |  | 4 | 15760 |  | 90%
198 | SITC of Bed Head Panel - as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications at Gandhi Hospital
[6 empty] | 2 | 33075 | Nos | 66150 |  |  |  |  | 2 | 66150 |  | 90%
[6 empty] | Grand Total |  |  | 37712086.21 |  |  |  | 33023724.9 |  | 4688361.31
[6 empty] | Add GST @ 18% |  |  | 6788176 |  |  |  | 5944270 |  | 843905
[6 empty] | Grand Total |  |  | 44500262.21 |  |  |  | 38967995 |  | 5532266.31
Certificate
[6 empty] | 1 | The work is in progress in according with the specification drawing and terms and condition the agreement.
[6 empty] | 2 | No recoveries are due for recovery from the contractor other than those propsed in the bill
[6 empty] | 3 | There are no further dues to be recovery from the contractor
[6 empty] | 4 | The contractor has conveyneced the materieals for use on the work as per the lead statement approved the agreement.
[6 empty] | 5 | The leads and lifts are cveried in the contractor.
Sumited to the Exective Engineer TSMSIDC Raga Reddy Division for favor of pri audit and payment

## CC 5th & part
CC 5th & Part Bill
| Name of the work:Design, Fabriction, establishing and commissioning of In - Vitro ferility centers (IVFC) alongwith allied Services on Turnkey basis at Gandhi hospital secunderabad. | [6 empty] | Agency: M/s. Asta Vardhman Consortium | [5 empty] | Agt.No: 344/A/TSMIDC/Spl.Proj/IVFCs/2022-23,Dt.05.07.2023
S.No | Discription Of Work etc., | Measurements Upto date | [6 empty] | Per | Total Volume |  | Deduct/previous Measurements |  | Since last measurement |  |  | Remarks
|  | No | L | B | D | Content | Rs | Ps. |  | Rs. | Ps | P.No. | Qty. | Qty | Value
[15 empty] | Rs. | Ps.
49 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete (Brick Masonary)
(Brick Masonary)
[6 empty] | 31.21 | 398 | Cum | 12422 |  |  | 31.21 | 12422 | 0
Old Cement Morter
[6 empty] | 37.13 | 8 | Sqm | 297 |  |  | 37.13 | 297 | 0
Unreinforcement Cement More Than 15cm
[6 empty] | 3.89 | 2842 | Cum | 11055 |  |  | 3.89 | 11055 | 0
Reinforcement Cement
[6 empty] | 0.7 | 3115 | Cum | 2181 |  |  | 0.7 | 2181 | 0
51 | Dismantling doors, windows and clear storey windows, Ventilators etc., (wood or steel) shutters including Chowkhats, architraves,hold fasts and other attachments etc., and stacking them within 100m lead including labour charge etc., and overheads & contractors profit complete for finished item of work.
[6 empty] | 5 | 468 | Each | 2340 |  |  | 5 | 2340 | 0
[5 empty] | AE | 2 | 374 | Each | 748 |  |  | 2 | 748 | 0
53 | Masonry work in CM (1:8) prop (cement: Screened sand) in super structure with / lime solid blocks of size 290mmx225mmx140mm from approved source having minimum crushing strength of 50 Kg/Sqcm including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, including sales & other taxes on all materials, all operational, incidental and labour charges such as mixing cement mortar, constructing masonry, scaffolding charges, lift charges, curing, etc., complete but excluding seigniorage charges for finished item of work. (APSS No. 501 & 504).
[6 empty] | 9.03 | 16055 | Cum | 144977 |  |  | 9.03 | 144977 | 0
54 | Reinforced brick Masonry for Partition Walls (11.0 cm thick) in CM (1:4) prop (cement: Screened sand) in super structure with / lime solid blocks of size 290mmx225mmx140mm from approved source having minimum crushing strength of 50 Kg/Sqcm including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, including sales & other taxes on all materials, all operational, incidental and labour charges such as mixing cement mortar, constructing masonry, scaffolding charges, lift charges, curing, etc., complete but excluding seigniorage charges for finished item of work. (APSS No. 501 & 504).
[6 empty] | 191.0305 | 1952 | Sqm | 372892 |  |  | 191.0305 | 372892 | 0
55 | Providing Thermo Mechanically Treated ( TMT) ( Fe-500/500D/550D from primery producer TATA, SAIL, VSP, JSW Steel, Goel steel, Jindal panther, X- Vega & balaji Shakthi as per IS 1786-2008) of Different Diameters RCC Works , including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and sizes and typing and lap - spacing with binding wire of 18 SWG, Forming grills for reinforcement work as per approved design and drawings, including and conveyanace of steel bars, including all wastages such as overlaps, coupling, chairs, spacer bars including cost and conveyance of binding wire cover blocks and incidential, operational, labour charges such as cutting bending, placing in position, typing incliding sales and other taxes on all materials etc., and overheads & contractors profit completefor finished item of work
[6 empty] | 0.103 | 116500 | MT | 12000 |  |  | 0.103 | 12000 | 0
Sup | Supply and placing of the Design Mix Concrete M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Weight Batcher / Concrete mixer with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials, centering using Casurina Ballies, Bamboos, Wooden Reapers, Runners, Wood Posts, Steel Plates etc., including all operational, incidental and labour charges such as weigh batching, machine mixing, lifting of concrete manually, laying concrete, curing , overheads & contractors profit etc., complete but excluding cost of steel and its fabrication charges for finished item of work (APSS No. 402) (For Lintels)
[6 empty] | 0.43 | 12775 | Cum | 5493 |  |  | 0.43 | 5493 | 0
56 | Plastering 12mm thick in two coats using screened sand with base coat of 8mm thick in CM (1:6) and top coat of 4mm thick in CM (1:4) with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales & other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and overheads & contractors profit complete for finished item of work. (SS 901,903 & 904).
[6 empty] | 536.1091 | 1041 | Sqm | 558090 |  |  | 536.1091 | 558090 | 0
Sup | Flooring with 16 to 18 mm thick high polished granite stone slabs black colour as approved by the Engineer-in-Charge of length not less than 2.43 mts set over base coat of cement mortar (1:8) , 20mm thick using screened sand over CC bed already laid or RCC roof slab including neat grey cement slurry of honey like consistency spread @ 3.3 Kg per sqm and jointed neatly with white cement paste mixed with pigment of matching shade to full depth including cost and conveyance of all materials like cement , sand , water , granite slabs etc., to work site and all operational, incidental labour & lift charges, half rounding the edge , polishing charges and all other taxes on all materials, cost of base coat and overheads & contractors profit complete for finished item of work for platforms (S.S.701 & special)
[6 empty] | 10.166 | 6300 | Sqm | 64071 |  |  | 10.166 | 64071 | 0
65 | Flooring with soluble salt porcelain vitrified tiles screen printed and polished of size 600 x 600 mm and thickness between 8 to 10mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630Parts 1 to 15 of any colour and finish in all shades and designs with borders and design as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM 1:8 prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread at the rate 3.3 kgs per Sqm. and jointed neatly with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site excluding cost of C.C. bed including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in- charge etc., and complete for finished item of work. TSSS No.701 and 707. 5th Floor at Gandhi Hospital
[6 empty] | 225 | 1725 | Sqm | 388125 |  |  | 225 | 388125 | 0
[6 empty] | 149.81 | 1380 | Sqm | 206738 |  |  | 149.81 | 206738 | 0
66 | Flooring with non-skid full body ceramic floor tiles of size 300mm x 300mm and thickness between 7 - 8mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630 Part 1 to 15 of any colour and finish in all shades and designs as approved by Engineer-in-charge, set over base coat of cement mortar 1:8, 12mm thick using screened sand over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread at the rate 3.3 Kgs per Sqm and jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, screened sand , water and tiles etc., complete for finished item of work. TSSS No.701 and 707 at Gandhi Hospital
[6 empty] | 14.618 | 1525 | Sqm | 22296 |  |  | 14.618 | 22296 | 0
68 | Providing dadooing to walls with glazed full body porcelain wall tiles of size 300 x 600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. 5th Floor at Gandhi Hospital
[6 empty] | 40 | 1423 | Sqm | 56920 |  |  | 40 | 56920 | 0
[6 empty] | 63.766 | 1138 | Sqm | 72566 |  |  | 63.766 | 72566 | 0
Sup | Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707)
[6 empty] | 107.179 | 114 | Rmt | 12219 |  |  | 107.179 | 12219 | 0
Electrical-1
96 | Supply and Fixing of 25mm outer dia medium grade, FRLS with IS:9537 part 3 rigid PVC pipe Concealed in with all required PVC/ Metalic junction boxes a including masonary work and labour charges etc., complete Makes:- Sudhakar / Modi
[6 empty] | 184.1 | 116 | Rmt | 21356 |  |  | 184.1 | 21356 | 0
97 | Supply and Fixing of 25mm outer dia medium grade, FRLS with IS:9537 part 3 rigid PVC pipe with all accessories fixing on wall / ceiling with chromium plated metallic base saddles including all labour charges etc., complete Makes:- Modi
[6 empty] | 500 | 107 | Rmt | 53500 |  |  | 500 | 53500 | 0
[5 empty] | AE | 560.2 | 86 | Rmt | 48177 |  |  | 560.2 | 48177 | 0
98 | Wiring with run of 2 of 22/0.3mm (1.5 Sqmm) FRLS / HFFR PVC insulated flexible ISI mark copper cable in existing PVC conduit pipe including Supply and fixing of Jumbo Ceiling rose and 6A/10A ISI Mark 1way Modular switch with required modular box and cover frame in existing Surface or Concealed pipe wiring including cost and conveyance of all material and all labour charges etc., complete for light, Fan, Exhaust fan and bell points in N.R.B. Makes of wires : Polycab (HFFR) Makes of switches :Honeywell Blenge Plus
[6 empty] | 110 | 945 | No | 103950 |  |  | 110 | 103950 | 0
[5 empty] | AE | 9 | 756 | No | 6804 |  |  | 9 | 6804 | 0
99 | Supply and fixing of 6A/10A ISI Mark 3/2 pin Modular socket with 6A/10A 1way Modular switch, 3 Module box with cover frame a Common switch board including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B. Makes of switches : Honeywell Blenge Plus
[6 empty] | 12 | 675 | No | 8100 |  |  | 12 | 8100 | 0
[5 empty] | AE | 18 | 540 | No | 9720 |  |  | 18 | 9720 | 0
100 | Supply and fixing of 16A switches - 1Nos and 6/16A 2 in one socket - 1Nos Modular type with cover plate and GI switch box fixing on separate board including all labour charges etc., complete. Makes of switches: - Hooney well Benzplus
[6 empty] | 14 | 1040 | No | 14560 |  |  | 14 | 14560 | 0
101 | Supply & fixing of 16A/6A, 2 in one socket - 2 Nos with 16A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benzplus
[6 empty] | 34 | 1755 | No | 59670 |  |  | 34 | 59670 | 0
104 | Supply and Run of 3 of 36/0.3mm (2.50 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
[6 empty] | 540.7 | 177 | Rmt | 95704 |  |  | 540.7 | 95704 | 0
105 | Supply and Run of 3 of 56/0.3mm (4.00 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
[6 empty] | 1170.8 | 255 | Rmt | 298554 |  |  | 1170.8 | 298554 | 0
106 | Supply and Run of 5 of 90/0.3mm (6.0 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
[6 empty] | 60 | 606 | Rmt | 36360 |  |  | 60 | 36360 | 0
[5 empty] | AE | 183.3 | 485 | Rmt | 88901 |  |  | 183.3 | 88901 | 0
107 | Supply & run of 5 of 10.0 Sqmm (140/0.3 mm) (3 phases, neutral and earth) FRLS / HFFR PVC insulated flexible copper cable in the existing conduit pipe for run of mains from Power panel board to TPN DB"s with pin type lugs and connections etc., complete. [for PDBs] Makes of wires: Polycab
[6 empty] | 40 | 967 | Rmt | 38680 |  |  | 40 | 38680 | 0
[6 empty] | 105.1 | 774 | Rmt | 81347 |  |  | 105.1 | 81347 | 0
109 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand and Supply and Fixing of 1 No., of 40A FP 30mA RCCB as incomer and 12 Nos 6-32 A 10kA SP MCBs Makes: Legrand-DX3 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. (For Lighting DBs) Make Legrand
[6 empty] | 3 | 18325 | No | 54975 |  |  | 3 | 54975 | 0
[6 empty] | 5 | 14660 | No | 73300 |  |  | 5 | 73300 | 0
110 | Supply and fixing of 8 Way VTPN DB with IP 43 Protection as per IS:13032 with 1 No., of 125A 4P MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted as incomer with 8 Nos of 63A, 10KA, TP MCBs C Curve ISI Mark as Out goings including internal connections and labour charges for FLUSH Mounting etc., complete. Makes : Legrand / Schneider
[6 empty] | 1 | 28460 | No | 28460 |  |  | 1 | 28460 | 0
114 | Supply, transportation and fixing of 24W edge lit LED Down light Square Housing Made of Aluminium alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser Square with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor > 0.9, Surge protection: > 2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI >80, and THD is less than 15% etc., with BIS Certification. Makes: Crompton
[6 empty] | 44 | 2652 | No | 116688 |  |  | 44 | 116688 | 0
115 | Supply and Transportation 36W Edge lit, 2' x2' (600mm x600mm) slim panel LED luminaire Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% etc., complete. Makes: Crompton
[6 empty] | 30 | 4350 | No | 130500 |  |  | 30 | 130500 | 0
[5 empty] | AE | 10 | 3480 | No | 34800 |  |  | 10 | 34800 | 0
119 | Supply and fixing of Modular type Stepped electronic regulator Makes : GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/ Cabtree Verna/ Million logus / Gold Medal Curve for sweep AC ceiling fans of 1200mm / 1400mm complete with connections.
[6 empty] | 12 | 827 | No | 9924 |  |  | 12 | 9924 | 0
[5 empty] | AE | 2 | 662 | No | 1324 |  |  | 2 | 1324 | 0
122 | SITC of Hot dip galvanized perforated cable tray of 300 mm Wide sizes for to run the cable from Floor Panel to Lab Panel & electrical room to AC panel and AC panel to Units. All necessary supports & accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. ( Elec 4.10.1 d)
[6 empty] | 80 | 1310 | Rmt | 104800 |  |  | 80 | 104800 | 0
[5 empty] | AE | 5.4 | 1048 | Rmt | 5659 |  |  | 5.4 | 5659 | 0
128 | Supply & installation of 50x6 GI flat for body earthing of electrical panel & AC Panel which is laid in 300mm cable tray
[6 empty] | 184.9 | 329 | Rmt | 60832 |  |  | 184.9 | 60832 | 0
129 | Supply & installation of 25x3 GI flat for body earthing of DBs & Cable tray which is laid in 100mm cable tray
[6 empty] | 100 | 163 | Rmt | 16300 |  |  | 100 | 16300 | 0
[5 empty] | AE | 16.3 | 130 | Rmt | 2119 |  |  | 16.3 | 2119 | 0
131 | Supply & installation of 4 sqmm Copper wire for Earthing of DBs Equipment
[6 empty] | 80 | 83 | Rmt | 6640 |  |  | 80 | 6640 | 0
[5 empty] | AE | 206 | 66 | Rmt | 13596 |  |  | 206 | 13596 | 0
132 | Supply, Lying & testing of 3.5Cx95 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/ Glostar/ Finolex Make of gland & Lungs: HMI/ Commet /Dowell’s
[6 empty] | 83 | 1207 | Rmt | 100181 |  |  | 83 | 100181 | 0
133 | Supply, Lying & testing of 3.5CX50 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/ Universal/ Glostar/ Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
[6 empty] | 40 | 722 | Rmt | 28880 |  |  | 40 | 28880 | 0
149 | Split AC unit 1.5 TR inverter type 3 Star capable of delivering 18000 BTU/hr and above with high wall mounted indoor unit and outdoor condensing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord , built-in stabilizer Voltage range 160- 264 volts and cordless remote control. Makes : Daikin / Thoshiba / O General at Gandhi Hospital
[6 empty] | 2 | 43200 | Nos | 86400 |  |  | 2 | 86400 |  |  |  | 90%
124 | Batteries : Supply and fixing of 12V 65 AH SMF battery including wire leads. Makes: Quanta / Racket / Exide. At Gandhi Hospital
[6 empty] | 32 | 18526 | Nos | 592832 |  |  | 32 | 592832 |  |  |  | 90%
125 | Supply and providing of UPS com Batteri rack for 20 batteries . At Gandhi Hospital
[6 empty] | 1 | 6088 | Nos | 6088 |  |  | 1 | 6088 |  |  |  | 90%
123 | 20 KVA UPS: Supply and installation of 20KVA 3ph in and 3ph out on line UPS system IGBT based rectifier with input power factor correction 32 bit microprocessor based with isolation transformers double conversion, SNMP controls, LCD display, Pure sine wave output, with auto static switch three phase input / Three phase output and modular structure for better thermal technology / cooling facility, with warranty up to three years.Makes: APC / Numeric / Emerson / Fuji Electric At Gandhi Hospital
[6 empty] | 1 | 274500 | Nos | 274500 |  |  | 1 | 274500 |  |  |  | 90%
173 | Condensing units - VRF/VRV System 16 HP: Supply, Installation, Nitrogen testing , Vacuuming and Commissioning of air cooled variable refrigerant flow modular type condensing units, each comprising of multiple scroll compressors all inverter driven, full charge of refrigerant gas R-410a including additional gas filling , lubricating oil and all accessories as per the specifications. The condensing units shall be suitable to work on cooling mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B . The COP of the system shall be greater than 4 under ARI conditions for 100percentage load . The condensing units shall be suitable for operation on 415 plus or minus 10percentage volts, 50Hz, 3 phase AC power supply and , outdoor units to be mounted on MS platform with suitable Vibration Isolation pads to avoid vibrations. All the supports and angle base frame structure to be duly black painted with synthetic epoxy paint. the condensing units shall be of following capacities: The VRF ODU should be capable of working with total capacity of connected indoor units ranging between 100percentage to 140percentage of ODU capacity . COP minimum 3.5. Make : Daikin / LG / O General / Toshiba. 16 HP At Gandhi Hospital
[6 empty] | 1 | 292500 | Nos | 292500 |  |  | 1 | 292500 |  |  |  | 90%
174 | VRF Indoor Units : Hi wall Splits 0.8 TR: Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 0.8 TR At Gandhi Hospital
[6 empty] | 1 | 27630 | Nos | 27630 |  |  | 1 | 27630 |  |  |  | 90%
175 | VRF Indoor Units : Hi wall Splits 1.0 TR: Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.0 TR At Gandhi Hospital
[6 empty] | 4 | 27630 | Nos | 110520 |  |  | 4 | 110520 |  |  |  | 90%
176 | VRF Indoor Units 1.5 TR : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.5 TR At Gandhi Hospital
[6 empty] | 5 | 31500 | Nos | 157500 |  |  | 5 | 157500 |  |  |  | 90%
177 | Cassette Units 3.0 TR : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling mode.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 3.0 TR – 4 way At Gandhi Hospital
[6 empty] | 1 | 45000 | Nos | 45000 |  |  | 1 | 45000 |  |  |  | 90%
3 | DICOM compatible fully digital, compact, portable, Ultrasound Scan Machine Colour Doppler at Gandhi Hospital
[6 empty] | 2 | 1228500 | Nos | 2457000 |  |  | 2 | 2457000 |  |  |  | 90%
27 | Defibrilator at Gandhi Hospital
[6 empty] | 1 | 281250 | Nos | 281250 |  |  | 1 | 281250 |  |  |  | 90%
30 | Anesthasia work station at Gandhi Hospital
[6 empty] | 1 | 843750 | Nos | 843750 |  |  | 1 | 843750 |  |  |  | 90%
31 | Autoclave at Gandhi Hospital
[6 empty] | 1 | 506250 | Nos | 506250 |  |  | 1 | 506250 |  |  |  | 90%
35 | Ultrasound Examination Couch at Gandhi Hospital
[6 empty] | 1 | 73125 | Nos | 73125 |  |  | 1 | 73125 |  |  |  | 90%
2 | IVF Test tube Warmers at Gandhi Hospital
[6 empty] | 2 | 44550 | Nos | 89100 |  |  | 2 | 89100 |  |  |  | 90%
4 | Multipurpose Electro hydraulic with manual override mobile OT Table, with divided leg section suitable for all Gynaecological surgical procedures, complete with 5cm Mattress and corded handset at Gandhi Hospital
[6 empty] | 2 | 507375 | Nos | 1014750 |  |  | 2 | 1014750 |  |  |  | 90%
5 | LED procedure Lights Double dome at Gandhi Hospital
[6 empty] | 1 | 281250 | Nos | 281250 |  |  | 1 | 281250 |  |  |  | 90%
6 | LED procedure Lights Single dome at Gandhi Hospital
[6 empty] | 1 | 168750 | Nos | 168750 |  |  | 1 | 168750 |  |  |  | 90%
14 | IVF Thermometer with Probe
[6 empty] | 1 | 55688 | Nos | 55688 |  |  | 1 | 55688 |  |  |  | 90%
15 | CO2 Cylinder with accessories
[6 empty] | 2 | 45000 | Nos | 90000 |  |  | 2 | 90000 |  |  |  | 90%
26 | Cryocane TA 26 Ltr with wheels
[6 empty] | 2 | 55688 | Nos | 111376 |  |  | 2 | 111376 |  |  |  | 90%
16 | CO2 and O2 Analyzer
[6 empty] | 1 | 340200 | Nos | 340200 |  |  | 1 | 340200 |  |  |  | 90%
17 | PH Meter
[6 empty] | 1 | 84375 | Nos | 84375 |  |  | 1 | 84375 |  |  |  | 90%
19 | Sperm Counting Chamber
[6 empty] | 1 | 68063 | Nos | 68063 |  |  | 1 | 68063 |  |  |  | 90%
20 | Binocular Microscope MLX-B Plus
[6 empty] | 1 | 37125 | Nos | 37125 |  |  | 1 | 37125 |  |  |  | 90%
22 | Clinical Centrifuge machine for Andrology with Acessories
[6 empty] | 1 | 31050 | Nos | 31050 |  |  | 1 | 31050 |  |  |  | 90%
34 | Mulitfunctional Printer
[6 empty] | 1 | 39375 | Nos | 39375 |  |  | 1 | 39375 |  |  |  | 90%
37 | Laptop
[6 empty] | 2 | 103500 | Nos | 207000 |  |  | 2 | 207000 |  |  |  | 90%
23 | DRY Incubator
[6 empty] | 1 | 507375 | Nos | 507375 |  |  | 1 | 507375 |  |  |  | 90%
9 | CO2 Incubators
[6 empty] | 2 | 742500 | Nos | 1485000 |  |  | 2 | 1485000 |  |  |  | 90%
1 | Ovum Aspiration Pumps at Gandhi Hospital
[6 empty] | 2 | 216000 | Nos | 432000 |  |  | 2 | 432000 |  |  |  | 90%
7 | IVF Workstation with LAF at Gandhi Hospital
[6 empty] | 1 | 618750 | Nos | 618750 |  |  | 1 | 618750 |  |  |  | 90%
8 | IVF Anti-vibration Table for Procedure
[6 empty] | 1 | 86625 | Nos | 86625 |  |  | 1 | 86625 |  |  |  | 90%
10 | Trigas Bench Top Incubators for Human Embryo culture
[6 empty] | 1 | 742500 | Nos | 742500 |  |  | 1 | 742500 |  |  |  | 90%
11 | Trinocular Stereozoom Microscope
[6 empty] | 1 | 278100 | Nos | 278100 |  |  | 1 | 278100 |  |  |  | 90%
12 | ICSI Micro Manipulator with Inverted Microscope
[6 empty] | 1 | 2362500 | Nos | 2362500 |  |  | 1 | 2362500 |  |  |  | 90%
13 | IVF Laser System
[6 empty] | 1 | 2304000 | Nos | 2304000 |  |  | 1 | 2304000 |  |  |  | 90%
18 | VOC Meter for ART Lab
[6 empty] | 1 | 658125 | Nos | 658125 |  |  | 1 | 658125 |  |  |  | 90%
21 | Laminar Flow Cabinet with Andrology Work Station
[6 empty] | 1 | 225000 | Nos | 225000 |  |  | 1 | 225000 |  |  |  | 90%
24 | Pipetter and Denudation system
[6 empty] | 1 | 92813 | Nos | 92813 |  |  | 1 | 92813 |  |  |  | 90%
25 | Pharmaceutical Refrigerator
[6 empty] | 1 | 202500 | Nos | 202500 |  |  | 1 | 202500 |  |  |  | 90%
28 | 7 Para Patient Monitor
[6 empty] | 2 | 252000 | Nos | 504000 |  |  | 2 | 504000 |  |  |  | 90%
29 | Suction Machine
[6 empty] | 1 | 44550 | Nos | 44550 |  |  | 1 | 44550 |  |  |  | 90%
32 | Operative Hysteroscopy and Resectoscope Set Machine
[6 empty] | 1 | 1912500 | Nos | 1912500 |  |  | 1 | 1912500 |  |  |  | 90%
33 | Operative Laparoscopy Set
[6 empty] | 1 | 3780000 | Nos | 3780000 |  |  | 1 | 3780000 |  |  |  | 90%
39 | Reception Chair
[6 empty] | 2 | 31050 | Nos | 62100 |  |  | 2 | 62100 |  |  |  | 90%
42 | Consultant Chair
[6 empty] | 3 | 17325 | Nos | 51975 |  |  | 3 | 51975 |  |  |  | 90%
43 | Patient Chair
[6 empty] | 6 | 12375 | Nos | 74250 |  |  | 6 | 74250 |  |  |  | 90%
44 | Small Trolley
[6 empty] | 3 | 35280 | Nos | 105840 |  |  | 3 | 105840 |  |  |  | 90%
45 | Big Trolley
[6 empty] | 3 | 56250 | Nos | 168750 |  |  | 3 | 168750 |  |  |  | 90%
46 | Wall Storage Cabinets
[6 empty] | 8 | 15750 | Nos | 126000 |  |  | 8 | 126000 |  |  |  | 90%
151 | Modular Double skin floor mounted EUROVENT Certified Air Handling Unit 3400CFM / 8.5 TR / 150mm SP made out of 45 plus or minus 2mm thick PUF insulated panels Thermal break aluminium profile frame work with 0.8mm thick pre painted / powder coated inner and outer skins comprising of mixing box with fresh air and return air dampers, pre filters with 10 and 5 microns combination filters in single frame, Interlaced/Intertwined DX Cooling Coil suitable for connecting 2 nos of 8.5TR capacity 1W plus 1S out door condensing units, SS304 drain pan with , blower section with Nicotra / Kruger make direct drive/ Plug type fan, vibration isolators, EFF1 motor and blower section with on/off switches to operate from outside, limit switch for the fan section access door with a view port, fine filter section with 3 microns filters inspection doors for all filter and fan sections and damper at the outlet of unit. Ports for differential pressure gauges across all filters and blower to measure differential pressure. AHU Make : VTS / Systemair, Make - Blower - Nicotra / Kruger ; Motor - Crompton Greaves / Siemens ; Filter - Thermodyne / Freudenberg / Ultrafil at Gandhi Hospital
[6 empty] | 1 | 531000 | Nos | 531000 |  |  | 1 | 531000 |  |  |  | 90%
166 | SITC of Magnehelic gauges across pre and fine filter at AHUs including mounting arrangement, SS nozzles, food grade PVC tubing, etc. At Gandhi Hospital
[6 empty] | 3 | 9450 | Nos | 28350 |  |  | 3 | 28350 |  |  |  | 90%
167 | SITC of Magnehelic gauges to measure the room differential pressures in operation theatres with SS mounting box, SS nozzles, food grade PVC tubing, etc. At Gandhi Hospital
[6 empty] | 2 | 11610 | Nos | 23220 |  |  | 2 | 23220 |  |  |  | 90%
153 | SITC of air cooled condensing units with two scroll compressors, air cooled condenser, power panel, vibration isolating pads, stand for ODU, thermostat, etc. of the following capacities. The nominal capacity of the condensing unit shall be as under. Air cooled condensing unit shall have horizontal discharge. All refrigerant piping accessories sight glass, drier, expansion valve, etc. shall be supplied with the condensing units and suitable to connect above AHUs. Refrigerant shall be R 407C / R 410A. Necessary thermostat, control wiring, etc. shall be included. Derating of the unit shall not be more than 15percentage under 45 deg. C ambient temperature. Condensing unit shall be capable of operating up 50 deg. C ambient temperature. 8.5 TR capacity At Gandhi Hospital
[6 empty] | 2 | 163800 | Nos | 327600 |  |  | 2 | 327600 |  |  |  | 90%
154 | SITC of Flange type, Flame proof FLP duct heaters of 5 kW capacity with Mineral Filled AISI SS304/SS321 Sheathed Tubular Heater with GI Helical fins, Tube dia 8.2mm min and Helical Finn dia 25mm min, enclosed in the frame, FLP Terminal box etc., Nickel Chromium Inner Element, Silicon Sealing to Restrict Moisture pickup, Silver brazed mounting plate etc., and heaters shall be controlled with PID thyrestor controller based on the analog output signal of 0-10 V DC of controller . And this should have saftey thermostat and cutouts and air stat etc. all safety controls. The capacities as follows and sizes of the heaters shall be as per the duct sizes and approved drawing. at Gandhi Hospital
[6 empty] | 1 | 184500 | Nos | 184500 |  |  | 1 | 184500 |  |  |  | 90%
152 | Supply and Installation of AL-powdercoated bottom loading type HEPA filter modules with bewel gear arrangement damper with access from clean room suitable to house the following size flange type HEPA filters including GI pressure plate, GI cleats with bolts and pressure drop & Integrity testing ports into room.Supply and Installation of H14 HEPA filters with 99.995% efficiency of the following sizes 600 X 600 X 150MM - HEPA filter - Module height <=350 mm,600 x 600 x 150 mm - 1000 CFM,600 x 600 x 150 mm - 1000 CFM
[6 empty] | 6 | 37800 | Nos | 226800 |  |  | 6 | 226800 |  |  |  | 90%
140 | Supply, Installation, testing And Commissioning of 20 nos LAN points with cat 6 cable and with suitable network rack and 5 nos of telephone points with knore box to existing EPABEX. At Gandhi Hospital
[6 empty] | 1 | 344700 | Job | 344700 |  |  | 1 | 344700 |  |  |  | 90%
141 | Supply, Installation, testing And Commissioning of 1 no of Access control system with egress switch, power cable communication cable to control panel with necessary required items etc,. At Gandhi Hospital
[6 empty] | 1 | 111600 | Nos | 111600 |  |  | 1 | 111600 |  |  |  | 90%
142 | Supply, Installation, testing And Commissioning of Automatic Fire Alaram system which is including 30 nos of smoke detectors 1nos manual call point 1 nos hooter with fire alaram cable connected to the existing fire control panel with necessary required item etc,. At Gandhi Hospital
[6 empty] | 1 | 459000 | Job | 459000 |  |  | 1 | 459000 |  |  |  | 90%
143 | Supply, Installation, testing And Commissioning of 5 nos IP Based CCTV camers and cat 6 cable with NVR system. At Gandhi Hospital
[6 empty] | 1 | 163800 | Job | 163800 |  |  | 1 | 163800 |  |  |  | 90%
144 | Supply, Installation, testing And Commissioning of Audio and video recording of counseling rooms . At Gandhi Hospital
[6 empty] | 1 | 124200 | Job | 124200 |  |  | 1 | 124200 |  |  |  | 90%
145 | Supply and Installation of fire Extinguisher of CO2 4.5 kg at Gandhi Hospital
[6 empty] | 5 | 10103 | Nos | 50515 |  |  | 5 | 50515 |  |  |  | 90%
146 | Supply and iInstalltion of ceiling mounted Fire extinguiser of ABC MAP 90, 5.0 kg stored pressure type at Gandhi Hospital
[6 empty] | 5 | 6917 | Nos | 34585 |  |  | 5 | 34585 |  |  |  | 90%
147 | Supply and Installtion of 2.0 kg clean agent HCFC 123 Fire Extinguiser at Gandhi Hospital
[6 empty] | 5 | 13559 | Nos | 67795 |  |  | 5 | 67795 |  |  |  | 90%
148 | Supply and Installaion of Fire escape signage Boards at Gandhi Hospital
[6 empty] | 1 | 50400 | Job | 50400 |  |  | 1 | 50400 |  |  |  | 90%
94 | Air Shower Supply and installation,testing and commissioning of 16 GI Power coated Suitable single person entry air shower
[6 empty] | 1 | 319500 | Job | 319500 |  |  | 1 | 319500 |  |  |  | 90%
95 | Supply and installation,testing and commissioning of Static Pass Boxes Of Size 450 x 450mm with 1.2mm thick SS 304 Mat finish, with interlock doors, UV light on When Doors Closed Condition. As per Clean room standard and requirements
[6 empty] | 3 | 54900 | Job | 164700 |  |  | 3 | 164700 |  |  |  | 90%
Copper Pipe
178 | Supply installation,Testing and Commissioning of Hard Copper REFRIGERANT PIPING of 16 swg various sizes with necessary supports,fittings, interconnecting the liquid and suction lines between the indoor units. The piping shall be carried out of hard drawn copper pipes of type K with soldered/brazed socket fittings.Isolate each compressor, stainers,sight glass and any other componenet requiring proper operation and maintanance.Both the suction and liquid lines sahll be insulated with 19mm thick closed cell insulation for above 25mm dia,13mm thick for pipes below 25mm dia. the insulation finished with treated woven glass fiber reinforced covering for inside piping and including making required holes in the wall and re finishing and water tight of holes after laying holes as per the specifications and approved drawings at Gandhi Hospital
[6 empty] | 1 | 360000 | Job | 360000 |  |  | 1 | 360000 |  |  |  | 90%
179 | Supply, Installation, Testing and Commissioning of refnet joints to be provided in refrigerant pipe line. Maretial of construction for fittings shall be similar to refrigerant piping.At Gandhi Hospital
[6 empty] | 11 | 5572 | Nos | 61292 |  |  | 11 | 61292 |  |  |  | 90%
Electrical -2
137 | SITC of IVF Center Main Panel Indoor IP-42 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with /without detachable extension type structure with all type of suitable switching accessories & bus-bar as per load requirement of respective IVF equipment’s. (Which is including Lighting, power DBs & UPS)
[6 empty] | 1 | 355000 | Nos | 355000 |  |  | 1 | 355000
138 | SITC of IVF center AC Panel outdoor IP-54 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with / without detachable extension type structure with all type of suitable switching accessories & bus-bar as per load requirement of respective AC equipment’s. (Which is including 1nos AHU’s stater with VFD by pass, Heater, ODU & VRF system)
[6 empty] | 1 | 270000 | Nos | 270000 |  |  | 1 | 270000
139 | Supply & installation of AHUs stater on/off push button station for Remote control for inside IVF center with control wiring from AC panel to on /off push button station with necessary items.
[6 empty] | 3 | 1540 | Nos | 4620 |  |  | 3 | 4620
136 | Supply, Laying & testing of 4Cx4 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
[6 empty] | 80 | 356 | Rmt | 28480 |  |  | 80 | 28480
[5 empty] | AE | 45 | 285 | Rmt | 12825 |  |  | 45 | 12825
135 | Supply, Laying & testing of 4Cx6 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
[6 empty] | 53 | 484 | Rmt | 25652 |  |  | 53 | 25652
134 | Supply, Lying & testing of 4Cx16 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
[6 empty] | 60 | 1483 | Rmt | 88980 |  |  | 60 | 88980
130 | Supply & installation of 25x3 Copper flat for Neutral earthing of UPS & Equipment which is laid in 100mm cable tray
[6 empty] | 65.3 | 902 | Rmt | 58900.6 |  |  | 65.3 | 58900.6
129 | Supply & installation of 25x3 GI flat for body earthing of DBs & Cable tray which is laid in 100mm cable tray
[6 empty] | 52.4 | 163 | Rmt | 8541.2 |  |  | 52.4 | 8541.2
127 | Providing and Fixing maintenance free earthing which consists of copper. Earth station, with 600X600X3.15mm Copper Plate at 2500mm Depth including construction of brick pedestal, providing meshed funnel, GI cover and other civil Engineering works, spreading a homogenous mixture of salt, charcoal around the pipe etc., completely as per IS 3043, 1987 or latest revision. Earthing testing should be done as per IE Rules like Earth valve test Etc.
[6 empty] | 2 | 22283 | Nos | 44566 |  |  | 2 | 44566
126 | Providing and Fixing maintenance free earthing which consists of G.I. Earth station, with 600X600X3.15mm GI Plate at 2500mm Depth including construction of brick pedestal, providing meshed funnel, GI cover and other civil Engineering works, spreading a homogenous mixture of salt, charcoal around the pipe etc., completely as per IS 3043, 1987 or latest revision. Earthing testing should be done as per IE Rules like Earth valve test Etc.
[6 empty] | 2 | 8500 | Nos | 17000 |  |  | 2 | 17000
121 | SITC of Hot dip galvanized perforated cable tray of 100 mm Wide sizes for to run the cable from DBs to SBs & sockets and AC panel to Units units. All necessary supports & accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. ( Elec 4.10.1 d)
[6 empty] | 36.2 | 429 | Rmt | 15529.8 |  |  | 36.2 | 15529.8
120 | Supply & installation of 225mm Light duty exhaust fan with metal blades etc complete Makes: Havells Ventilair-DB
[6 empty] | 4 | 2203 | Nos | 8812 |  |  | 4 | 8812
112 | Providing and fixing of 125A 25KA TPN Thermal Magnetic Release Based MCCB & Terminal Spreaders in Existing panel board with 1 No. and 1 Set of Indication Lamps, LED type, R,Y,B and breaker 'ON' , 'OFF', 'TRIP' & spring charged lamps. and replace with above Mentioned with required Drilling Holes, removing & Making Busbar connections etc, as required. Makes: Legrand / Schneider/ABB/L&T/C&S
[6 empty] | 1 | 28883 | Nos | 28883 |  |  | 1 | 28883
108 | Supply and fixing of DP Metal Enclosure with IP 20 Protection DB Make with 1 No 20A, 10 KA DP MCB Make: Legrand / Schneider including internal connection and labour charges for Flush Mounting etc., complete. Makes: Legrand
[6 empty] | 1 | 2562 | Nos | 2562 |  |  | 1 | 2562
96 | Supply and Fixing of 25mm outer dia medium grade, FRLS with IS:9537 part 3 rigid PVC pipe with all accessories fixing on wall / ceiling with chromium plated metallic base saddles including all labour charges etc., complete Makes:- Modi
[6 empty] | 200 | 116 | Rmt | 23200 |  |  | 200 | 23200
[5 empty] | AE | 31.4 | 93 | Rmt | 2920.2 |  |  | 31.4 | 2920.2
98 | Wiring with run of 2 of 22/0.3mm (1.5 Sqmm) FRLS / HFFR PVC insulated flexible ISI mark copper cable in existing PVC conduit pipe including Supply and fixing of Jumbo Ceiling rose and 6A/10A ISI Mark 1way Modular switch with required modular box and cover frame in existing Surface or Concealed pipe wiring including cost and conveyance of all material and all labour charges etc., complete for light, Fan, Exhaust fan and bell points in N.R.B. Makes of wires : Polycab (HFFR) Makes of switches :Honeywell Blenge Plus
[6 empty] | 27 | 945 | Rmt | 25515 |  |  | 27 | 25515
101 | Supply & fixing of 16A/6A, 2 in one socket - 2 Nos with 16A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benzplus
[6 empty] | 19 | 1755 | Nos | 33345 |  |  | 19 | 33345
105 | Supply and Run of 3 of 56/0.3mm (4.00 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Million(HFFR) / KEI (HFFR) /
[6 empty] | 178.3 | 255 | Nos | 45466.5 |  |  | 178.3 | 45466.5
106 | Supply and Run of 5 of 90/0.3mm (6.0 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Million
[6 empty] | 60 | 606 | Rmt | 36360 |  |  | 60 | 36360
[5 empty] | AE | 30 | 485 | Rmt | 14550 |  |  | 30 | 14550
104 | Supply and Run of 3 of 36/0.3mm (2.50 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
[6 empty] | 96.4 | 177 | Rmt | 17062.8 |  |  | 96.4 | 17062.8
sup | Supply and Transportation 56W Clean room Light fixture, 2' x2' (600mm x600mm) LED luminaire CRCA powder coated white after phosphocreatine treatment provided as standard. with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% etc., complete. MAKE: OSRAM / Wipro / Crompton / Bajaj / Havells
12
sup | Supply and Transportation of 48" ( 1200 mm) High Speed Fan Sweep Celing Fan with all accessories etc., complete. Make Havells S S 390
14
sup | Labour Charges for fixing of 48" Celing fan
14
sup | Supply and fixing of Anchor Fastner
14
sup | Supply & fixing of 2nos6A, 2 in one socket - 2 Nos with 6A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benz Plus
30
sup | Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete
14
sup | Supply and fixing of 15" Heavy Duty Exfan Make Almonard
1
Sup | Supply and fixing of 63 Amps 4 pole MCB in metal enclouser
1
Civil -2
49 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete (Brick Masonary)
[6 empty] | 1.47 | 358 | Cum | 526.26 |  |  |  |  | 1.47 | 526.26 |  | 90%
53 | Masonry work in CM (1:6) prop (cement: Screened sand) in super structure with Aerated (Cellular) Autoclaved Concrete Blocks conforming to IS:2185 (Part-3) - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600x 230 x 200 mm from approved source having minimum crushing strength of 3 N/Sq.m including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, including sales & other taxes on all materials, all operational, incidental and labour charges such as mixing cement mortar, constructing masonry, scaffolding charges, lift charges, curing, etc., complete but excluding seigniorage charges for finished item of work. (APSS No. 501 & 504).
[6 empty] | 6.24 | 14450 | Cum | 90168 |  |  |  |  | 6.24 | 90168 |  | 90%
56 | Plastering 20mm thick in two coats using screened sand with base coat of 8mm thick in CM (1:6) and top coat of 4mm thick in CM (1:4) with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales & other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and overheads & contractors profit complete for finished item of work. (SS 901,903 & 904).
[6 empty] | 11.04 | 969 | Sqm | 10697.76 |  |  |  |  | 11.04 | 10697.76 |  | 90%
77 | Supplying and fixing of SWR PVC pipes (Prince/Sudhakar/Kisan/Supreme or any ISI brand) 4 Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, overheads & contractors profit complete for finished item of work at all floor levels. (APSS No. 1302 1319 & 1326)
[6 empty] | 26.63 | 400 | Rmt | 10652 |  |  |  |  | 26.63 | 10652 |  | 90%
75 | Supply and fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings SDR 13.5 to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" to 2") for hot and cold water (IS 15778:2007) including cost and conveyance of all materials to site, labour charges for fixing, overheads & contractors profit complete for finished item of work at all floor levels.
[6 empty] | 75 | 206 | Rmt | 15450 |  |  |  |  | 75 | 15450 |  | 90%
[6 empty] | 23 | 183 | Rmt | 4209 |  |  |  |  | 23 | 4209 |  | 80%
81 | Supply, installation and commissioning approved make floor mounted Anglo Indian wash down EWC conforming to IS: 2556 part8-2004 suit with P or S trap with dual flush porcelain cistren fixed on wash down EWC with all intenal parts of dual flush cistren. ultra solid seat cover of approved make with rubber buffer and cap and 15mm angle stop cock and 450mm long PVC iner connection pipe wall flanges all of approved make etc. Complete for finished item of work
[6 empty] | 4 | 6831 | Nos | 27324 |  |  |  |  | 4 | 27324 |  | 90%
80 | Supplying and fixing Indian make Flat Back Wash Hand Basin 1st quality conforming to IS:2556-Part-4:1972 of size 550mm x 400mm with 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make heavy duty complete with standard CI brackets including wooden blocks ,1 No.12.70mm PVC connection with brass union nuts CP coated , angle stop cock 12.70mm dia. first quality Indian make heavy duty, 30mm dia. PVC flexible waste pipe 914.4mm length of 1st quality including cost and conveyance of all materials to site, labour charges , overheads & contractors profit for finished item of work.
[6 empty] | 4 | 3420 | Nos | 13680 |  |  |  |  | 4 | 13680 |  | 90%
83 | Supplying and fixing CP finish brass soap dish of approved make ISI quality including cost and conveyance of all materials, labour charges for fixing, overheads & contractors profit for finished item of work
[6 empty] | 4 | 785 | Nos | 3140 |  |  |  |  | 4 | 3140 |  | 90%
84 | Supplying and fixing TV shape mirror with plastic frame of size 609.6mm x 457.2mm , plywood back with NP screws 1st quality including cost and conveyance of all materials, labour charges , overheads & contractors profit for finished item of work
[6 empty] | 4 | 654 | Nos | 2616 |  |  |  |  | 4 | 2616 |  | 90%
85 | Supplying and fixing of CP finish steel towel rods 600mm long and 20mm dia with brackets and aluminium screws including cost and conveyance of all materials, labour charges , overheads & contractors profit for finished item of work.
[6 empty] | 4 | 785 | Nos | 3140 |  |  |  |  | 4 | 3140 |  | 90%
86 | Supplying and fixing 15 mm Steel body CP finish self closing tap push type conforming to IS 1711 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, overheads & contractors profit complete for finished item of work in all floors.
[6 empty] | 4 | 376 | Nos | 1504 |  |  |  |  | 4 | 1504 |  | 90%
82 | Supplying and fixing Chromium plated finish brass body quarter turn Bibcock cum Health Faucet with 1m long tube and wall hook with necessary fittings etc., complete including cost and conveyance of all materials, labour charges, complete for finished item of work in all floors. at Gandhi Hospital
[6 empty] | 4 | 4122 | Nos | 16488 |  |  |  |  | 4 | 16488 |  | 90%
73 | Supplying and fixing 15 mm brass body CP finish bib tap of not less than 300 grams weight screw type full turn with internal/external threaded connection conforming to IS 8931 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, overheads and contractors profit complete for finished item of work in all floors. at Gandhi Hospital
[6 empty] | 1 | 793 | Nos | 793 |  |  |  |  | 1 | 793 |  | 90%
79 | Supply and fixing of 4 inches 101.6mm multi floor trap with jali -UPVC/SWR pipe fittings as per site requirements with standard practice for all floor including cost and conveyance of all materials to site ,labour charges ,etc,. Complete for finshed item of work at handhi hospital
[6 empty] | 5 | 198 | Nos | 990 |  |  |  |  | 5 | 990 |  | 90%
58 | Supply and Installation change room Cubicles at Gandhi Hospital GENERAL SPECIFICATIONS: Thickness of compact Laminate:12mm Thick Colour OF HPL Boards,In Single Colour,Size of Cubicle As per DWG, Door Size For Normal Cubicles AS per DWG Overall Height of Cubicle,2105mm Including bottom gap of 100mm,Accessories , Manufacturers standard makes of aluminium , SS Accessories .a Aluminium H Top Rail b. SS Hinges c. SS privacy Thumb turn occupancy indicator d.SS coat hook e. SS Door knob f. Aluminium U Channel g.Aluminium Door Stopper Channel h. Runner lining i.SS Screw And PVC Wall Plugs
[6 empty] | 16.83 | 8150 | Sqm | 137164.5 |  |  |  |  | 16.83 | 137164.5 |  | 90%
69 | Providing and applying Wall putty of White Cement or Polymer or Cement based of average 1 to 2 mm thickness over plastered surface to prepare the surface even and smooth after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, applying emery paper, Sand the surface, clean & wipe off loose dust, applying knifing paste filler by putty knife / muslin pad, air dry for 2 - 3 hrs, sand with 180 and 320 No., emery paper for the surface preparation including cost and conveyance of all materials to work site and all operational, incidental, labour charges, over heads and contractors profit etc., complete for finished item of work in all floors for Internal walls.
[6 empty] | 1007.4 | 284 | Sqm | 286101.6 |  |  |  |  | 1007.4 | 286101.6 |  | 90%
71 | Supply and application of one coat water based cement primer of interior grade I and two coats of water based PU paint having anti-bacterial applications content less than 50 grams/litre for internal walls including cost and conveyance of all materials to site, sales and other taxes, incidental, operational and all labour charges etc., and complete for finished item of work in 5th floor. at Gandhi Hospital
[6 empty] | 872.09 | 234 | Sqm | 204069.06 |  |  |  |  | 872.09 | 204069.06 |  | 90%
67 | Providing and fixing in true horizontal level 14 mm - Mineral Fiber sheet 595 x 595 Square / Tegular Fissura fine model edge tiles with a Humidity Resistance of 90percentage RH, Average NRC 0.50, Light Reflectance greater than80percentage, Thermal Conductivity equal to 0.052 to 0.057 w/mk, Fire Performance Class 0/Class 1 using hot dipped Galvanized Steel section exposed surface with pre-coated capping, main Tee of size 24 x 32 mm at every 1200 mm c/c maximum and rotary stitched cross tee of size 24 x 27 mm at every 600 mm c/c and sub-cross tee of size 24 mm x 25 mm at 1200 mm c/c and wall angle of size 19 x 19 mm fixed to periphery of the wall and the above grid is suspended at every 1200 mm c/c in both directions using 2.0 mm thick pre-straightened GI Wire including cost and conveyance of all materials and labour charges such as cutting , fixing of standing of frame work exposing roof making etc., complete for finished item of work in 5th floor. at Gandhi Hospital
[6 empty] | 316.08 | 1472 | Sqm | 465269.76 |  |  |  |  | 316.08 | 465269.76 |  | 90%
93 | Providing Laying of scratch proof PVC/vinyl flooring of 2mm thickness with proper welded joints air tight along with leveling compound to match the existing flooring levels as per the engineer in charge instructions. Sub floor preparation with self leveling compound. After the sub floor preparation, it should be suitable for ESD Flooring.Rate inclusive of sifting of material and labour charges.at Gandhi Hospital
[6 empty] | 124.84 | 3663 | Sqm | 457288.92 |  |  |  |  | 124.84 | 457288.92 |  | 90%
52 | Conveyance of un- useful excavated earth to a distance of 21 km for disposal including hire charges of T and P, labour charges etc,. Complete for finished item of work Dismantled Brick Masonary at Gandhi Hospital
[6 empty] | 72.93 | 409 | Sqm | 29828.37 |  |  |  |  | 72.93 | 29828.37 |  | 90%
160 | SITC of Factory fabricated and boxed ducting using Aluminium Sheets / coils, should be fabricated as per SMACNA, galvanised hardware and supports, silicon sealant at all longitudinal joints, Galvanized /GI Electroplated iron angle flanges for all the joints, bracing angles and minimum 5mm thick neoprene rubber gasket.- Duct pressure testing at 75mm to be carried oubefore insulatiting the duct. pressure testing to be done as per SMACNA. Procedure to be approved by consultant. 22G - 0.8 mm Thick at Gandhi Hospital
[6 empty] | 230.19 | 2093 | Sqm | 481787.67 |  |  |  |  | 230.19 | 481787.67 |  | 90%
156 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Suction Line at Gandhi Hospital
[6 empty] | 12 | 1071 | Rmt | 12852 |  |  |  |  | 12 | 12852 |  | 90%
155 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Liquid Line at Gandhi Hospital
[6 empty] | 10 | 918 | Rmt | 9180 |  |  |  |  | 10 | 9180 |  | 90%
158 | SITC of CPVC drain ping with supports, clamps and 9 mm thk. Nitrile rubber tube insulation of the following sizes. Insulation shall have factory laminated glass cloth. 25mm Dia at Gandhi Hospital
[6 empty] | 12 | 464 | Rmt | 5568 |  |  |  |  | 12 | 5568 |  | 90%
161 | Aluminium low leakage aerofoil design volume control dampers Suitable for manual and motorised operation At Gandhi Hospital
[6 empty] | 1.24 | 14220 | Sqm | 17632.8 |  |  |  |  | 1.24 | 17632.8 |  | 90%
162 | CBRI approved 16G GI Spring return actuated fire dampers rated for 90 minutes with limit switch. At Gandhi Hospital
[6 empty] | 0.84 | 23310 | Sqm | 19580.4 |  |  |  |  | 0.84 | 19580.4 |  | 90%
163 | SITC of SS perforated return raiser grilles with 10 microns filters with collar dampers At Gandhi Hospital
[6 empty] | 2 | 23670 | Sqm | 47340 |  |  |  |  | 2 | 47340 |  | 90% | 3.29
[6 empty] | 1.29 | 21040 | Sqm | 27141.6 |  |  |  |  | 1.29 | 27141.6 |  | 80%
164 | Extruded Al. powder coated EXHAUST / RETURN discrete grilles At Gandhi Hospital
[6 empty] | 1 | 7313 | Sqm | 7313 |  |  |  |  | 1 | 7313 |  | 90% | 1.25
[6 empty] | 0.25 | 6500 | Sqm | 1625 |  |  |  |  | 0.25 | 1625 |  | 80%
165 | SITC of Collar Dampers made of Al. extrusions with black powder coating for Grilles / Diffusers At Gandhi Hospital
[6 empty] | 0.72 | 6750 | Sqm | 4860 |  |  |  |  | 0.72 | 4860 |  | 90%
168 | SITC of Aluminium powder coated Fresh air and Exhaust Louvers of nonvision type with nylon mosquito net etc. At Gandhi Hospital
[6 empty] | 0.12 | 9270 | Sqm | 1112.4 |  |  |  |  | 0.12 | 1112.4 |  | 90%
169 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 32mm Thick for Exposed Supply Air duct and finished with UV Protective Paint. at Gandhi Hospital
[6 empty] | 119.84 | 1103 | Sqm | 132183.52 |  |  |  |  | 119.84 | 132183.52 |  | 90%
170 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Exposed Return Air Duct and finished with UV Protective Paint. at Gandhi Hospital
[6 empty] | 84.41 | 968 | sqm | 81708.88 |  |  |  |  | 84.41 | 81708.88 |  | 90%
171 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Supply air duct running inside the building. at Gandhi Hospital
[6 empty] | 40 | 707 | Sqm | 28280 |  |  |  |  | 40 | 28280 |  | 90% | 75.04
[5 empty] | AE | 35 | 628 | Sqm | 21980 |  |  |  |  | 35 | 21980 |  | 80%
172 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 19mm Thick for Return air running inside the building. at Gandhi Hospital
[6 empty] | 19.24 | 594 | Sqm | 11428.56 |  |  |  |  | 19.24 | 11428.56 |  | 90%
87 | Supply and instalaion of Wall Panels 80mm thick double skin Modular wall panels made of .8mm Powder Coated GI on both sides, with 40 plus or minus 2 kg/cum demsity pUF as infill, GI profiles all along the periphery,flush on both sides with maximum allowable gap of 3-4mm filled with food grade silicon sealent and placed on cold rolled galvanised bottom tracks with a recess to provide floor to wall coving flush with the wall panel. This including all required hardware for completion panels to be covered with a protective film to avoid any damages during transpotation and installation at Gandhi Hispital
[6 empty] | 96.75 | 5058 | Sqm | 489361.5 |  |  |  |  | 96.75 | 489361.5 |  | 90%
88 | Supply and installtion of 50mm thick double skin cealing system made .8mm thich powder coated GI sheet on both sides, 40 plus or minus 2kg/cum density PUF ad infill, GI Profiles all along the periphery, panels flush towards room sides with maximum allowable gap of 3-4mm at panelto panel joints filled with silicon sealent ceiling panels are suspended from the RCC salb bu using concealed Aall ceiling grid with tie rod and adjestable turn bickle arrangement etc. This includes all required hardware for completition. panels to be covered with a protective film to avoid any damge during transpotation and installation at Gandhi Hospital.
[6 empty] | 48.02 | 4622 | Sqm | 221948.44 |  |  |  |  | 48.02 | 221948.44 |  | 90%
92 | Supply and installation of Extruded Aluminium Coving at Gndhi Hopital
[6 empty] | 63.61 | 527 | Rmt | 33522.47 |  |  |  |  | 63.61 | 33522.47 |  | 90%
90 | Single leaf clean room door 46mm thick flush made of .8mm thick powedr coated GI sheet on both sides 90 pus or minus 2kg/cum density honeycomb with stand upto 220 deg.C temperature ,and compressible strength upto 400 kg/sqm,1.2mm thick GPSP door frames ,double glazed vision panel with necessary adhesive tapes and silicon swalent, necessary hardware like SS304 ball bearing butt hinges D- hnadles,push plates ,Dorma make door closer concealed tower bolt ,drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms,BOth sides lock and key etc,. Complete .
[6 empty] | 1 | 25830 | Nos | 25830 |  |  |  |  | 1 | 25830 |  | 90% | 3
[5 empty] | AE | 2 | 22960 | Nos | 45920 |  |  |  |  | 2 | 45920 |  | 80%
89 | Double leaf clean room door 46mm thick flush made of .8mm thick powedr coated GI sheet on both sides 90 pus or minus 2kg/cum density honeycomb with stand upto 220 deg.C temperature ,and compressible strength upto 400 kg/sqm,1.2mm thick GPSP door frames ,double glazed vision panel with necessary adhesive tapes and silicon swalent, necessary hardware like SS304 ball bearing butt hinges D- hnadles,push plates ,Dorma make door closer concealed tower bolt ,drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms,BOth sides lock and key etc,. Complete .
[6 empty] | 5 | 41400 | Nos | 207000 |  |  |  |  | 5 | 207000 |  | 90%
91 | Emergency Fire door 46mm thick flush made of .8mm thick powedr coated GI sheet on both sides 90 pus or minus 2kg/cum density honeycomb with stand upto 220 deg.C temperature ,and compressible strength upto 400 kg/sqm,1.2mm thick GPSP door frames ,double glazed vision panel with necessary adhesive tapes and silicon swalent, necessary hardware like SS304 ball bearing butt hinges D- hnadles,push plates ,Dorma make door closer concealed tower bolt ,drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms,BOth sides lock and key etc,. Complete .
[6 empty] | 1 | 49500 | Nos | 49500 |  |  |  |  | 1 | 49500 |  | 90%
61 | Supplying and fixing of Unplasticised Poly Vinyl Chloride UPVC 3 track sliding windows with mesh shutter – 2-glass shutters and 1-mesh shutter duly manufactured using UPVC reinforced profiles Composition of profile shall consists a minimum of 5.5 PHR of TiO2 and not more than 12 PHR of CaCo3 for every 100 parts of PVC resin of 94mm x 45 mm/80 mm x 52 mm x 2.20 mm for outer frames, 58 mm x 39 mm/54 mm x 38 mm x 2.20mm for sliding shutter frames capable of mounting single glazing system structurally reinforced with hot dip galvanized up to 50 microns of minimum thickness of 1.0/1.2 mm prefabricated and welded through fusion welding. The window sash shall be fitted with 5 mm thick clear float glass of reputed make and mesh shutter frame shall be 42 mm x 25mm/52 mm x 21.5 mm x 2.0 mm fitted with Vinyl Coated Fiber mesh- on rollers/ pulley duly fixed with Grey colour TPV Gasket for sash and Glazing bead shall be co extruded with Grey colour soft PVC. System shall have single point locking with Touch Lock and the system is to be installed at the site using anchor fasteners, silicon rubber sealant, easy glazing/deglazing at site etc., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site includingetc., complete for finished item of work. at Gandhi Hospital
[6 empty] | 7.88 | 8565 | Sqm | 67492.2 |  |  |  |  | 7.88 | 67492.2 |  | 90%
62 | Providing, supplying and fixing of Fixed Louvered Ventilator made out of multi chambered uPVC sections with Glazing bead shall be co-extruded with Grey colour soft PVC. having isolated drainage and reinforced with Galvanized Iron profiles throughout the window. The outer frame having an overall size of 60 mm x 55 mm x 2.40 with reinforcement of 1 mm thickness and Mullion with overall size of 74 mm x 60 mm x 2.40 mm with reinforcement of 1 mm thickness. Composition of profile shall consists a minimum of 5.5 PHR of TiO2 and not more than 12 PHR of CaCo3 for every 100 parts of PVC resin. Ventilator shall be provided with 4.5 mm Pin Head glass, standard hardware. Wall thickness of frame and Mullion shall be 2.4 mm., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site etc., complete for finished item of work hinges IS:205 150mm long, 1 No. aldrop IS:2681 300mm long, 1 No. tower bolt IS:204 of 200 mm x 10 mm dia at top, 2 Nos. 150 mm at Gandhi Hospital
[6 empty] | 1.53 | 7708 | Sqm | 11793.24 |  |  |  |  | 1.53 | 11793.24 |  | 90%
[6 empty] | Grand Total |  |  | 37544861.01 |  |  |  | 33699819.1 |  | 3845041.91
[6 empty] | Add GST @ 18% |  |  | 6758075 |  |  |  | 6065967 |  | 692108
[6 empty] | Grand Total |  |  | 44302936.01 |  |  |  | 39765786.1 |  | 4537149.91

## Bill-6
DETAILED MEASUREMENTS
Name of the work:Design, Fabriction, establishing and commissioning of In - Vitro ferility centers (IVFC) alongwith allied Services on Turnkey basis at Gandhi hospital secunderabad. | [10 empty] | Agency: M/s. Asta vardhman Consortium | [5 empty] | Agt.No: 344/A/TSMIDC/Spl.Proj/IVFCs/2022-23, Dt. 05.07.2023
S.No | Aggrement S.No | Discription Of Work etc., | Measurements Upto date | [5 empty] | Rate |  |  | Per | Total Volume |  | Deduct/previous Measurements |  | Since last measurement |  |  | Remarks
|  |  | No |  | L | B | D | Content | Units | Rs | Ps. |  | Rs. | Ps | P.No. | Qty. | Qty | Value
[18 empty] | Rs. | Ps.
1 | Sup | Core Cutting For VRV Copper Pipe 110mm Dia
|  | Out Door Unit Terrace | 1 | 1 |  |  |  | 1
|  | Minor OT | 1 | 1 |  |  |  | 1
|  | Manifold Corridoor | 1 | 2 |  |  |  | 2
|  | Sperm Collection Room | 1 | 2 |  |  |  | 2
|  | Andrology Lab | 1 | 4 |  |  |  | 4
|  | Infront Store Room | 1 | 1 |  |  |  | 1
|  | Counseling Room1 | 1 | 1 |  |  |  | 1
|  | Autoclave Room | 1 | 1 |  |  |  | 1
|  | Ultra Sound Room | 1 | 1 |  |  |  | 1
|  | UPS Room | 1 | 1 |  |  |  | 1
|  | Prepost Operative Wards | 1 | 2 |  |  |  | 2
|  | Change Room | 1 | 2 |  |  |  | 2
|  | Auto Clave Toom | 1 | 1 |  |  |  | 1
|  | Cryo Room | 1 | 1 |  |  |  | 1
[8 empty] | 21 | Nos
2 | Sup | Supplying and fixing GI pipe Medium Grade properties & weight as per IS 1239 in ground or on wall with GI fittings such as elbows tees couplings, nipples, plugs including excavation for trenches and refilling the trenches ,chiselling masonry walls and making good the walls & floors to the original surface and fixing MS clamps on TW blocks on walls including cost and conveyance of all materials and labour charges , overheads & contractors profit complete for finished item of work except for GI bends union and GI connectors with checkout and socket Tata or Zenith make or equivalent.
|  | Autoclave Outline 40mm | 1 | 1 | 17.55 |  |  | 17.55
|  | Autoclave Outline 25mm | 1 | 1 | 17.55 |  |  | 17.55
[8 empty] | 35.1 | Rmt
3 | Sup | Supplying and fixing of 3" (75mm) Nahany trap with jali - UPVC/SWR pipe fittings as per site requirements with standard practice for all floors including cost and conveyance of all materials to site, labour charges , overheads & contractors profit etc., complete for finished item of work.
|  | Prepost Operative wards | 1 | 1 |  |  |  | 1
|  | Toilet At Counseling Room2 | 1 | 1 |  |  |  | 1
|  | Dr. Toilet | 1 | 1 |  |  |  | 1
|  | Sperm Collection Room | 1 | 1 |  |  |  | 1
|  | Scrub Wastewater Line | 1 | 1 |  |  |  | 1
[8 empty] | 5 | Nos
4 | Sup | V-Board Partition
|  | Dr. Change Room | 2 | 2 | 1.43 |  | 3.35 | 19.162
|  | do | 1 | 2 | 0.075 |  | 3.35 | 0.5025
|  | Store Room | 1 | 2 | 3 |  | 3.35 | 20.1
|  | do | 1 | 2 | 2.26 |  | 3.35 | 15.142
|  | Door Deduction(-) | -1 | 1 | 1 |  | 2.1 | -2.1
|  | Patient and Staff Change Room | 2 | 2 | 1.87 |  | 3.45 | 25.806
|  | Window Closings Embryology Lab And UPS Room | 1 | 4 | 1.5 |  | 1.5 | 9
|  | Sperm Collection Toilet | 1 | 1 | 1 |  | 1.5 | 1.5
[8 empty] | 89.1125 | Sqm
5 | Sup | Supply & application of one coat water based cement primer of interior grade I and two coats of acrylic emulsion paint having VOC (Volatile Organic Compound) content less than 50 grams/litre for internal walls including cost and conveyance of all materials to site, sales & other taxes, incidental, operational and all labour charges etc., and overheads & contractors profit complete for finished item of work in all floors.
|  | Step Down Room Door Replacing | 1 | 2 | 1.5 |  | 2.6 | 7.8
|  | do | 1 | 2 | 1.7 |  | 0.4 | 1.36
|  | Door Jam | 1 | 1 | 6.635 | 0.23 |  | 1.526
|  | Prepost operative room Door Replace | 1 | 2 | 1 |  | 2.6 | 5.2
|  | Embryology Lab Door Replacing | 1 | 2 | 1.16 |  | 2.9 | 6.728
|  | do | 1 | 2 | 1.7 |  | 0.4 | 1.36
|  | Door Jam | 1 | 1 | 6.7 | 0.23 |  | 1.541
|  | Major OT Door | 1 | 2 | 1.7 |  | 0.4 | 1.36
|  | Door Jam | 1 | 1 | 6.7 | 0.23 |  | 1.541
|  | OT Room Window Replacing | 3 | 2 | 1.5 |  | 1.5 | 13.5
|  | Toilet Room Window Replacing | 1 | 2 | 1.5 |  | 1.5 | 4.5
|  | Embrology Lab Windows Replacing | 3 | 2 | 1.5 |  | 1.5 | 13.5
|  | Access Control Door Wall | 2 | 2 | 3 |  | 3 | 36
|  | Door Deduction(-) | -2 | 2 | 1.5 |  | 2.6 | -15.6
|  | Door Jam | 1 | 2 | 6.7 | 0.23 |  | 3.082
|  | Prepost operative Window Closing | 1 | 2 | 1.1 |  | 1.9 | 4.18
|  | Record Room Wall | 1 | 2 | 3 |  | 3.45 | 20.7
|  | Door Deduction(-) | -1 | 2 | 1 |  | 2.1 | -4.2
|  | Door Jam | 1 | 1 | 5.2 | 0.15 |  | 0.78
|  | Partition Wall b/w Ultra Sound And Autoclave Room | 1 | 2 | 2.18 |  | 3.5 | 15.26
|  | Partition Wall b/w Counciling -2 And Counciling -1 | 1 | 2 | 2.452 |  | 3.5 | 17.164
|  | Doctors Toilet Room Wall | 1 | 2 | 4.7 |  | 3.5 | 32.9
|  | Door Deduction(-) | -1 | 2 | 1 |  | 2.1 | -4.2
|  | Door Jam | 1 | 1 | 5.2 | 0.15 |  | 0.78
|  | Partition Wall b/w Carridor and OT Room | 1 | 2 | 6.485 |  | 3.5 | 45.395
|  | Partition Wall b/w OT Rooms | 1 | 2 | 6.485 |  | 3.5 | 45.395
|  | P.Change Room Wall | 1 | 2 | 2.02 |  | 3.5 | 14.14
|  | Store Room | 1 | 2 | 2.582 |  | 3.5 | 18.074
|  | Door Jams | 1 | 1 | 5.2 | 0.15 |  | 0.78
|  | Door Deduction(-) | -1 | 2 | 1 |  | 2.1 | -4.2
|  | Partition Wall b/w Store And Blod Collection | 1 | 2 | 3.4 |  | 2.4 | 16.32
|  | Top | 1 | 2 | 3.4 | 0.15 |  | 1.02
|  | Blod Collection Room Wall | 1 | 2 | 2.582 |  | 3.5 | 18.074
|  | Door Jam | 1 | 1 | 5.2 | 0.15 |  | 0.78
|  | Door Deduction(-) | -1 | 2 | 1 |  | 2.1 | -4.2
|  | Partition Wall b/w Blood Collection And Sperm Collection | 1 | 2 | 3.3 |  | 2.4 | 15.84
|  | Top | 1 | 1 | 3.4 | 0.15 |  | 0.51
|  | do | 1 | 2 | 1 |  | 1.2 | 2.4
|  | partition Wall b/w Sperm Collection Room And Toilet Room | 1 | 2 | 3.3 |  | 3.5 | 23.1
|  | Door Jam | 1 | 1 | 5 | 0.15 |  | 0.75
|  | Door Deduction(-) | -1 | 2 | 0.8 |  | 2.1 | -3.36
|  | Sperm Collection Toilet Wall | 1 | 2 | 2.05 |  | 3.5 | 14.35
|  | Partition Wall b/w Toilet And Cryo Room | 1 | 2 | 1.7 |  | 3.5 | 11.9
|  | Cryo Room Wall | 1 | 2 | 3 |  | 3.5 | 21
|  | Door Jams | 1 | 1 | 5.2 | 0.15 |  | 0.78
|  | Door Deduction | -1 | 2 | 1 |  | 2.1 | -4.2
|  | Manifold Room | 1 | 2 | 3.185 |  | 3.5 | 22.295
|  | do | 1 | 2 | 1.385 |  | 3 | 8.31
|  | do | 1 | 2 | 2.23 |  | 3.5 | 15.61
|  | do | 1 | 2 | 1.33 |  | 3 | 7.98
|  | Andrology Lab Scrub Area | 1 | 2 | 2.585 |  | 3.45 | 17.8365
|  | Doctors Corridor Door Jam | 1 | 1 | 8.1 | 0.23 |  | 1.863
|  | Corridor Change Room | 1 | 1 | 8.1 | 0.23 |  | 1.863
|  | Prepost Operative Room Wall Area | 1 | 1 | 12.6 | 0.23 |  | 2.898
|  | Toilet Wall | 1 | 1 | 4.65 | 0.15 |  | 0.6975
|  | Counseling Rooms Partition Wall Area | 1 | 1 | 9.3 | 0.15 |  | 1.395
|  | Andrology Lab Main Door wall area | 1 | 1 | 11.2 | 0.23 |  | 2.576
|  | Toilet Wall | 1 | 1 | 5.25 | 0.15 |  | 0.7875
|  | do | 1 | 1 | 6.45 | 0.15 |  | 0.9675
|  | partition Wall | 1 | 1 | 1.8 | 0.15 |  | 0.27
|  | Toilet Wall Major OT | 1 | 1 | 5.25 | 0.15 |  | 0.7875
|  | do | 1 | 1 | 6.45 | 0.15 |  | 0.9675
|  | partition Wall | 1 | 1 | 1.8 | 0.15 |  | 0.27
|  | Andrlogy Lab Wall plastring | 1 | 1 | 3.2 |  | 1.5 | 4.8
|  | Reciption Platform Wall | 1 | 2 | 1.5 |  | 0.9 | 2.7
|  | do | 3 | 2 | 0.5 |  | 0.9 | 2.7
|  | Toilet Inside Prepost Operative Room | 1 | 1 | 3 |  | 1.5 | 4.5
|  | do | 1 | 1 | 0.8 |  | 1.5 | 1.2
|  | Andrlogy Lab Toilet Wall | 1 | 1 | 1.8 |  | 1.5 | 2.7
|  | do | 1 | 1 | 3 |  | 1.5 | 4.5
|  | do | 1 | 1 | 1.8 |  | 1.5 | 2.7
|  | Andrology lab Partition wall | 1 | 1 | 5.2 |  | 1.5 | 7.8
|  | Door Deduction(-) | -1 | 1 | 1.5 |  | 1.5 | -2.25
|  | Major OT Toilet Wall | 1 | 1 | 1.8 |  | 1.5 | 2.7
|  | Major OT | 1 | 1 | 4.05 |  | 1.5 | 6.075
|  | do | 1 | 1 | 3 |  | 1.5 | 4.5
|  | partiton wall | 1 | 1 | 1.8 |  | 1.5 | 2.7
[8 empty] | 536.1091 | Sqm
6 | Sup | Supply & Installation of MS Angle for Duct Support, Cable Tray Support and Condensing Unit Stand of size 40 X 40 x 5 mm Thick.
|  | Condensing Unit-1 Supports Long Direction | 1 | 2 | 1.37 |  |  | 2.74
|  | Condensing Unit-1 Supports Short Direction | 1 | 2 | 0.33 |  |  | 0.66
|  | Legs | 1 | 4 | 0.32 |  |  | 1.28
|  | Square Plate 100 x 100 x 5mm Thick | 1 | 4 | 0.1 | 0.1 |  | 0.04
|  | Condensing Unit-2 Supports Long Direction | 1 | 2 | 1.37 |  |  | 2.74
|  | Condensing Unit-2 Supports Short Direction | 1 | 2 | 0.33 |  |  | 0.66
|  | Legs | 1 | 4 | 0.32 |  |  | 1.28
|  | Square Plate 100 x 100 x 5mm Thick | 1 | 4 | 0.1 | 0.1 |  | 0.04
|  | Cable Tray Supports Legs | 1 | 8 | 0.4 |  |  | 3.2
|  | Horizontals | 1 | 4 | 0.3 |  |  | 1.2
|  | Plate 75 mm Dia | 1 | 8 | 0.0044156 |  |  | 0.035325
|  | AHU Supply duct supports legs | 1 | 4 | 0.8 |  |  | 3.2
|  | AHU Supply duct supports legs | 1 | 2 | 0.9 |  |  | 1.8
|  | AHU Supply duct supports legs | 1 | 4 | 1.95 |  |  | 7.8
|  | Horizontals | 1 | 5 | 0.8 |  |  | 4
|  | Plate 75 mm Dia | 1 | 10 | 0.0044156 |  |  | 0.044156
[8 empty] | 30.7195 | 92.1584 | Kgs
7 | Sup | Supply & Installation of MS Angle for Duct Support, Cable Tray Support and Condensing Unit Stand of size 25 X 25 x 5 mm Thick.
|  | AHU Return Duct Support Legs | 1 | 12 | 0.75 |  |  | 9
|  | Horizontals | 1 | 6 | 0.85 |  |  | 5.1
| ` | Plate 75 mm Dia | 1 | 12 | 0.0044156 |  |  | 0.052988
[8 empty] | 14.153 | 25.4754
8 | Sup | Supply and installation of Canvas Connections For AHUS
|  | 750 x 350 Supply for AHU | 1 | 1 |  |  |  | 1
|  | 800 x 400 Return For AHU | 1 | 1 |  |  |  | 1
[8 empty] | 2 | Nos
9 | Sup | 4C x 1.5 Sqmm Copper Flexible Cable For Condensing Unit to Electrical Panel
|  | Condensing unit to Electrical Panel | 1 | 1 | 22.4 |  |  | 22.4
|  | Electrical Panel to Heater | 1 | 1 | 21.5 |  |  | 21.5
|  | AHU to Electrical Panel | 1 | 1 | 30.2 |  |  | 30.2
[8 empty] | 74.1 | Rmt
10 | Sup | Supply & installation of 50x6 GI flat for AHU Copper Pipe which is laid in 300mm cable tray
|  | AHU To Condensing Unit-1 | 1 | 1 | 2.3 |  |  | 2.3
|  | Condensing Unit-1 to Condensing Unit-2 | 1 | 1 | 1.65 |  |  | 1.65
[8 empty] | 3.95 | Rmt
11 | Sup | IVF Main Entry Door
|  | Main Door | 1 | 1 |  |  |  | 1
[8 empty] | 1 | Nos
12 | Sup | Providing of factory made prelaminated FPVC (Foamed Polyvinyl Chloride) Doors frame of the size 105 x 40 mm with a wall thickness of 10mm made out of extroded rigid FPVC profile mitre joined with 6 Nos. of 50mm long Screw. The Door frame shall be fixed to the wall by using 80mm long screws through the frame with the help of PVC fastners of 3 no's to be provuded for each vertical membr, GI Stiffenrs of ( "U" GI Channel of size 29 x 9 x 1 mm, 150mm long) - no's at hinge point, Frame reinforcement of ("U" GI Channel Of Size 46 x 22 .06mm), Bottom tie rod of ("U" GI Channel Size of 15 x15 1mm ) etc. complete as per the manufactures specification for finished item of work. Maximum door frame size :980 x 2070 including providing of 35mm thick factory made prelaminated ABS (Acrolynitrile Butadyne Styrene) Door shutter Moulded in Different designes,consisting of all round Frame made out of water proof solid foam PVC bar of size 20 x 32 mm, reinforced by 32 x 32 mm -2 no's for vertical made out of LVL (Laminated Veneer lumber) , core material of 32 mm thick high density craft paper honey comb board, sandwiched on both sides with prelaminated ABS sheet thickness of 1.5mm. PVC edge banding of size .45 mm on the vertcal sides. Hardware made out of steel coated butterfly hinges -3 No's. for each shutter and ISI make S.S round lock completes for finished item of work. maximum shutter of: 910 x 1030mm
|  | Prepost Oreraive Wards Double Shutter Door | 1 | 1 | 1.48 |  | 2.57 | 3.8036
|  | Store Room | 1 | 1 | 0.99 |  | 2.095 | 2.0741
|  | Manifold Room Single Shutter | 1 | 1 | 1.01 |  | 2.29 | 2.3129
|  | Sperm Collection Room Single Shutter | 1 | 1 | 0.978 |  | 2.27 | 2.2201
|  | Blood Collection Room Single Shutter | 1 | 1 | 0.991 |  | 2.26 | 2.2397
|  | Counseling Room1 | 1 | 1 | 1.08 |  | 2.25 | 2.43
|  | Counseling Room2 | 1 | 1 | 1.07 |  | 2.24 | 2.3968
|  | Ultra Sound Room Single Shutter Door | 1 | 1 | 1.2 |  | 2.37 | 2.844
|  | Record Room | 1 | 1 | 1.2 |  | 2.35 | 2.82
[8 empty] | 23.1411 | Sqm
13 | Sup | WPC Doors
|  | Toilet At Counseling Room | 1 | 1 | 0.8 |  | 2.1 | 1.68
|  | Toilet at Wards | 1 | 1 | 0.8 |  | 2.1 | 1.68
|  | Sperm Collection Toilet | 1 | 1 | 0.8 |  | 2.1 | 1.68
|  | Dr. Toilet | 1 | 1 | 1 |  | 2.1 | 2.1
[8 empty] | 7.14 | Sqm
14 | Sup | Blood Collection Room Table/Bed Chair
|  |  | 1 | 1 |  |  |  | 1
[8 empty] | 1 | Nos
15 | Sup | CSSD Table Autoclave room
|  |  | 1 | 1 |  |  |  | 1
[8 empty] | 1 | Nos
16 | Sup | 3-Bay Scrub Station
|  |  | 1 | 1 |  |  |  | 1
[8 empty] | 1 | Nos
17 | Sup | Cyocane 11 Ltrs
|  |  | 1 | 1 |  |  |  | 1
[8 empty] | 1 | Nos
18 | Sup | ICU Beds With Side Tables
|  |  | 1 | 5 |  |  |  | 5
[8 empty] | 5 | Nos
20 | Sup | RO Plant Autoclave Room
|  |  | 1 | 1 |  |  |  | 1
[8 empty] | 1 | Nos

## Abs-6
ABSTRACT
| Name of the work:Design, Fabriction, establishing and commissioning of In - Vitro ferility centers (IVFC) alongwith allied Services on Turnkey basis at Gandhi hospital secunderabad. | [7 empty] | Agency: M/s. Asta Vardhman Consortium | [5 empty] | Agt.No: 344/A/TSMIDC/Spl.Proj/IVFCs/2022-23,Dt.05.07.2023
S.No | Discription Of Work etc., | Measurements Upto date | [7 empty] | Per | Total Volume |  | Deduct/previous Measurements |  | Since last measurement |  |  | Remarks
|  | No |  | L | B | D | Content | Rs | Ps. |  | Rs. | Ps | P.No. | Qty. | Qty | Value
[16 empty] | Rs. | Ps.
49 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete (Brick Masonary)
| (Brick Masonary) |  |  |  |  | 32.68
| V.P 01 ABNO 10 |  |  |  |  | 31.21 | 31.21 | 398 | Cum | 12421.58 |  |  | 31.21 | 12421.58 | 0 | 0 |  |  | 398
| V.P 01 ABNO 10 |  |  |  |  | 1.47 | 1.47 | 398 | Cum | 585.06 |  |  | 1.47 | 585.06 | 0 | 0
Old Cement Morter
| V.P 01 ABNO 10 |  |  |  |  | 37.13 | 37.13 | 8 | Sqm | 297 |  |  | 37.13 | 297 | 0 | 0
Unreinforcement Cement More Than 15cm
| V.P 01 ABNO 10 |  |  |  |  | 3.89 | 3.89 | 2842 | Cum | 11055 |  |  | 3.89 | 11055 | 0 | 0
Reinforcement Cement
| V.P 01 ABNO 10 |  |  |  |  | 0.7 | 0.7 | 3115 | Cum | 2181 |  |  | 0.7 | 2181 | 0 | 0
51 | Dismantling doors, windows and clear storey windows, Ventilators etc., (wood or steel) shutters including Chowkhats, architraves,hold fasts and other attachments etc., and stacking them within 100m lead including labour charge etc., and overheads & contractors profit complete for finished item of work.
| V.P 01 ABNO 10 |  |  |  | Total | 7
| V.P 01 ABNO 10 |  |  |  | Ag | 5 | 5 | 468 | Each | 2340 |  |  | 5 | 2340 | 0 | 0 |  |  | 468
| V.P 01 ABNO 10 |  |  |  | AE | 2 | 2 | 468 | Each | 936 |  |  | 0 | 0 | 2 | 936
53 | Masonry work in CM (1:8) prop (cement: Screened sand) in super structure with / lime solid blocks of size 290mmx225mmx140mm from approved source having minimum crushing strength of 50 Kg/Sqcm including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, including sales & other taxes on all materials, all operational, incidental and labour charges such as mixing cement mortar, constructing masonry, scaffolding charges, lift charges, curing, etc., complete but excluding seigniorage charges for finished item of work. (APSS No. 501 & 504).
| V.P 01 ABNO 10 |  |  |  | Total | 15.27
| V.P 01 ABNO 10 |  |  |  | Ag | 9.03 | 9.03 | 16055 | Cum | 144977 |  |  | 9.03 | 144977 | 0 | 0 |  |  | 16055
| V.P 01 ABNO 10 |  |  |  | AE | 6.24 | 6.24 | 16055 | Cum | 100183 |  |  | 0 | 0 | 6.24 | 100183
54 | Reinforced brick Masonry for Partition Walls (11.0 cm thick) in CM (1:4) prop (cement: Screened sand) in super structure with / lime solid blocks of size 290mmx225mmx140mm from approved source having minimum crushing strength of 50 Kg/Sqcm including cost and conveyance of all materials like cement, sand, bricks, water etc., to site, including sales & other taxes on all materials, all operational, incidental and labour charges such as mixing cement mortar, constructing masonry, scaffolding charges, lift charges, curing, etc., complete but excluding seigniorage charges for finished item of work. (APSS No. 501 & 504).
| V.P 01 ABNO 10 |  |  |  | Total | 191.03 | 191.0305 | 1952 | Sqm | 372892 |  |  | 191.0305 | 372892 | 0 | 0 |  |  | 1952
55 | Providing Thermo Mechanically Treated ( TMT) ( Fe-500/500D/550D from primery producer TATA, SAIL, VSP, JSW Steel, Goel steel, Jindal panther, X- Vega & balaji Shakthi as per IS 1786-2008) of Different Diameters RCC Works , including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and sizes and typing and lap - spacing with binding wire of 18 SWG, Forming grills for reinforcement work as per approved design and drawings, including and conveyanace of steel bars, including all wastages such as overlaps, coupling, chairs, spacer bars including cost and conveyance of binding wire cover blocks and incidential, operational, labour charges such as cutting bending, placing in position, typing incliding sales and other taxes on all materials etc., and overheads & contractors profit completefor finished item of work
| V.P 01 ABNO 10 |  |  |  | Total | 0.103 | 0.103 | 116500 | MT | 12000 |  |  | 0.103 | 12000 | 0 | 0 |  |  | 116500
Sup | Supply and placing of the Design Mix Concrete M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Weight Batcher / Concrete mixer with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials, centering using Casurina Ballies, Bamboos, Wooden Reapers, Runners, Wood Posts, Steel Plates etc., including all operational, incidental and labour charges such as weigh batching, machine mixing, lifting of concrete manually, laying concrete, curing , overheads & contractors profit etc., complete but excluding cost of steel and its fabrication charges for finished item of work (APSS No. 402) (For Lintels)
| V.P 01 ABNO 10 |  |  |  | Total | 0.43 | 0.43 | 12775 | Cum | 5493 |  |  | 0.43 | 5493 | 0 | 0
56 | Plastering 12mm thick in two coats using screened sand with base coat of 8mm thick in CM (1:6) and top coat of 4mm thick in CM (1:4) with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales & other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and overheads & contractors profit complete for finished item of work. (SS 901,903 & 904).
| V.P 01 ABNO 10 |  |  |  | Total | 536.11 | 536.1091 | 1041 | Sqm | 558090 |  |  | 536.1091 | 558090 | 0 | 0 |  |  | 1041 | 22295.5
Sup | Flooring with 16 to 18 mm thick high polished granite stone slabs black colour as approved by the Engineer-in-Charge of length not less than 2.43 mts set over base coat of cement mortar (1:8) , 20mm thick using screened sand over CC bed already laid or RCC roof slab including neat grey cement slurry of honey like consistency spread @ 3.3 Kg per sqm and jointed neatly with white cement paste mixed with pigment of matching shade to full depth including cost and conveyance of all materials like cement , sand , water , granite slabs etc., to work site and all operational, incidental labour & lift charges, half rounding the edge , polishing charges and all other taxes on all materials, cost of base coat and overheads & contractors profit complete for finished item of work for platforms (S.S.701 & special) | [18 empty] | 22295.5
| V.P 02 ABNO 10 |  |  |  | Total | 10.17 | 10.166 | 6300 | Sqm | 64071 |  |  | 10.166 | 64071 | 0 | 0
65 | Flooring with soluble salt porcelain vitrified tiles screen printed and polished of size 600 x 600 mm and thickness between 8 to 10mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630Parts 1 to 15 of any colour and finish in all shades and designs with borders and design as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM 1:8 prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread at the rate 3.3 kgs per Sqm. and jointed neatly with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site excluding cost of C.C. bed including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in- charge etc., and complete for finished item of work. TSSS No.701 and 707. 5th Floor at Gandhi Hospital
| V.P 02 AB NO 10 |  |  |  | Total | 374.81
[5 empty] | Ag | 225 | 225 | 1725 | Sqm | 388125 |  |  | 225 | 388125 | 0 | 0 |  |  | 1725
[5 empty] | AE | 149.81 | 149.81 | 1725 | Sqm | 258422 |  |  | 0 | 0 | 149.81 | 258422
66 | Flooring with non-skid full body ceramic floor tiles of size 300mm x 300mm and thickness between 7 - 8mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630 Part 1 to 15 of any colour and finish in all shades and designs as approved by Engineer-in-charge, set over base coat of cement mortar 1:8, 12mm thick using screened sand over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread at the rate 3.3 Kgs per Sqm and jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, screened sand , water and tiles etc., complete for finished item of work. TSSS No.701 and 707 at Gandhi Hospital
| V.P 02 AB NO 10 |  |  |  | Total | 14.62 | 14.618 | 1525 | Sqm | 22296 |  |  | 14.618 | 22296 | 0 | 0 |  |  | 1525
68 | Providing dadooing to walls with glazed full body porcelain wall tiles of size 300 x 600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. 5th Floor at Gandhi Hospital
| V.P 02 AB NO 10 |  |  |  | Total | 103.76
[5 empty] | Ag | 40 | 40 | 1423 | Sqm | 56920 |  |  | 40 | 56920 | 0 | 0 |  |  | 1423
[5 empty] | AE | 63.77 | 63.766 | 1423 | Sqm | 90739 |  |  | 0 | 0 | 63.766 | 90739
Sup | Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707)
| V.P 02 AB NO 10 |  |  |  | Total | 107.18 | 107.179 | 114 | Rmt | 12219 |  |  | 107.179 | 12219 | 0 | 0
Electrical-1
96 | Supply and Fixing of 25mm outer dia medium grade, FRLS with IS:9537 part 3 rigid PVC pipe Concealed in with all required PVC/ Metalic junction boxes a including masonary work and labour charges etc., complete Makes:- Sudhakar / Modi
| V.P 02 AB NO 10 |  |  |  | Total | 415.5
[5 empty] | Ag | 200 | 200 | 116 | Rmt | 23200 |  |  | 200 | 23200 | 0 | 0 |  |  | 116
| V.P 02 AB NO 10 |  |  |  | AE | 215.5 | 215.5 | 116 | Rmt | 24998 |  |  | 0 | 0 | 215.5 | 24998
97 | Supply and Fixing of 25mm outer dia medium grade, FRLS with IS:9537 part 3 rigid PVC pipe with all accessories fixing on wall / ceiling with chromium plated metallic base saddles including all labour charges etc., complete Makes:- Modi
| V.P 02 AB NO 10 |  |  |  | Total | 1060.2
| V.P 02 AB NO 10 |  |  |  | Ag | 500 | 500 | 107 | Rmt | 53500 |  |  | 500 | 53500 | 0 | 0 |  |  | 107
| V.P 02 AB NO 10 |  |  |  | AE | 560.2 | 560.2 | 107 | Rmt | 59941 |  |  | 0 | 0 | 560.2 | 59941
98 | Wiring with run of 2 of 22/0.3mm (1.5 Sqmm) FRLS / HFFR PVC insulated flexible ISI mark copper cable in existing PVC conduit pipe including Supply and fixing of Jumbo Ceiling rose and 6A/10A ISI Mark 1way Modular switch with required modular box and cover frame in existing Surface or Concealed pipe wiring including cost and conveyance of all material and all labour charges etc., complete for light, Fan, Exhaust fan and bell points in N.R.B. Makes of wires : Polycab (HFFR) Makes of switches :Honeywell Blenge Plus
| V.P 02 AB NO 10 |  |  |  | Total | 146
| V.P 02 AB NO 10 |  |  |  | Ag | 110 | 110 | 945 | No | 103950 |  |  | 110 | 103950 | 0 | 0 |  |  | 945
| V.P 02 AB NO 10 |  |  |  | AE | 36 | 36 | 975 | No | 35100 |  |  | 0 | 0 | 36 | 35100
99 | Supply and fixing of 6A/10A ISI Mark 3/2 pin Modular socket with 6A/10A 1way Modular switch, 3 Module box with cover frame a Common switch board including cost and conveyance of all materials and all labour charges etc., complete in N.R.B. / R.B. Makes of switches : Honeywell Blenge Plus
| V.P 03 AB NO 10 |  |  |  | Total | 30
| V.P 03 AB NO 10 |  |  |  | Ag | 12 | 12 | 675 | No | 8100 |  |  | 12 | 8100 | 0 |  |  |  | 675
| V.P 03 AB NO 10 |  |  |  | AE | 18 | 18 | 675 | No | 12150 |  |  | 0 | 0 | 18 | 12150
100 | Supply and fixing of 16A switches - 1Nos and 6/16A 2 in one socket - 1Nos Modular type with cover plate and GI switch box fixing on separate board including all labour charges etc., complete. Makes of switches: - Hooney well Benzplus
| V.P 03 AB NO 10 |  |  |  | Total | 14 | 14 | 1040 | No | 14560 |  |  | 14 | 14560 | 0 | 0 |  |  | 1040
101 | Supply & fixing of 16A/6A, 2 in one socket - 2 Nos with 16A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benzplus
| V.P 03 AB NO 10 |  |  |  | Total | 53 | 53 | 1755 | No | 93015 |  |  | 53 | 93015 | 0 | 0 |  |  | 1755
104 | Supply and Run of 3 of 36/0.3mm (2.50 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
| V.P 03 AB NO 10 |  |  |  | Total | 637.1
| V.P 03 AB NO 10 |  |  |  | Ag | 600 | 600 | 177 | Rmt | 106200 |  |  | 600 | 106200 | 0 | 0 |  |  | 177
| V.P 03 AB NO 10 |  |  |  | AE | 37.1 | 37.1 | 177 | Rmt | 6567 |  |  | 0 | 0 | 37.1 | 6567
105 | Supply and Run of 3 of 56/0.3mm (4.00 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
| V.P 03 AB NO 10 |  |  |  | Total | 1349.1
| V.P 03 AB NO 10 |  |  |  | Ag | 1200 | 1200 | 255 | Rmt | 306000 |  |  | 1200 | 306000 | 0 | 0 |  |  | 255
| V.P 03 AB NO 10 |  |  |  | AE | 149.1 | 149.1 | 255 | Rmt | 38021 |  |  | 0 | 0 | 149.1 | 38021
106 | Supply and Run of 5 of 90/0.3mm (6.0 Sq.mm) FRLS / HFFR PVC insulated flexible ISI mark copper cable of in existing pipe for run of mains inlcuding all labour charges etc., complete. Makes of wires : Polycab
| V.P 03 AB NO 10 |  |  |  | Total | 333.3
| V.P 03 AB NO 10 |  |  |  | Ag | 60 | 60 | 606 | Rmt | 36360 |  |  | 60 | 36360 | 0 | 0 |  |  | 606
| V.P 03 AB NO 10 |  |  |  | AE | 273.3 | 273.3 | 606 | Rmt | 165620 |  |  | 0 | 0 | 273.3 | 165620
107 | Supply & run of 5 of 10.0 Sqmm (140/0.3 mm) (3 phases, neutral and earth) FRLS / HFFR PVC insulated flexible copper cable in the existing conduit pipe for run of mains from Power panel board to TPN DB"s with pin type lugs and connections etc., complete. [for PDBs] Makes of wires: Polycab
| V.P 03 AB NO 10 |  |  |  | Total | 145.1
| V.P 03 AB NO 10 |  |  |  | Ag | 40 | 40 | 967 | Rmt | 38680 |  |  | 40 | 38680 | 0 | 0 |  |  | 967
| V.P 03 AB NO 10 |  |  |  | AE | 105.1 | 105.1 | 967 | Rmt | 101632 |  |  | 0 | 0 | 105.1 | 101632
109 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand and Supply and Fixing of 1 No., of 40A FP 30mA RCCB as incomer and 12 Nos 6-32 A 10kA SP MCBs Makes: Legrand-DX3 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. (For Lighting DBs) Make Legrand
| V.P 03 AB NO 10 |  |  |  | Total | 8
| V.P 03 AB NO 10 |  |  |  | Ag | 3 | 3 | 18325 | No | 54975 |  |  | 3 | 54975 | 0 | 0 |  |  | 18325
| V.P 03 AB NO 10 |  |  |  | AE | 5 | 5 | 18325 | No | 91625 |  |  | 0 | 0 | 5 | 91625
110 | Supply and fixing of 8 Way VTPN DB with IP 43 Protection as per IS:13032 with 1 No., of 125A 4P MCCB, Adjustable, Confirms to IS/IEC 60947-2 having Breaking Capacity 25 KA with thermal magnetic release Panel Mounted as incomer with 8 Nos of 63A, 10KA, TP MCBs C Curve ISI Mark as Out goings including internal connections and labour charges for FLUSH Mounting etc., complete. Makes : Legrand / Schneider
| V.P 04 AB NO 10 |  |  |  | Total | 1 | 1 | 28460 | No | 28460 |  |  | 1 | 28460 | 0 | 0 |  |  | 28460
114 | Supply, transportation and fixing of 24W edge lit LED Down light Square Housing Made of Aluminium alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser Square with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor > 0.9, Surge protection: > 2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI >80, and THD is less than 15% etc., with BIS Certification. Makes: Crompton
| V.P 04 AB NO 10 |  |  |  | Total | 44 | 44 | 2652 | No | 116688 |  |  | 44 | 116688 | 0 | 0 |  |  | 2652
115 | Supply and Transportation 36W Edge lit, 2' x2' (600mm x600mm) slim panel LED luminaire Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% etc., complete. Makes: Crompton
| V.P 04 AB NO 10 |  |  |  | Total | 40
| V.P 04 AB NO 10 |  |  |  | Ag | 30 | 30 | 4350 | No | 130500 |  |  | 30 | 130500 | 0 | 0 |  |  | 4350
| V.P 04 AB NO 10 |  |  |  | AE | 10 | 10 | 4350 | No | 43500 |  |  | 0 | 0 | 10 | 43500
119 | Supply and fixing of Modular type Stepped electronic regulator Makes : GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/ Cabtree Verna/ Million logus / Gold Medal Curve for sweep AC ceiling fans of 1200mm / 1400mm complete with connections.
| V.P 04 AB NO 10 |  |  |  | Total | 14
| V.P 04 AB NO 10 |  |  |  | Ag | 12 | 12 | 827 | No | 9924 |  |  | 12 | 9924 | 0 | 0 |  |  | 827
| V.P 04 AB NO 10 |  |  |  | AE | 2 | 2 | 827 | No | 1654 |  |  | 0 | 0 | 2 | 1654
122 | SITC of Hot dip galvanized perforated cable tray of 300 mm Wide sizes for to run the cable from Floor Panel to Lab Panel & electrical room to AC panel and AC panel to Units. All necessary supports & accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. ( Elec 4.10.1 d)
| V.P 04 AB NO 10 |  |  |  | Total | 85.4
| V.P 04 AB NO 10 |  |  |  | Ag | 80 | 80 | 1310 | Rmt | 104800 |  |  | 80 | 104800 | 0 | 0 |  |  | 1310
| V.P 04 AB NO 10 |  |  |  | AE | 5.4 | 5.4 | 1310 | Rmt | 7074 |  |  | 0 | 0 | 5.4 | 7074
128 | Supply & installation of 50x6 GI flat for body earthing of electrical panel & AC Panel which is laid in 300mm cable tray
| V.P 04 AB NO 10 |  |  |  | Total | 184.9 | 184.9 | 329 | Rmt | 60832 |  |  | 184.9 | 60832 | 0 | 0 |  |  | 329
129 | Supply & installation of 25x3 GI flat for body earthing of DBs & Cable tray which is laid in 100mm cable tray
| V.P 04 AB NO 10 |  |  |  | Total | 116.3
| V.P 04 AB NO 10 |  |  |  | Ag | 100 | 100 | 163 | Rmt | 16300 |  |  | 100 | 16300 | 0 | 0 |  |  | 163
| V.P 04 AB NO 10 |  |  |  | AE | 16.3 | 16.3 | 163 | Rmt | 2657 |  |  | 0 | 0 | 16.3 | 2657
131 | Supply & installation of 4 sqmm Copper wire for Earthing of DBs Equipment
| V.P 04 AB NO 10 |  |  |  | Total | 286
| V.P 04 AB NO 10 |  |  |  | Ag | 80 | 80 | 83 | Rmt | 6640 |  |  | 80 | 6640 | 0 | 0 |  |  | 83
| V.P 04 AB NO 10 |  |  |  | AE | 206 | 206 | 83 | Rmt | 17098 |  |  | 0 | 0 | 206 | 17098
132 | Supply, Lying & testing of 3.5Cx95 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/ Glostar/ Finolex Make of gland & Lungs: HMI/ Commet /Dowell’s
| V.P 05 AB NO 10 |  |  |  | Total | 83 | 83 | 1207 | Rmt | 100181 |  |  | 83 | 100181 | 0 | 0 |  |  | 1207
133 | Supply, Lying & testing of 3.5CX50 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/ Universal/ Glostar/ Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
| V.P 05 AB NO 10 |  |  |  | Total | 40 | 40 | 722 | Rmt | 28880 |  |  | 40 | 28880 | 0 | 0 |  |  | 722
149 | Split AC unit 1.5 TR inverter type 3 Star capable of delivering 18000 BTU/hr and above with high wall mounted indoor unit and outdoor condensing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord , built-in stabilizer Voltage range 160- 264 volts and cordless remote control. Makes : Daikin / Thoshiba / O General at Gandhi Hospital
| V.P 05 AB NO 10 |  |  |  | Total | 2
[5 empty] | Ag | 1 | 1 | 43200 | Nos | 43200 |  |  | 1 | 43200 | 0 | 0 |  |  | 48000
[5 empty] | AE | 1 | 1 | 43200 | Nos | 43200 |  |  | 0 | 0 | 1 | 43200
124 | Batteries : Supply and fixing of 12V 65 AH SMF battery including wire leads. Makes: Quanta / Racket / Exide. At Gandhi Hospital
| V.P 05 AB NO 10 |  |  |  | Total | 32
| V.P 05 AB NO 10 |  |  |  | Ag | 20 | 20 | 18526 | Nos | 370520 |  |  | 20 | 370520 |  |  |  |  | 20584
| V.P 05 AB NO 10 |  |  |  | AE | 12 | 12 | 18526 | Nos | 222312 |  |  | 0 | 0 | 12 | 222312
125 | Supply and providing of UPS com Batteri rack for 20 batteries . At Gandhi Hospital
| V.P 05 AB NO 10 |  |  |  | Total | 1 | 1 | 6088 | Nos | 6088 |  |  | 1 | 6088 | 0 | 0 |  |  | 6764
123 | 20 KVA UPS: Supply and installation of 20KVA 3ph in and 3ph out on line UPS system IGBT based rectifier with input power factor correction 32 bit microprocessor based with isolation transformers double conversion, SNMP controls, LCD display, Pure sine wave output, with auto static switch three phase input / Three phase output and modular structure for better thermal technology / cooling facility, with warranty up to three years.Makes: APC / Numeric / Emerson / Fuji Electric At Gandhi Hospital
| V.P 05 AB NO 10 |  |  |  | Total | 1 | 1 | 274500 | Nos | 274500 |  |  | 1 | 274500 | 0 | 0 |  |  | 305000
173 | Condensing units - VRF/VRV System 16 HP: Supply, Installation, Nitrogen testing , Vacuuming and Commissioning of air cooled variable refrigerant flow modular type condensing units, each comprising of multiple scroll compressors all inverter driven, full charge of refrigerant gas R-410a including additional gas filling , lubricating oil and all accessories as per the specifications. The condensing units shall be suitable to work on cooling mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B . The COP of the system shall be greater than 4 under ARI conditions for 100percentage load . The condensing units shall be suitable for operation on 415 plus or minus 10percentage volts, 50Hz, 3 phase AC power supply and , outdoor units to be mounted on MS platform with suitable Vibration Isolation pads to avoid vibrations. All the supports and angle base frame structure to be duly black painted with synthetic epoxy paint. the condensing units shall be of following capacities: The VRF ODU should be capable of working with total capacity of connected indoor units ranging between 100percentage to 140percentage of ODU capacity . COP minimum 3.5. Make : Daikin / LG / O General / Toshiba. 16 HP At Gandhi Hospital
| V.P 05 AB NO 10 |  |  |  | Total | 1 | 1 | 292500 | Nos | 292500 |  |  | 1 | 292500 | 0 | 0 |  |  | 325000
174 | VRF Indoor Units : Hi wall Splits 0.8 TR: Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 0.8 TR At Gandhi Hospital
| V.P 05 AB NO 10 |  |  |  | Total | 1 | 1 | 27630 | Nos | 27630 |  |  | 1 | 27630 | 0 | 0 |  |  | 30700
175 | VRF Indoor Units : Hi wall Splits 1.0 TR: Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.0 TR At Gandhi Hospital
| V.P 06 AB NO 10 |  |  |  | Total | 4 | 4 | 27630 | Nos | 110520 |  |  | 4 | 110520 | 0 | 0 |  |  | 30700
176 | VRF Indoor Units 1.5 TR : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.5 TR At Gandhi Hospital
| V.P 06 AB NO 10 |  |  |  | Total | 5
[5 empty] | Ag | 4 | 4 | 31500 | Nos | 126000 |  |  | 4 | 126000 | 0 | 0 |  |  | 35000
[5 empty] | AE | 1 | 1 | 31500 | Nos | 31500 |  |  | 0 | 0 | 1 | 31500
177 | Cassette Units 3.0 TR : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling mode.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 3.0 TR – 4 way At Gandhi Hospital
| V.P 06 AB NO 10 |  |  |  | Total | 1 | 1 | 45000 | Nos | 45000 |  |  | 1 | 45000 | 0 | 0 |  |  | 50000
3 | DICOM compatible fully digital, compact, portable, Ultrasound Scan Machine Colour Doppler at Gandhi Hospital
| V.P 06 AB NO 10 |  |  |  | Total | 2 | 2 | 1228500 | Nos | 2457000 |  |  | 2 | 2457000 | 0 | 0 |  |  | 1365000
27 | Defibrilator at Gandhi Hospital
| V.P 06 AB NO 10 |  |  |  | Total | 1 | 1 | 281250 | Nos | 281250 |  |  | 1 | 281250 | 0 | 0 |  |  | 312500
30 | Anesthasia work station at Gandhi Hospital
| V.P 06 AB NO 10 |  |  |  | Total | 1 | 1 | 843750 | Nos | 843750 |  |  | 1 | 843750 | 0 | 0 |  |  | 937500
31 | Autoclave at Gandhi Hospital
| V.P 06 AB NO 10 |  |  |  | Total | 1 | 1 | 506250 | Nos | 506250 |  |  | 1 | 506250 | 0 | 0 |  |  | 562500
35 | Ultrasound Examination Couch at Gandhi Hospital
| V.P 06 AB NO 10 |  |  |  | Total | 1 | 1 | 73125 | Nos | 73125 |  |  | 1 | 73125 | 0 | 0 |  |  | 81250
2 | IVF Test tube Warmers at Gandhi Hospital
| V.P 06 AB NO 10 |  |  |  | Total | 2 | 2 | 44550 | Nos | 89100 |  |  | 2 | 89100 | 0 | 0 |  |  | 49500
4 | Multipurpose Electro hydraulic with manual override mobile OT Table, with divided leg section suitable for all Gynaecological surgical procedures, complete with 5cm Mattress and corded handset at Gandhi Hospital
| V.P 07 AB No 10 |  |  |  | Total | 2
[5 empty] | Ag | 1 | 1 | 507375 | Nos | 507375 |  |  | 1 | 507375 |  |  |  |  | 563750
[5 empty] | AE | 1 | 1 | 507375 | Nos | 507375 |  |  | 0 | 0 | 1 | 507375
5 | LED procedure Lights Double dome at Gandhi Hospital
| V.P 07 AB No 10 |  |  |  | Total | 1 | 1 | 281250 | Nos | 281250 |  |  | 1 | 281250 | 0 | 0 |  |  | 312500
6 | LED procedure Lights Single dome at Gandhi Hospital
| V.P 07 AB No 10 |  |  |  | Total | 1 | 1 | 168750 | Nos | 168750 |  |  | 1 | 168750 | 0 | 0 |  |  | 187500
14 | IVF Thermometer with Probe
| V.P 07 AB No 10 |  |  |  | Total | 1 | 1 | 55688 | Nos | 55688 |  |  | 1 | 55688 | 0 | 0 |  |  | 61875
15 | CO2 Cylinder with accessories
| V.P 07 AB No 10 |  |  |  | Total | 2 | 2 | 45000 | Nos | 90000 |  |  | 2 | 90000 | 0 | 0 |  |  | 50000
26 | Cryocane TA 26 Ltr with wheels
| V.P 07 AB No 10 |  |  |  | Total | 2 | 2 | 55688 | Nos | 111376 |  |  | 2 | 111376 | 0 | 0 |  |  | 61875
16 | CO2 and O2 Analyzer
| V.P 07 AB No 10 |  |  |  | Total | 1 | 1 | 340200 | Nos | 340200 |  |  | 1 | 340200 | 0 | 0 |  |  | 378000
17 | PH Meter
| V.P 07 AB No 10 |  |  |  | Total | 1 | 1 | 84375 | Nos | 84375 |  |  | 1 | 84375 | 0 | 0 |  |  | 93750
19 | Sperm Counting Chamber
| V.P 07 AB No 10 |  |  |  | Total | 1 | 1 | 68063 | Nos | 68063 |  |  | 1 | 68063 | 0 | 0 |  |  | 75625
20 | Binocular Microscope MLX-B Plus
| V.P 07 AB No 10 |  |  |  | Total | 1 | 1 | 37125 | Nos | 37125 |  |  | 1 | 37125 | 0 | 0 |  |  | 41250
22 | Clinical Centrifuge machine for Andrology with Acessories
| V.P 07 AB No 10 |  |  |  | Total | 1 | 1 | 31050 | Nos | 31050 |  |  | 1 | 31050 | 0 | 0 |  |  | 34500
34 | Mulitfunctional Printer
| V.P 08 AB No 010 |  |  |  | Total | 1 | 1 | 39375 | Nos | 39375 |  |  | 1 | 39375 | 0 | 0 |  |  | 43750
37 | Laptop
| V.P 08 AB No 010 |  |  |  | Total | 2 | 2 | 103500 | Nos | 207000 |  |  | 2 | 207000 | 0 | 0 |  |  | 115000
23 | DRY Incubator
| V.P 08 AB No 010 |  |  |  | Total | 1 | 1 | 507375 | Nos | 507375 |  |  | 1 | 507375 | 0 | 0 |  |  | 563750
9 | CO2 Incubators
| V.P 08 AB No 010 |  |  |  | Total | 2 | 2 | 742500 | Nos | 1485000 |  |  | 2 | 1485000 | 0 | 0 |  |  | 825000
1 | Ovum Aspiration Pumps at Gandhi Hospital
| V.P 08 AB No 010 |  |  |  | Total | 2 | 2 | 216000 | Nos | 432000 |  |  | 2 | 432000 | 0 | 0 |  |  | 240000
7 | IVF Workstation with LAF at Gandhi Hospital
| V.P 08 AB No 010 |  |  |  | Total | 1 | 1 | 618750 | Nos | 618750 |  |  | 1 | 618750 | 0 | 0 |  |  | 687500
8 | IVF Anti-vibration Table for Procedure
| V.P 08 AB No 010 |  |  |  | Total | 1 | 1 | 86625 | Nos | 86625 |  |  | 1 | 86625 | 0 | 0 |  |  | 96250
10 | Trigas Bench Top Incubators for Human Embryo culture
| V.P 08 AB No 010 |  |  |  | Total | 1 | 1 | 742500 | Nos | 742500 |  |  | 1 | 742500 | 0 | 0 |  |  | 825000
11 | Trinocular Stereozoom Microscope
| V.P 08 AB No 010 |  |  |  | Total | 1 | 1 | 278100 | Nos | 278100 |  |  | 1 | 278100 | 0 | 0 |  |  | 309000
12 | ICSI Micro Manipulator with Inverted Microscope
| V.P 08 AB No 010 |  |  |  | Total | 1 | 1 | 2362500 | Nos | 2362500 |  |  | 1 | 2362500 | 0 | 0 |  |  | 2625000
13 | IVF Laser System
| V.P 08 AB No 010 |  |  |  | Total | 1 | 1 | 2304000 | Nos | 2304000 |  |  | 1 | 2304000 | 0 | 0 |  |  | 2560000
18 | VOC Meter for ART Lab
| V.P 09 AB No 010 |  |  |  | Total | 1 | 1 | 658125 | Nos | 658125 |  |  | 1 | 658125 | 0 | 0 |  |  | 731250
21 | Laminar Flow Cabinet with Andrology Work Station
| V.P 09 AB No 010 |  |  |  | Total | 1 | 1 | 225000 | Nos | 225000 |  |  | 1 | 225000 | 0 | 0 |  |  | 250000
24 | Pipetter and Denudation system
| V.P 09 AB No 010 |  |  |  | Total | 1 | 1 | 92813 | Nos | 92813 |  |  | 1 | 92813 | 0 | 0 |  |  | 103125
25 | Pharmaceutical Refrigerator
| V.P 09 AB No 010 |  |  |  | Total | 1 | 1 | 202500 | Nos | 202500 |  |  | 1 | 202500 | 0 | 0 |  |  | 225000
28 | 7 Para Patient Monitor
| V.P 09 AB No 010 |  |  |  | Total | 2 | 2 | 252000 | Nos | 504000 |  |  | 2 | 504000 | 0 | 0 |  |  | 280000
29 | Suction Machine
| V.P 09 AB No 010 |  |  |  | Total | 1 | 1 | 44550 | Nos | 44550 |  |  | 1 | 44550 | 0 | 0 |  |  | 49500
32 | Operative Hysteroscopy and Resectoscope Set Machine
| V.P 09 AB No 010 |  |  |  | Total | 1 | 1 | 1912500 | Nos | 1912500 |  |  | 1 | 1912500 | 0 | 0 |  |  | 2125000
33 | Operative Laparoscopy Set
| V.P 09 AB No 010 |  |  |  | Total | 1 | 1 | 3780000 | Nos | 3780000 |  |  | 1 | 3780000 | 0 | 0 |  |  | 4200000
39 | Reception Chair
| V.P 09 AB No 010 |  |  |  | Total | 2 | 2 | 31050 | Nos | 62100 |  |  | 2 | 62100 | 0 | 0 |  |  | 34500
42 | Consultant Chair
| V.P 09 AB No 010 |  |  |  | Total | 3 | 3 | 17325 | Nos | 51975 |  |  | 3 | 51975 | 0 | 0 |  |  | 19250
43 | Patient Chair
| V.P 09 AB No 010 |  |  |  | Total | 6 | 6 | 12375 | Nos | 74250 |  |  | 6 | 74250 | 0 | 0 |  |  | 13750
44 | Small Trolley
| V.P 09 AB No 010 |  |  |  | Total | 3 | 3 | 35280 | Nos | 105840 |  |  | 3 | 105840 | 0 | 0 |  |  | 39200
45 | Big Trolley
| V.P 10 AB No 010 |  |  |  | Total | 3 | 3 | 56250 | Nos | 168750 |  |  | 3 | 168750 | 0 | 0 |  |  | 62500
46 | Wall Storage Cabinets
| V.P 10 AB No 010 |  |  |  | Total | 8 | 8 | 15750 | Nos | 126000 |  |  | 8 | 126000 | 0 | 0 |  |  | 17500
151 | Modular Double skin floor mounted EUROVENT Certified Air Handling Unit 3400CFM / 8.5 TR / 150mm SP made out of 45 plus or minus 2mm thick PUF insulated panels Thermal break aluminium profile frame work with 0.8mm thick pre painted / powder coated inner and outer skins comprising of mixing box with fresh air and return air dampers, pre filters with 10 and 5 microns combination filters in single frame, Interlaced/Intertwined DX Cooling Coil suitable for connecting 2 nos of 8.5TR capacity 1W plus 1S out door condensing units, SS304 drain pan with , blower section with Nicotra / Kruger make direct drive/ Plug type fan, vibration isolators, EFF1 motor and blower section with on/off switches to operate from outside, limit switch for the fan section access door with a view port, fine filter section with 3 microns filters inspection doors for all filter and fan sections and damper at the outlet of unit. Ports for differential pressure gauges across all filters and blower to measure differential pressure. AHU Make : VTS / Systemair, Make - Blower - Nicotra / Kruger ; Motor - Crompton Greaves / Siemens ; Filter - Thermodyne / Freudenberg / Ultrafil at Gandhi Hospital
| V.P 10 AB No 010 |  |  |  | Total | 1 | 1 | 531000 | Nos | 531000 |  |  | 1 | 531000 | 0 | 0 |  |  | 590000
166 | SITC of Magnehelic gauges across pre and fine filter at AHUs including mounting arrangement, SS nozzles, food grade PVC tubing, etc. At Gandhi Hospital
| V.P 10 AB No 010 |  |  |  | Total | 3 | 2 | 9450 | Nos | 18900 |  |  | 2 | 18900 | 0 | 0 |  |  | 10500
[6 empty] | AE | 1
167 | SITC of Magnehelic gauges to measure the room differential pressures in operation theatres with SS mounting box, SS nozzles, food grade PVC tubing, etc. At Gandhi Hospital
| V.P 10 AB No 010 |  |  |  | Total | 2 | 2 | 11610 | Nos | 23220 |  |  | 2 | 23220 | 0 | 0 |  |  | 12900
153 | SITC of air cooled condensing units with two scroll compressors, air cooled condenser, power panel, vibration isolating pads, stand for ODU, thermostat, etc. of the following capacities. The nominal capacity of the condensing unit shall be as under. Air cooled condensing unit shall have horizontal discharge. All refrigerant piping accessories sight glass, drier, expansion valve, etc. shall be supplied with the condensing units and suitable to connect above AHUs. Refrigerant shall be R 407C / R 410A. Necessary thermostat, control wiring, etc. shall be included. Derating of the unit shall not be more than 15percentage under 45 deg. C ambient temperature. Condensing unit shall be capable of operating up 50 deg. C ambient temperature. 8.5 TR capacity At Gandhi Hospital
| V.P 10 AB No 010 |  |  |  | Total | 2
| V.P 10 AB No 010 |  |  |  | Ag | 1 | 1 | 163800 | Nos | 163800 |  |  | 1 | 163800 | 0 | 0 |  |  | 182000
| V.P 10 AB No 010 |  |  |  | AE | 1 | 1 | 163800 | Nos | 163800 |  |  | 0 | 0 | 1 | 163800
154 | SITC of Flange type, Flame proof FLP duct heaters of 5 kW capacity with Mineral Filled AISI SS304/SS321 Sheathed Tubular Heater with GI Helical fins, Tube dia 8.2mm min and Helical Finn dia 25mm min, enclosed in the frame, FLP Terminal box etc., Nickel Chromium Inner Element, Silicon Sealing to Restrict Moisture pickup, Silver brazed mounting plate etc., and heaters shall be controlled with PID thyrestor controller based on the analog output signal of 0-10 V DC of controller . And this should have saftey thermostat and cutouts and air stat etc. all safety controls. The capacities as follows and sizes of the heaters shall be as per the duct sizes and approved drawing. at Gandhi Hospital
| V.P 10 AB No 010 |  |  |  | Total | 1 | 1 | 184500 | Nos | 184500 |  |  | 1 | 184500 | 0 | 0 |  |  | 205000
152 | Supply and Installation of AL-powdercoated bottom loading type HEPA filter modules with bewel gear arrangement damper with access from clean room suitable to house the following size flange type HEPA filters including GI pressure plate, GI cleats with bolts and pressure drop & Integrity testing ports into room.Supply and Installation of H14 HEPA filters with 99.995% efficiency of the following sizes 600 X 600 X 150MM - HEPA filter - Module height <=350 mm,600 x 600 x 150 mm - 1000 CFM,600 x 600 x 150 mm - 1000 CFM
| V.P 10 AB No 010 |  |  |  | Total | 6 | 6 | 37800 | Nos | 226800 |  |  | 6 | 226800 | 0 | 0 |  |  | 42000
140 | Supply, Installation, testing And Commissioning of 20 nos LAN points with cat 6 cable and with suitable network rack and 5 nos of telephone points with knore box to existing EPABEX. At Gandhi Hospital
| V.P 11 AB No 010 |  |  |  | Total | 1 | 1 | 344700 | Job | 344700 |  |  | 1 | 344700 | 0 | 0 |  |  | 383000
141 | Supply, Installation, testing And Commissioning of 1 no of Access control system with egress switch, power cable communication cable to control panel with necessary required items etc,. At Gandhi Hospital
| V.P 11 AB No 010 |  |  |  | Total | 1 | 1 | 111600 | Nos | 111600 |  |  | 1 | 111600 | 0 | 0 |  |  | 124000
142 | Supply, Installation, testing And Commissioning of Automatic Fire Alaram system which is including 30 nos of smoke detectors 1nos manual call point 1 nos hooter with fire alaram cable connected to the existing fire control panel with necessary required item etc,. At Gandhi Hospital
| V.P 11 AB No 010 |  |  |  | Total | 1 | 1 | 459000 | Job | 459000 |  |  | 1 | 459000 | 0 | 0 |  |  | 510000
143 | Supply, Installation, testing And Commissioning of 5 nos IP Based CCTV camers and cat 6 cable with NVR system. At Gandhi Hospital
| V.P 11 AB No 010 |  |  |  | Total | 1 | 1 | 163800 | Job | 163800 |  |  | 1 | 163800 | 0 | 0 |  |  | 182000
144 | Supply, Installation, testing And Commissioning of Audio and video recording of counseling rooms . At Gandhi Hospital
| V.P 11 AB No 010 |  |  |  | Total | 1 | 1 | 124200 | Job | 124200 |  |  | 1 | 124200 | 0 | 0 |  |  | 138000
145 | Supply and Installation of fire Extinguisher of CO2 4.5 kg at Gandhi Hospital
| V.P 11 AB No 010 |  |  |  | Total | 5 | 5 | 10103 | Nos | 50515 |  |  | 5 | 50515 | 0 | 0 |  |  | 11225
146 | Supply and iInstalltion of ceiling mounted Fire extinguiser of ABC MAP 90, 5.0 kg stored pressure type at Gandhi Hospital
| V.P 11 AB No 010 |  |  |  | Total | 5 | 5 | 6917 | Nos | 34585 |  |  | 5 | 34585 | 0 | 0 |  |  | 7686
147 | Supply and Installtion of 2.0 kg clean agent HCFC 123 Fire Extinguiser at Gandhi Hospital
| V.P 12 AB No 010 |  |  |  | Total | 5 | 5 | 13559 | Nos | 67795 |  |  | 5 | 67795 | 0 | 0 |  |  | 15065
148 | Supply and Installaion of Fire escape signage Boards at Gandhi Hospital
| V.P 12 AB No 010 |  |  |  | Total | 1 | 1 | 50400 | Job | 50400 |  |  | 1 | 50400 | 0 | 0 |  |  | 56000
94 | Air Shower Supply and installation,testing and commissioning of 16 GI Power coated Suitable single person entry air shower
| V.P 12 AB No 010 |  |  |  | Total | 1 | 1 | 319500 | Job | 319500 |  |  | 1 | 319500 | 0 | 0 |  |  | 355000
95 | Supply and installation,testing and commissioning of Static Pass Boxes Of Size 450 x 450mm with 1.2mm thick SS 304 Mat finish, with interlock doors, UV light on When Doors Closed Condition. As per Clean room standard and requirements
| V.P 12 AB No 010 |  |  |  | Total | 3 | 3 | 54900 | Job | 164700 |  |  | 3 | 164700 | 0 | 0 |  |  | 61000
Copper Pipe
178 | Supply installation,Testing and Commissioning of Hard Copper REFRIGERANT PIPING of 16 swg various sizes with necessary supports,fittings, interconnecting the liquid and suction lines between the indoor units. The piping shall be carried out of hard drawn copper pipes of type K with soldered/brazed socket fittings.Isolate each compressor, stainers,sight glass and any other componenet requiring proper operation and maintanance.Both the suction and liquid lines sahll be insulated with 19mm thick closed cell insulation for above 25mm dia,13mm thick for pipes below 25mm dia. the insulation finished with treated woven glass fiber reinforced covering for inside piping and including making required holes in the wall and re finishing and water tight of holes after laying holes as per the specifications and approved drawings at Gandhi Hospital
| V.P 12 AB No 010 |  |  |  | Total | 1 | 1 | 360000 | Job | 360000 |  |  | 1 | 360000 | 0 | 0 |  |  | 400000
179 | Supply, Installation, Testing and Commissioning of refnet joints to be provided in refrigerant pipe line. Maretial of construction for fittings shall be similar to refrigerant piping.At Gandhi Hospital
| V.P 12 AB No 010 |  |  |  | Total | 11
| V.P 12 AB No 010 |  |  |  | Ag | 10 | 10 | 5572 | Nos | 55720 |  |  | 10 | 55720 | 0 | 0 |  |  | 6191
| V.P 12 AB No 010 |  |  |  | AE | 1 | 1 | 5572 | Nos | 5572 |  |  | 0 | 0 | 1 | 5572
Electrical -2
137 | SITC of IVF Center Main Panel Indoor IP-42 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with /without detachable extension type structure with all type of suitable switching accessories & bus-bar as per load requirement of respective IVF equipment’s. (Which is including Lighting, power DBs & UPS)
| V.P 13 AB No 010 |  |  |  | Total | 1 | 1 | 355000 | Nos | 355000 |  |  | 1 | 355000 | 0 | 0 |  |  | 355000
138 | SITC of IVF center AC Panel outdoor IP-54 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with / without detachable extension type structure with all type of suitable switching accessories & bus-bar as per load requirement of respective AC equipment’s. (Which is including 1nos AHU’s stater with VFD by pass, Heater, ODU & VRF system)
| V.P 13 AB No 010 |  |  |  | Total | 1 | 1 | 270000 | Nos | 270000 |  |  | 1 | 270000 | 0 | 0 |  |  | 270000
139 | Supply & installation of AHUs stater on/off push button station for Remote control for inside IVF center with control wiring from AC panel to on /off push button station with necessary items.
| V.P 13 AB No 010 |  |  |  | Total | 3 | 3 | 1540 | Nos | 4620 |  |  | 3 | 4620 | 0 | 0 |  |  | 1540
136 | Supply, Laying & testing of 4Cx4 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
| V.P 13 AB No 010 |  |  |  | Total | 125
[5 empty] | Ag | 80 | 80 | 356 | Rmt | 28480 |  |  | 80 | 28480 | 0 | 0 |  |  | 356
[5 empty] | AE | 45 | 45 | 356 | Rmt | 16020 |  |  | 0 | 0 | 45 | 16020
135 | Supply, Laying & testing of 4Cx6 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
| V.P 14 AB No 010 |  |  |  | Total | 53 | 53 | 484 | Rmt | 25652 |  |  | 53 | 25652 | 0 | 0 |  |  | 484
134 | Supply, Lying & testing of 4Cx16 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 (Part - I) with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt & washer etc. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex Make of gland & Lungs: HMI/Commet/Dowell’s
| V.P 14 AB No 010 |  |  |  | Total | 60 | 60 | 1483 | Rmt | 88980 |  |  | 60 | 88980 | 0 | 0 |  |  | 1483
130 | Supply & installation of 25x3 Copper flat for Neutral earthing of UPS & Equipment which is laid in 100mm cable tray
| V.P 14 AB No 010 |  |  |  | Total | 65.3 | 65.3 | 902 | Rmt | 58900.6 |  |  | 65.3 | 58900.6 | 0 | 0 |  |  | 902
129 | Supply & installation of 25x3 GI flat for body earthing of DBs & Cable tray which is laid in 100mm cable tray
| V.P 14 AB No 010 |  |  |  | Total | 52.4 | 52.4 | 163 | Rmt | 8541.2 |  |  | 52.4 | 8541.2 | 0 | 0 |  |  | 163
127 | Providing and Fixing maintenance free earthing which consists of copper. Earth station, with 600X600X3.15mm Copper Plate at 2500mm Depth including construction of brick pedestal, providing meshed funnel, GI cover and other civil Engineering works, spreading a homogenous mixture of salt, charcoal around the pipe etc., completely as per IS 3043, 1987 or latest revision. Earthing testing should be done as per IE Rules like Earth valve test Etc.
| V.P 14 AB No 010 |  |  |  | Total | 2 | 2 | 22283 | Nos | 44566 |  |  | 2 | 44566 | 0 | 0 |  |  | 22283
126 | Providing and Fixing maintenance free earthing which consists of G.I. Earth station, with 600X600X3.15mm GI Plate at 2500mm Depth including construction of brick pedestal, providing meshed funnel, GI cover and other civil Engineering works, spreading a homogenous mixture of salt, charcoal around the pipe etc., completely as per IS 3043, 1987 or latest revision. Earthing testing should be done as per IE Rules like Earth valve test Etc.
| V.P 14 AB No 010 |  |  |  | Total | 2 | 2 | 8500 | Nos | 17000 |  |  | 2 | 17000 | 0 | 0 |  |  | 8500
121 | SITC of Hot dip galvanized perforated cable tray of 100 mm Wide sizes for to run the cable from DBs to SBs & sockets and AC panel to Units units. All necessary supports & accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. ( Elec 4.10.1 d)
| V.P 15 AB No 010 |  |  |  | Total | 36.2 | 36.2 | 429 | Rmt | 15529.8 |  |  | 36.2 | 15529.8 | 0 | 0 |  |  | 429
120 | Supply & installation of 225mm Light duty exhaust fan with metal blades etc complete Makes: Havells Ventilair-DB
| V.P 15 AB No 010 |  |  |  | Total | 4 | 4 | 2203 | Nos | 8812 |  |  | 4 | 8812 | 0 | 0 |  |  | 2203
112 | Providing and fixing of 125A 25KA TPN Thermal Magnetic Release Based MCCB & Terminal Spreaders in Existing panel board with 1 No. and 1 Set of Indication Lamps, LED type, R,Y,B and breaker 'ON' , 'OFF', 'TRIP' & spring charged lamps. and replace with above Mentioned with required Drilling Holes, removing & Making Busbar connections etc, as required. Makes: Legrand / Schneider/ABB/L&T/C&S
| V.P 15 AB No 010 |  |  |  | Total | 1 | 1 | 28883 | Nos | 28883 |  |  | 1 | 28883 | 0 | 0 |  |  | 28883
108 | Supply and fixing of DP Metal Enclosure with IP 20 Protection DB Make with 1 No 20A, 10 KA DP MCB Make: Legrand / Schneider including internal connection and labour charges for Flush Mounting etc., complete. Makes: Legrand
| V.P 15 AB No 010 |  |  |  | Total | 1 | 1 | 2562 | Nos | 2562 |  |  | 1 | 2562 | 0 | 0 |  |  | 2562
sup | Supply and Transportation 56W Clean room Light fixture, 2' x2' (600mm x600mm) LED luminaire CRCA powder coated white after phosphocreatine treatment provided as standard. with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% etc., complete. MAKE: OSRAM / Wipro / Crompton / Bajaj / Havells
| V.P 16 AB No 010 |  |  |  | Total | 12 | 12
sup | Supply and Transportation of 48" ( 1200 mm) High Speed Fan Sweep Celing Fan with all accessories etc., complete. Make Havells S S 390
| V.P 16 AB No 010 |  |  |  | Total | 14 | 14
sup | Labour Charges for fixing of 48" Celing fan
| V.P 16 AB No 010 |  |  |  | Total | 14 | 14
sup | Supply and fixing of Anchor Fastner
| V.P 16 AB No 010 |  |  |  | Total | 14 | 14
sup | Supply & fixing of 2nos6A, 2 in one socket - 2 Nos with 6A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benz Plus
| V.P 17 AB No 010 |  |  |  | Total | 30 | 30
sup | Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete
| V.P 17 AB No 010 |  |  |  | Total | 14 | 14
sup | Supply and fixing of 15" Heavy Duty Exfan Make Almonard
| V.P 17 AB No 010 |  |  |  | Total | 1 | 1
Sup | Supply and fixing of 63 Amps 4 pole MCB in metal enclouser
| V.P 17 AB No 010 |  |  |  | Total | 1 | 1
Civil -2
56 | Plastering 20mm thick in two coats using screened sand with base coat of 8mm thick in CM (1:6) and top coat of 4mm thick in CM (1:4) with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales & other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and overheads & contractors profit complete for finished item of work. (SS 901,903 & 904).
| V.P 18 MB No 010 |  |  |  | Total | 11.04 | 11.04 | 969 | Sqm | 10697.76 |  |  | 11.04 | 10697.76 | 0 | 0 |  |  | 1077
77 | Supplying and fixing of SWR PVC pipes (Prince/Sudhakar/Kisan/Supreme or any ISI brand) 4 Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, overheads & contractors profit complete for finished item of work at all floor levels. (APSS No. 1302 1319 & 1326)
| V.P 18 MB No 010 |  |  |  | Total | 26.63 | 26.63 | 400 | Rmt | 10652 |  |  | 26.63 | 10652 | 0 | 0 |  |  | 444
75 | Supply and fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings SDR 13.5 to meet the requirement of ASTM-D 2846 and are produced in CTS (Copper Tube Sizes 1/2" to 2") for hot and cold water (IS 15778:2007) including cost and conveyance of all materials to site, labour charges for fixing, overheads & contractors profit complete for finished item of work at all floor levels.
| V.P 18 MB No 010 |  |  |  | Total | 105.4
| V.P 18 MB No 010 |  |  |  | Ag | 75 | 75 | 206 | Rmt | 15450 |  |  | 75 | 15450 | 0 | 0 |  |  | 229
| V.P 18 MB No 010 |  |  |  | AE | 30.4 | 30.4 | 206 | Rmt | 6262.4 |  |  | 0 | 0 | 30.4 | 6262.4
81 | Supply, installation and commissioning approved make floor mounted Anglo Indian wash down EWC conforming to IS: 2556 part8-2004 suit with P or S trap with dual flush porcelain cistren fixed on wash down EWC with all intenal parts of dual flush cistren. ultra solid seat cover of approved make with rubber buffer and cap and 15mm angle stop cock and 450mm long PVC iner connection pipe wall flanges all of approved make etc. Complete for finished item of work
| V.P 18 MB No 010 |  |  |  | Total | 4 | 4 | 6831 | Nos | 27324 |  |  | 4 | 27324 | 0 | 0 |  |  | 7590
80 | Supplying and fixing Indian make Flat Back Wash Hand Basin 1st quality conforming to IS:2556-Part-4:1972 of size 550mm x 400mm with 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963-1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make heavy duty complete with standard CI brackets including wooden blocks ,1 No.12.70mm PVC connection with brass union nuts CP coated , angle stop cock 12.70mm dia. first quality Indian make heavy duty, 30mm dia. PVC flexible waste pipe 914.4mm length of 1st quality including cost and conveyance of all materials to site, labour charges , overheads & contractors profit for finished item of work.
| V.P 18 MB No 010 |  |  |  | Total | 4 | 4 | 3420 | Nos | 13680 |  |  | 4 | 13680 | 0 | 0 |  |  | 3800
83 | Supplying and fixing CP finish brass soap dish of approved make ISI quality including cost and conveyance of all materials, labour charges for fixing, overheads & contractors profit for finished item of work
| V.P 18 MB No 010 |  |  |  | Total | 4 | 4 | 785 | Nos | 3140 |  |  | 4 | 3140 | 0 | 0 |  |  | 872
84 | Supplying and fixing TV shape mirror with plastic frame of size 609.6mm x 457.2mm , plywood back with NP screws 1st quality including cost and conveyance of all materials, labour charges , overheads & contractors profit for finished item of work
| V.P 19 MB No 010 |  |  |  | Total | 4 | 4 | 654 | Nos | 2616 |  |  | 4 | 2616 | 0 | 0 |  |  | 727
85 | Supplying and fixing of CP finish steel towel rods 600mm long and 20mm dia with brackets and aluminium screws including cost and conveyance of all materials, labour charges , overheads & contractors profit for finished item of work.
| V.P 19 MB No 010 |  |  |  | Total | 4 | 4 | 785 | Nos | 3140 |  |  | 4 | 3140 | 0 | 0 |  |  | 872
86 | Supplying and fixing 15 mm Steel body CP finish self closing tap push type conforming to IS 1711 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, overheads & contractors profit complete for finished item of work in all floors.
| V.P 19 MB No 010 |  |  |  | Total | 4 | 4 | 376 | Nos | 1504 |  |  | 4 | 1504 | 0 | 0 |  |  | 418
82 | Supplying and fixing Chromium plated finish brass body quarter turn Bibcock cum Health Faucet with 1m long tube and wall hook with necessary fittings etc., complete including cost and conveyance of all materials, labour charges, complete for finished item of work in all floors. at Gandhi Hospital
| V.P 19 MB No 010 |  |  |  | Total | 4 | 4 | 4122 | Nos | 16488 |  |  | 4 | 16488 | 0 | 0 |  |  | 4580
73 | Supplying and fixing 15 mm brass body CP finish bib tap of not less than 300 grams weight screw type full turn with internal/external threaded connection conforming to IS 8931 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, overheads and contractors profit complete for finished item of work in all floors. at Gandhi Hospital
| V.P 19 MB No 010 |  |  |  | Total | 1 | 1 | 793 | Nos | 793 |  |  | 1 | 793 | 0 | 0 |  |  | 881
79 | Supply and fixing of 4 inches 101.6mm multi floor trap with jali -UPVC/SWR pipe fittings as per site requirements with standard practice for all floor including cost and conveyance of all materials to site ,labour charges ,etc,. Complete for finshed item of work at handhi hospital
| V.P 19 MB No 010 |  |  |  | Total | 5 | 5 | 198 | Nos | 990 |  |  | 5 | 990 | 0 | 0 |  |  | 220
58 | Supply and Installation change room Cubicles at Gandhi Hospital GENERAL SPECIFICATIONS: Thickness of compact Laminate:12mm Thick Colour OF HPL Boards,In Single Colour,Size of Cubicle As per DWG, Door Size For Normal Cubicles AS per DWG Overall Height of Cubicle,2105mm Including bottom gap of 100mm,Accessories , Manufacturers standard makes of aluminium , SS Accessories .a Aluminium H Top Rail b. SS Hinges c. SS privacy Thumb turn occupancy indicator d.SS coat hook e. SS Door knob f. Aluminium U Channel g.Aluminium Door Stopper Channel h. Runner lining i.SS Screw And PVC Wall Plugs
| V.P 19 MB No 010 |  |  |  | Total | 16.83 | 16.83 | 8150 | Sqm | 137164.5 |  |  | 16.83 | 137164.5 | 0 | 0 |  |  | 9055
69 | Providing and applying Wall putty of White Cement or Polymer or Cement based of average 1 to 2 mm thickness over plastered surface to prepare the surface even and smooth after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, applying emery paper, Sand the surface, clean & wipe off loose dust, applying knifing paste filler by putty knife / muslin pad, air dry for 2 - 3 hrs, sand with 180 and 320 No., emery paper for the surface preparation including cost and conveyance of all materials to work site and all operational, incidental, labour charges, over heads and contractors profit etc., complete for finished item of work in all floors for Internal walls.
| V.P 20 MB No 010 |  |  |  | Total | 1007.4 | 1007.4 | 284 | Sqm | 286101.6 |  |  | 1007.4 | 286101.6 | 0 | 0 |  |  | 315
71 | Supply and application of one coat water based cement primer of interior grade I and two coats of water based PU paint having anti-bacterial applications content less than 50 grams/litre for internal walls including cost and conveyance of all materials to site, sales and other taxes, incidental, operational and all labour charges etc., and complete for finished item of work in 5th floor. at Gandhi Hospital
| V.P 20 MB No 010 |  |  |  | Total | 872.13 | 872.13 | 234 | Sqm | 204078.42 |  |  | 872.13 | 204078.42 | 0 | 0 |  |  | 260
67 | Providing and fixing in true horizontal level 14 mm - Mineral Fiber sheet 595 x 595 Square / Tegular Fissura fine model edge tiles with a Humidity Resistance of 90percentage RH, Average NRC 0.50, Light Reflectance greater than80percentage, Thermal Conductivity equal to 0.052 to 0.057 w/mk, Fire Performance Class 0/Class 1 using hot dipped Galvanized Steel section exposed surface with pre-coated capping, main Tee of size 24 x 32 mm at every 1200 mm c/c maximum and rotary stitched cross tee of size 24 x 27 mm at every 600 mm c/c and sub-cross tee of size 24 mm x 25 mm at 1200 mm c/c and wall angle of size 19 x 19 mm fixed to periphery of the wall and the above grid is suspended at every 1200 mm c/c in both directions using 2.0 mm thick pre-straightened GI Wire including cost and conveyance of all materials and labour charges such as cutting , fixing of standing of frame work exposing roof making etc., complete for finished item of work in 5th floor. at Gandhi Hospital
| V.P 20 MB No 010 |  |  |  | Total | 316.08 | 316.08 | 1472 | Sqm | 465269.76 |  |  | 316.08 | 465269.76 | 0 | 0 |  |  | 1636
93 | Providing Laying of scratch proof PVC/vinyl flooring of 2mm thickness with proper welded joints air tight along with leveling compound to match the existing flooring levels as per the engineer in charge instructions. Sub floor preparation with self leveling compound. After the sub floor preparation, it should be suitable for ESD Flooring.Rate inclusive of sifting of material and labour charges.at Gandhi Hospital
| V.P 20 MB No 010 |  |  |  | Total | 124.84 | 124.84 | 3663 | Sqm | 457288.92 |  |  | 124.84 | 457288.92 | 0 | 0 |  |  | 4070
160 | SITC of Factory fabricated and boxed ducting using Aluminium Sheets / coils, should be fabricated as per SMACNA, galvanised hardware and supports, silicon sealant at all longitudinal joints, Galvanized /GI Electroplated iron angle flanges for all the joints, bracing angles and minimum 5mm thick neoprene rubber gasket.- Duct pressure testing at 75mm to be carried oubefore insulatiting the duct. pressure testing to be done as per SMACNA. Procedure to be approved by consultant. 22G - 0.8 mm Thick at Gandhi Hospital
| V.P 20 MB No 010 |  |  |  | Total | 230.24 | 230.24 | 2093 | Sqm | 481892.32 |  |  | 230.24 | 481892.32 | 0 | 0 |  |  | 2325
156 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Suction Line at Gandhi Hospital
| V.P 21 MB No 010 |  |  |  | Total | 12 | 12 | 1071 | Rmt | 12852 |  |  | 12 | 12852 | 0 | 0 |  |  | 1190
155 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Liquid Line at Gandhi Hospital
| V.P 21 MB No 010 |  |  |  | Total | 10 | 10 | 918 | Rmt | 9180 |  |  | 10 | 9180 | 0 | 0 |  |  | 1020
158 | SITC of CPVC drain ping with supports, clamps and 9 mm thk. Nitrile rubber tube insulation of the following sizes. Insulation shall have factory laminated glass cloth. 25mm Dia at Gandhi Hospital
| V.P 21 MB No 010 |  |  |  | Total | 12 | 12 | 464 | Rmt | 5568 |  |  | 12 | 5568 | 0 | 0 |  |  | 515
161 | Aluminium low leakage aerofoil design volume control dampers Suitable for manual and motorised operation At Gandhi Hospital
| V.P 21 MB No 010 |  |  |  | Total | 1.24 | 1.24 | 14220 | Sqm | 17632.8 |  |  | 1.24 | 17632.8 | 0 | 0 |  |  | 15800
162 | CBRI approved 16G GI Spring return actuated fire dampers rated for 90 minutes with limit switch. At Gandhi Hospital
| V.P 21 MB No 010 |  |  |  | Total | 0.84 | 0.84 | 23310 | Sqm | 19580.4 |  |  | 0.84 | 19580.4 | 0 | 0 |  |  | 25900
163 | SITC of SS perforated return raiser grilles with 10 microns filters with collar dampers At Gandhi Hospital
| V.P 21 MB No 010 |  |  |  | Total | 3.29
[5 empty] | Ag | 2 | 2 | 23670 | Sqm | 47340 |  |  | 2 | 47340 | 0 | 0 |  |  | 26300
[5 empty] | AE | 1.29 | 1.29 | 23670 | Sqm | 30534.3 |  |  | 0 | 0 | 1.29 | 30534.3
164 | Extruded Al. powder coated EXHAUST / RETURN discrete grilles At Gandhi Hospital
| V.P 22 MB No 010 |  |  |  | Total | 1.25
| V.P 22 MB No 010 |  |  |  | Ag | 1 | 1 | 7313 | Sqm | 7313 |  |  | 1 | 7313 |  |  |  |  | 8125
| V.P 22 MB No 010 |  |  |  | AE | 0.25 | 0.25 | 7313 | Sqm | 1828.25 |  |  | 0 | 0 | 0.25 | 1828.25
165 | SITC of Collar Dampers made of Al. extrusions with black powder coating for Grilles / Diffusers At Gandhi Hospital
| V.P 22 MB No 010 |  |  |  | Total | 0.72 | 0.72 | 6750 | Sqm | 4860 |  |  | 0.72 | 4860 | 0 | 0 |  |  | 7550
168 | SITC of Aluminium powder coated Fresh air and Exhaust Louvers of nonvision type with nylon mosquito net etc. At Gandhi Hospital
| V.P 22 MB No 010 |  |  |  | Total | 0.12 | 0.12 | 9270 | Sqm | 1112.4 |  |  | 0.12 | 1112.4 | 0 | 0 |  |  | 10300
169 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 32mm Thick for Exposed Supply Air duct and finished with UV Protective Paint. at Gandhi Hospital
| V.P 22 MB No 010 |  |  |  | Total | 119.84 | 119.84 | 1103 | Sqm | 132183.52 |  |  | 119.84 | 132183.52 | 0 | 0 |  |  | 1225
170 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Exposed Return Air Duct and finished with UV Protective Paint. at Gandhi Hospital
| V.P 22 MB No 010 |  |  |  | Total | 84.41 | 84.41 | 968 | sqm | 81708.88 |  |  | 84.41 | 81708.88 | 0 | 0 |  |  | 1075
171 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Supply air duct running inside the building. at Gandhi Hospital
| V.P 22 MB No 010 |  |  |  | Total | 75.04
| V.P 22 MB No 010 |  |  |  | Ag | 40 | 40 | 707 | Sqm | 28280 |  |  | 40 | 28280 | 0 | 0 |  |  | 785
| V.P 22 MB No 010 |  |  |  | AE | 35.04 | 35.04 | 707 | Sqm | 24773.28 |  |  | 0 | 0 | 35.04 | 24773.28
172 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 19mm Thick for Return air running inside the building. at Gandhi Hospital
| V.P 22 MB No 010 |  |  |  | Total | 19.24 | 19.24 | 594 | Sqm | 11428.56 |  |  | 19.24 | 11428.56 | 0 | 0 |  |  | 660
87 | Supply and instalaion of Wall Panels 80mm thick double skin Modular wall panels made of .8mm Powder Coated GI on both sides, with 40 plus or minus 2 kg/cum demsity pUF as infill, GI profiles all along the periphery,flush on both sides with maximum allowable gap of 3-4mm filled with food grade silicon sealent and placed on cold rolled galvanised bottom tracks with a recess to provide floor to wall coving flush with the wall panel. This including all required hardware for completion panels to be covered with a protective film to avoid any damages during transpotation and installation at Gandhi Hispital
| V.P 23 MB No 010 |  |  |  | Total | 96.75 | 96.75 | 5058 | Sqm | 489361.5 |  |  | 96.75 | 489361.5 | 0 | 0 |  |  | 5620
88 | Supply and installtion of 50mm thick double skin cealing system made .8mm thich powder coated GI sheet on both sides, 40 plus or minus 2kg/cum density PUF ad infill, GI Profiles all along the periphery, panels flush towards room sides with maximum allowable gap of 3-4mm at panelto panel joints filled with silicon sealent ceiling panels are suspended from the RCC salb bu using concealed Aall ceiling grid with tie rod and adjestable turn bickle arrangement etc. This includes all required hardware for completition. panels to be covered with a protective film to avoid any damge during transpotation and installation at Gandhi Hospital.
| V.P 23 MB No 010 |  |  |  | Total | 48.02 | 48.02 | 4622 | Sqm | 221948.44 |  |  | 48.02 | 221948.44 | 0 | 0 |  |  | 5135
92 | Supply and installation of Extruded Aluminium Coving at Gndhi Hopital
| V.P 23 MB No 010 |  |  |  | Total | 63.61 | 63.61 | 527 | Rmt | 33522.47 |  |  | 63.61 | 33522.47 | 0 | 0 |  |  | 585
90 | Single leaf clean room door 46mm thick flush made of .8mm thick powedr coated GI sheet on both sides 90 pus or minus 2kg/cum density honeycomb with stand upto 220 deg.C temperature ,and compressible strength upto 400 kg/sqm,1.2mm thick GPSP door frames ,double glazed vision panel with necessary adhesive tapes and silicon swalent, necessary hardware like SS304 ball bearing butt hinges D- hnadles,push plates ,Dorma make door closer concealed tower bolt ,drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms,BOth sides lock and key etc,. Complete .
| V.P 23 MB No 010 |  |  |  | Total | 3
[5 empty] | Ag | 1 | 1 | 25830 | Nos | 25830 |  |  | 1 | 25830 | 0 | 0 |  |  | 28700
[5 empty] | AE | 2 | 2 | 25830 | Nos | 51660 |  |  | 0 | 0 | 2 | 51660
89 | Double leaf clean room door 46mm thick flush made of .8mm thick powedr coated GI sheet on both sides 90 pus or minus 2kg/cum density honeycomb with stand upto 220 deg.C temperature ,and compressible strength upto 400 kg/sqm,1.2mm thick GPSP door frames ,double glazed vision panel with necessary adhesive tapes and silicon swalent, necessary hardware like SS304 ball bearing butt hinges D- hnadles,push plates ,Dorma make door closer concealed tower bolt ,drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms,BOth sides lock and key etc,. Complete .
| V.P 23 MB No 010 |  |  |  | Total | 5 | 5 | 41400 | Nos | 207000 |  |  | 5 | 207000 | 0 | 0 |  |  | 46000
91 | Emergency Fire door 46mm thick flush made of .8mm thick powedr coated GI sheet on both sides 90 pus or minus 2kg/cum density honeycomb with stand upto 220 deg.C temperature ,and compressible strength upto 400 kg/sqm,1.2mm thick GPSP door frames ,double glazed vision panel with necessary adhesive tapes and silicon swalent, necessary hardware like SS304 ball bearing butt hinges D- hnadles,push plates ,Dorma make door closer concealed tower bolt ,drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms,BOth sides lock and key etc,. Complete .
| V.P 24 MB No 010 |  |  |  | Total | 1 | 1 | 49500 | Nos | 49500 |  |  | 1 | 49500 | 0 | 0 |  |  | 55000
61 | Supplying and fixing of Unplasticised Poly Vinyl Chloride UPVC 3 track sliding windows with mesh shutter – 2-glass shutters and 1-mesh shutter duly manufactured using UPVC reinforced profiles Composition of profile shall consists a minimum of 5.5 PHR of TiO2 and not more than 12 PHR of CaCo3 for every 100 parts of PVC resin of 94mm x 45 mm/80 mm x 52 mm x 2.20 mm for outer frames, 58 mm x 39 mm/54 mm x 38 mm x 2.20mm for sliding shutter frames capable of mounting single glazing system structurally reinforced with hot dip galvanized up to 50 microns of minimum thickness of 1.0/1.2 mm prefabricated and welded through fusion welding. The window sash shall be fitted with 5 mm thick clear float glass of reputed make and mesh shutter frame shall be 42 mm x 25mm/52 mm x 21.5 mm x 2.0 mm fitted with Vinyl Coated Fiber mesh- on rollers/ pulley duly fixed with Grey colour TPV Gasket for sash and Glazing bead shall be co extruded with Grey colour soft PVC. System shall have single point locking with Touch Lock and the system is to be installed at the site using anchor fasteners, silicon rubber sealant, easy glazing/deglazing at site etc., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site includingetc., complete for finished item of work. at Gandhi Hospital
| V.P 24 MB No 010 |  |  |  | Total | 7.88 | 7.88 | 8565 | Sqm | 67492.2 |  |  | 7.88 | 67492.2 | 0 | 0 |  |  | 9517
62 | Providing, supplying and fixing of Fixed Louvered Ventilator made out of multi chambered uPVC sections with Glazing bead shall be co-extruded with Grey colour soft PVC. having isolated drainage and reinforced with Galvanized Iron profiles throughout the window. The outer frame having an overall size of 60 mm x 55 mm x 2.40 with reinforcement of 1 mm thickness and Mullion with overall size of 74 mm x 60 mm x 2.40 mm with reinforcement of 1 mm thickness. Composition of profile shall consists a minimum of 5.5 PHR of TiO2 and not more than 12 PHR of CaCo3 for every 100 parts of PVC resin. Ventilator shall be provided with 4.5 mm Pin Head glass, standard hardware. Wall thickness of frame and Mullion shall be 2.4 mm., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site etc., complete for finished item of work hinges IS:205 150mm long, 1 No. aldrop IS:2681 300mm long, 1 No. tower bolt IS:204 of 200 mm x 10 mm dia at top, 2 Nos. 150 mm at Gandhi Hospital
| V.P 24 MB No 010 |  |  |  | Total | 1.53 | 1.53 | 7708 | Sqm | 11793.24 |  |  | 1.53 | 11793.24 | 0 | 0 |  |  | 8564
182 | SITC of Oxygen Manifold Emergency for 1 plus 1 Cylinders, as per technical specifications. At Gandhi Hospital
| V.P 24 MB No 010 |  |  |  | Total | 1 | 1 | 18675 | Set | 18675 |  |  | 1 | 18675 | 0 | 0 |  |  | 20750
183 | SITC of Oxygen Outlets with matching probes, as per HTM-2022/02-01 of UK/NFPA99C of USA as per enclosed technical specifications - Imported At Gandhi Hospital
| V.P 24 MB No 010 |  |  |  | Total | 6
| V.P 24 MB No 010 |  |  |  | Ag | 4 | 4 | 2255 | Nos | 9020 |  |  | 4 | 9020 | 0 | 0 |  |  | 2506
| V.P 24 MB No 010 |  |  |  | AE | 2 | 2 | 2255 | Nos | 4510 |  |  | 0 | 0 | 2 | 4510
184 | SITC of Oxygen Flow meter with Humidifier, CE Certified with four digit number as per enclosed technical specifications - Imported At Gandhi Hospital
| V.P 25 MB No 010 |  |  |  | Total | 6
| V.P 25 MB No 010 |  |  |  | Ag | 4 | 4 | 1625 | Nos | 6500 |  |  | 4 | 6500 | 0 | 0 |  |  | 1805
| V.P 25 MB No 010 |  |  |  | AE | 2 | 2 | 1625 | Nos | 3250 |  |  | 0 | 0 | 2 | 3250
185 | SITC of Nitrous Oxide Manifold Emergency for 1 Cylinder, with high pressure Regulator, NRV, tailpipes etc. as per technical specifications At Gandhi Hospital
| V.P 25 MB No 010 |  |  |  | Total | 1 | 1 | 11925 | Set | 11925 |  |  | 1 | 11925 | 0 | 0 |  |  | 13250
186 | SITC of N20 Outlets with matching probes, as per HTM-2022/02-01 of UK/NFPA99C of USA as per enclosed technical specifications - Imported At Gandhi Hospital
| V.P 25 MB No 010 |  |  |  | Total | 4 | 4 | 2255 | Nos | 9020 |  |  | 4 | 9020 | 0 | 0 |  |  | 2506
187 | SITC of C02 Manifold for 2 Cylinders, with high pressure Regulator, NRV, tailpipes etc. as per technical specifications At Gandhi Hospital
| V.P 25 MB No 010 |  |  |  | Total | 1 | 1 | 18675 | Set | 18675 |  |  | 1 | 18675 | 0 | 0 |  |  | 20750
188 | SITC of C02 Outlets with matching probes, as per HTM-2022102-01ofUK/NFPA99C of USA as per enclosed technical specifications - Imported At Gandhi Hospital
| V.P 25 MB No 010 |  |  |  | Total | 6
| V.P 25 MB No 010 |  |  |  | Ag | 4 | 4 | 2255 | Nos | 9020 |  |  | 4 | 9020 | 0 | 0 |  |  | 2506
| V.P 25 MB No 010 |  |  |  | AE | 2 | 2 | 2255 | Nos | 4510 |  |  | 0 | 0 | 2 | 4510
189 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 12mm COPPER PIPE at Gandhi Hospital
| V.P 25 MB No 010 |  |  |  | Total | 38.3
| V.P 25 MB No 010 |  |  |  | Ag | 24 | 24 | 578 | Rmt | 13872 |  |  | 24 | 13872 | 0 | 0 |  |  | 642
| V.P 25 MB No 010 |  |  |  | AE | 14.3 | 14.3 | 578 | Rmt | 8265.4 |  |  | 0 | 0 | 14.3 | 8265.4
190 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 15mm COPPER PIPE at Gandhi Hospital
| V.P 25 MB No 010 |  |  |  | Total | 157.7
| V.P 25 MB No 010 |  |  |  | Ag | 114 | 114 | 742 | Rmt | 84588 |  |  | 114 | 84588 | 0 | 0 |  |  | 824
| V.P 25 MB No 010 |  |  |  | AE | 43.7 | 43.7 | 742 | Rmt | 32425.4 |  |  | 0 | 0 | 43.7 | 32425.4
191 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 22mm COPPER PIPE at Gandhi Hospital
| V.P 25 MB No 010 |  |  |  | Total | 79.5
| V.P 25 MB No 010 |  |  |  | Ag | 36 | 36 | 1072 | Rmt | 38592 |  |  | 36 | 38592 | 0 | 0 |  |  | 1191
| V.P 25 MB No 010 |  |  |  | AE | 43.5 | 43.5 | 1072 | Rmt | 46632 |  |  | 0 | 0 | 43.5 | 46632
192 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 28mm COPPER PIPE at Gandhi Hospital
| V.P 26 MB No 010 |  |  |  | Total | 27
[5 empty] | Ag | 18 | 18 | 1326 | Rmt | 23868 |  |  | 18 | 23868 | 0 | 0 |  |  | 1473
[5 empty] | AE | 9 | 9 | 1326 | Rmt | 11934 |  |  | 0 | 0 | 9 | 11934
193 | SITC of Touch type LCD Area Alarm and Zonal Valve box- as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications imported for 3 gases at Gandhi Hospital
| V.P 26 MB No 010 |  |  |  | Total | 1 | 1 | 247500 | Nos | 247500 |  |  | 1 | 247500 | 0 | 0 |  |  | 275000
194 | SITC of Touch type LCD Area Alarm and Zonal Valve box- as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications imported for Master Main Alarm including all Gases at Gandhi Hospital
| V.P 26 MB No 010 |  |  |  | Total | 1 | 1 | 337500 | Nos | 337500 |  |  | 1 | 337500 | 0 | 0 |  |  | 375000
195 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 15mm 0D at Gandhi Hospital
| V.P 26 MB No 010 |  |  |  | Total | 8
[5 empty] | Ag | 3 | 3 | 1744 | Nos | 5232 |  |  | 3 | 5232 | 0 | 0 |  |  | 1938
[5 empty] | AE | 5 | 5 | 1744 | Nos | 8720 |  |  | 0 | 0 | 5 | 8720
196 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 22mm 0D at Gandhi Hospital
| V.P 26 MB No 010 |  |  |  | Total | 3 | 3 | 2466 | Nos | 7398 |  |  | 3 | 7398 | 0 | 0 |  |  | 2740
197 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 28mm 0D at Gandhi Hospital
| V.P 26 MB No 010 |  |  |  | Total | 4 | 4 | 3940 | Nos | 15760 |  |  | 4 | 15760 | 0 | 0 |  |  | 4378
198 | SITC of Bed Head Panel - as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications at Gandhi Hospital
| V.P 26 MB No 010 |  |  |  | Total | 2 | 2 | 33075 | Nos | 66150 |  |  | 2 | 66150 | 0 | 0 |  |  | 36750
[7 empty] | Grand Total |  |  | 38743335.96 |  |  |  | 36460334.93 |  | 2283001.03
[7 empty] | Add GST @ 18% |  |  | 6973800 |  |  |  | 6562860 |  | 410940
[7 empty] | Grand Total |  |  | 45717135.96 |  |  |  | 43023195 |  | 2693941.03
Seignoirage Charges
Certificate
|  | Qty | Sand | Metal | Brick
1 | Brick work | 6.24 |  |  | 540 |  | 1 | The work is in progress in according with the specification drawing and terms and condition the agreement.
5 | Plastering 12mm | 11.04 | 1.14 |  |  |  | 2 | No recoveries are due for recovery from the contractor other than those propsed in the bill
|  |  | 1.14 | 0 | 540 |  | 3 | There are no further dues to be recovery from the contractor
|  |  | @ | @ | @ |  | 4 | The contractor has conveyneced the materieals for use on the work as per the lead statement approved the agreement.
|  |  | 44 | 75 | 60/1000 |  | 5 | The leads and lifts are cveried in the contractor.
|  |  | 50 | 0 | 32 |  |  | Sumited to the Exective Engineer TSMSIDC Raga Reddy Division for favor of pri audit and payment
| Total:- | 82
| Previous | 11134
| Grand Total | 11216
| Net | 82