## Inventory
Sl.no | Room Name | Light Point | CPP | Dimmer | 2No 16A Switch & Socket | 1No 16A Switch & Socket | 36W 2'x2' Ceiling Light | 24W Down Light Fitting | 52W Clean Room Fitting | 48" Ceiling Fan | 9" Exhaust fan | 2No 6A Switch & Socket | 1No 6A,2No 6A | 3no 16a switch and sockets
1 | Waiting Room | 5 | 1 |  |  |  | 3 |  |  | 1
2 | Reception | 8 | 1 | 2 |  | 2 | 3 |  |  | 2 |  | 2
3 | Passage @ Reception | 3 | 1 |  |  |  | 1
4 | Sr Faculty Room | 6 | 1 | 1 | 1 | 2 | 4 |  |  | 1 |  | 3
5 | Record Room | 6 | 1 | 1 | 2 |  |  | 2 |  | 1
6 | Passage @ Record Room | 6 | [5 empty] | 5
7 | Toilet @ Record Room | 5 | 1 |  |  |  |  | 1 |  |  | 1
8 | Dr.Changing Rooms | 8 | 1 |  | 1 |  |  | 4 |  |  |  | 1
9 | Ultra Sound Room | 6 | 1 | 1 | 2 | 1 |  | 4 |  | 1 |  |  | 1
10 | Counselling Room-1 | 6 |  | 1 |  | 2 | 2 |  |  | 1 |  | 1
11 | Counselling Room-2 | 6 |  | 1 |  | 2 | 2 |  |  | 1 |  | 1
12 | Toilet @ Counseling Room | 3 | 1 |  |  |  |  | 1 |  |  | 1
13 | Passage @ Counselling Room | 3 | 1 |  |  |  |  | 3
14 | Staff Changing Room-1 | 1 | 1 |  | 1 |  |  | 1
15 | Staff Changing Room-2 | 5 | [5 empty] | 1
16 | Patient Changing Room | 6 | 1 | 1 | 1 |  | 2
17 | Toilet @ Patient Changing Room | 3 | 1 |  |  |  |  | 1 |  |  | 1
18 | Non Sterile Corridoor | 6 |  |  |  |  | 4
19 | Sample Collection Room | 6 | 1 | 1 | 2 | 2 | 2 |  |  | 1
20 | Store Room | 6 | 1 | 1 | 1 |  | 2 |  |  | 1
21 | Corridar @ Store Room | 3 | 1 |  |  |  |  | 2
22 | Anesthetist Room | 6 | 1 | 1 | 2 | 1 | 2 |  |  | 1
23 | Embryologist Room | 6 | 1 | 1 | 2 | 1 | 2 |  |  | 1
24 | Toilet @ Embryologist Room | 3 | 1 |  |  |  |  | 1 |  |  | 1
25 | Passage @ Embryologist Room | 3 | 1 |  |  |  |  | 3
26 | Pre Operative ward | 8 | 1 | 2 | 2 |  | 6 |  |  | 2 |  | 1
27 | Post Operative Ward | 8 | 1 | 2 | 5 |  | 5 |  |  | 1
28 | Toilet @ Post Operative Ward | 3 | [5 empty] | 1 |  |  | 1
29 | Autoclave Room | 6 | 1 | 1 | 4 |  | 2 |  |  | 1 | 1
30 | Clean Store | 6 | 1 | 1 |  |  | 2 |  |  | 1
31 | Passage @ Autoclave Room | 3 | 1 |  |  |  |  | 3
32 | Waiting Room & Corridar | 7 |  | 1 | 2 | 1 |  | 3 |  | 1
33 | Semen Collection Room | 6 | 1 | 1 | 3 | 1 | 3 |  |  | 1 |  | 1
34 | Toilet @ Semen Collection Room | 3 | [5 empty] | 1 |  |  | 1
35 | Semi Sterile Corridar | 6 |  |  |  |  | 4
36 | IVF OT | 8 |  |  | 6 |  |  |  | 6
37 | Embryology Lab | 8 |  |  | 6 |  |  |  | 6 |  |  |  |  | 2
38 | Andrology Lab SB-1 | 9 | 2 |  | 4 | 3 | 3
39 | Andrology Lab SB-2 | 6 | 1 | 1 | 1 |  | 2
40 | Cryo Room | 6 | 1 | 1 | 2 | 1 | 2
41 | Major OT | 9 | 1 |  | 7 | 4 | 6
42 | Sterile Corridar | 5 | 1 |  |  |  | 5
43 | Manifold Room | 6 | 1 | 1 | 3 |  | 3 |  |  | 1 |  | 2
44 | Manifold Corridar | 3 | 1 |  |  |  | 2
45 | Electrical Room | 6 |  | 1 |  |  |  | 4 |  | 1
46 | Ups Room | 6 |  | 1 |  |  |  | 4 |  | 1
| Total | 253 | 34 | 25 | 60 | 23 | 74 | 45 | 12 | 22 | 7 | 12 | 1 | 2

## SPS Bill
ABSTRACT
Name of Work:- Design, Fabriction, establishing and commissioning of In - Vitro ferility centers (IVFC) alongwith allied Services on Turnkey basis at MGMH Petlaburj,Hyd. | [7 empty] | Agency: | M/s. Asta Vardhman Consortium
S.No | Date of measurement/ S.No. in Agt. | Description Of Work etc., | Measurements Upto date |  |  |  |  | Rate |  | Per | Total Value to date
|  |  | No | L | B | D | Content | Rs | Ps. |  | Rs. | Ps | BOQ
Electrical-1
1 | 294 | Supply and laying of ISI 25mm outer dia medium grade with IS:9537-part 3 rigid PVC pipe concealed in wall with all required PVC / Metallic Junction Boxes including masonry work and labour charges etc., Makes: Modi . at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 463.5 | 88 |  | Rmt | 40788 |  | 200 | 263.5 | 23188
2 | 294 | Supply and laying of ISI 25mm outer dia medium grade with IS:9537-part 3 rigid PVC pipe surface on wall with all required PVC / Metallic Junction Boxes including masonry work and labour charges etc., Makes: Modi. at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 1352.8 | 82 |  | Rmt | 110929.6 |  | 450 | 902.8 | 74029.6
3 | 295 | Wiring with 2 runs of 22/0.3mm 1.5 Sq.mm FRLS / HFFR P.V.C. insulated flexible copper cable ISI MARK in existing pipe with 6A Modular switch, Ceiling rose/BH/SBH Modular switches with cover plate and GI switch box including all labour charges etc., complete. for Non- Residential Building Makes of wires: Polycab Makes of switches: - /Honeywell Blenge Plus at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB: |  |  |  |  | 253 | 720 |  | Nos | 182160 |  | 100 | 153 | 110160
4 | 300 | Supply and run of 1 of 22 /0.3mm 1.5 Sq.mm FRLS / HFFR P.V.C. insulated flexible copper cable in existing conduit pipe for earth continuity including all labour charges etc., complete. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 379.6 | 30 |  | Rmt | 11388 |  | 350 | 29.6 | 888
5 |  | Supply and fixing of 6A ISI Mark 3/2 pin Modular socket with 6A 1way Modular switch, 3 Module box with cover frame and GI switch box on common switch board with connections etc., complete. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. Makes of switches: - Honeywell Blenge Plus at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 34 | 516 |  | Nos | 17544 |  | 12 | 22 | 11352
Supply and fixing of 16A switches - 1Nos and 6/16A 2 in one socket - 1Nos Modular type with cover plate and GI switch box fixing on separate board including all labour charges etc., complete. Makes of switches: -Honeywell Blenge Plus. at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 23 | 796 |  | Nos | 18308 |  | 40 | -17 | -13532
Supply and fixing of 16A/6A, 2 in one socket - 2 Nos with 16A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: - /Honeywell Blenge Plus. at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 60 | 1342 |  | Nos | 80520 |  | 60 | 0 | 0
5 | 301 | Supply and run of 3 of 2.5 sq.mm 36/0.mm phase neutral and earth FRLS / HFFR PVC insulated flexible copper cable in existing conduit pipe for individual lighting circuits including labour charges etc., complete as required for switch boards. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 1713.1 | 135 |  | Rmt | 231268.5 |  | 600 | 1113.1 | 150268.5
6 | 302 | Supply and 3 runs of 4.0 sq mm 56/0.3 mm phase neutral and earth FRLS / HFFR PVC insulated flexible copper cable in existing conduit pipe including labour charges etc., complete for 16A sockets. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 2421 | 194 |  | Nos | 469674 |  | 1200 | 1221 | 236874
7 | 303 | Supply and run of 5 of 6.0 Sqmm 90/0.3 mm 3 phases, neutral and earth FRLS / HFFR PVC insulated flexible copper cable in the existing conduit pipe for run of mains from Power panel board to TPN DBs with pin type lugs and connections etc., complete. for LDBs Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 240.1 | 464 |  | Rmt | 111406.4 |  | 60 | 180.1 | 83566.4
8 | 304 | Supply and run of 5 of 10.0 Sqmm 140/0.3 mm 3 phases, neutral and earth FRLS / HFFR PVC insulated flexible copper cable in the existing conduit pipe for run of mains from Power panel board to TPN DBs with pin type lugs and connections etc., complete. for PDBs Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 284 | 740 |  | Rmt | 210160 |  | 40 | 244 | 180560
Supply, transportation and fixing of 24W edge lit LED Down light Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser Square with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor greater than 0.9, Surge protection: greater than 2KV, System efficacy of greater than100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI greater than80, and THD is less than 15percentage etc., with BIS Certification. Makes: Phillips / OSRAM / Wipro / Crompton / Bajaj / Havells at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 45 | 2030 |  | Nos | 91350 |  | 50 | -5 | -10150
Supply and Transportation 36W Edge lit, 2 feet x2 feet 600mm x600mm slim panel LED luminaire Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor greater than 0.9, Surge protection greater than 2KV, System efficacy of greater than100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI greater than 80, and THD is less than 15percentage etc., complete. Makes: Phillips / OSRAM / Wipro / Crompton / Bajaj / Havells at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 74 | 3325 |  | Nos | 246050 |  | 30 | 44 | 146300
Supply and fixing of Modular type Stepped electronic regulator Makes : GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/ Cabtree Verna/ Million logus / Gold Medal Curve for sweep AC ceiling fans of 1200mm / 1400mm complete with connections. at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 25 | 633 |  | Nos | 15825 |  | 12 | 13 | 8229
Supply and installation of 225mm Light duty exhaust fan with metal blades etc complete Makes: Crompton / Havells Ventilair-DB/ Orient hill air. at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 7 | 1685 |  | Nos | 11795 |  | 7 | 0 | 0
9 | 306 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand / Schneider and Supply and Fixing of 1 No., of 40A FP 30mA RCCB as incomer and 12 Nos 6-32 A 10kA SP MCBs Makes: Legrand-DX3 / Schneider-Acti9 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. For Lighting DBs at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 10 | 14018 |  | Rmt | 140180 |  | 3 | 7 | 98126
10 | 308 | Supply and fixing of 8 Way VTPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand / Schneider and Supply and Fixing of 1 No., of 100A FP 10KA MCB as incomer and 4 Nos 63 A 10kA TP MCBs, 4 Nos 40 A 10kA TP MCBs Makes: Legrand-DX3 / Schneider-Acti9 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. For UPS MDB DBs at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 1 | 49000 |  | Nos | 49000 |  | 1 | 0 | 0
11 | 309 | Providing and fixing of 125A 25KA TPN Thermal Magnetic Release Based MCCB and Terminal Spreaders in Existing panel board with 1 No. and 1 Set of Indication Lamps, LED type, R,Y,B and breaker ON , OFF, TRIP and spring charged lamps. and replace with above Mentioned with required Drilling Holes, removing and Making Busbar connections etc, as required. Makes: Legrand / Schneider/ABB/LandT/CandS at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 1 | 22000 |  | Nos | 22000 |  | 1 | 0 | 0
12 | 318 | SITC of Hot dip galvanized perforated cable tray of 100 mm Wide sizes for to run the cable from DBs to SBs and sockets and AC panel to Units units. All necessary supports and accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 79 | 328 |  | Rmt | 25912 |  | 70 | 9 | 2952
13 | 319 | SITC of Hot dip galvanized perforated cable tray of 300 mm Wide sizes for to run the cable from Floor Panel to Lab Panel and electrical room to AC panel and AC panel to Units. All necessary supports and accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 102.5 | 1000 |  | Rmt | 102500 |  | 80 | 22.5 | 22500
14 | 325 | Supply and installation of 50x6 GI flat for body earthing of electrical panel and AC Panel which is laid in 300mm cable tray at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 217.3 | 251 |  | Rmt | 54542.3 |  | 200 | 17.3 | 4342.3
15 | 323 | Providing and Fixing maintenance free earthing which consists of G.I. Earth station, with 600X600X3.15mm GI Plate at 2500mm Depth including construction of brick pedestal, providing meshed funnel, GI cover and other civil Engineering works, spreading a homogenous mixture of salt, charcoal around the pipe etc., completely as per IS 3043, 1987 or latest revision. Earthing testing should be done as per IE Rules like Earth valve test Etc. at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 2 | 6500 |  | Nos | 13000 |  | 2 | 0
16 | 324 | Providing and Fixing maintenance free earthing which consists of copper. Earth station, with 600X600X3.15mm Copper Plate at 2500mm Depth including construction of brick pedestal, providing meshed funnel, GI cover and other civil Engineering works, spreading a homogenous mixture of salt, charcoal around the pipe etc., completely as per IS 3043, 1987 or latest revision. Earthing testing should be done as per IE Rules like Earth valve test Etc. at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 4 | 17046 |  | Nos | 68184 |  | 2 | 2 | 34092
17 | 327 | Supply and installation of 25x3 Copper flat for Neutral earthing of UPS and Equipment which is laid in 100mm cable tray at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 207.3 | 690 |  | Rmt | 143037 |  | 200 | 7.3 | 5037
18 | 328 | Supply and installation of 4 sqmm Copper wire for Earthing of DBs Equipment at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 450.6 | 63 |  | Rmt | 28387.8 |  | 80 | 370.6 | 23347.8
19 | 329 | Supply, Laying and testing of 3.5Cx95 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc.. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex. Make of gland and Lungs: HMI/Commet/Dowell’s at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 180 | 923 |  | Rmt | 166140 |  | 120 | 60 | 55380
20 | 330 | Supply, Lying and testing of 3.5CX50 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc.. Make of Cable: Polycab Make of gland and Lungs: HMI at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 180 | 552 |  | Rmt | 99360 |  | 70 | 110 | 60720
21 | 331 | Supply, Lying and testing of 4Cx16 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc.. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex. Make of gland and Lungs: HMI/Commet/Dowell’s at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 155 | 1134 |  | Rmt | 175770 |  | 100 | 55 | 62370
22 | 332 | Supply, Laying and testing of 4Cx6 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc. Make of Cable: Polycab/ KEI/Universal/ Glostar/Finolex. Make of gland and Lungs: HMI/Commet/Dowell’s at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 120 | 370 |  | Rmt | 44400 |  | 120 | 0
23 | 333 | Supply, Lying and testing of 4Cx4 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc. Make of Cable:Polycab/ KEI/Universal/Glostar/Finolex. Make of gland and Lungs: HMI/Commet/Dowell’s at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 80 | 272 |  | Rmt | 21760 |  | 80 | 0
24 | 334 | SITC of IVF Center Main Panel Indoor IP-42 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with /without detachable extension type structure with all type of suitable switching accessories and bus-bar as per load requirement of respective IVF equipment’s. Which is including Lighting, power DBs and UPS at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 1 | 310500 |  | Nos | 310500 |  | 1 | 0
25 | 335 | SITC of IVF center AC Panel outdoor IP-54 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with / without detachable extension type structure with all type of suitable switching accessories and bus-bar as per load requirement of respective AC equipment’s. Which is including 1nos AHU’s stater with VFD by pass, Heater, ODU and VRF system at MGMH Petlaburj
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 1 | 238500 |  | Nos | 238500 |  | 1 | 0
3552339.6
SUPPLEMENTAL ITEMS
1 |  | Supply and Transportation 56W Clean room Light fixture, 2' x2' (600mm x600mm) LED luminaire CRCA powder coated white after phosphocreatine treatment provided as standard. with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% etc., complete. MAKE: Philips
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 12 | 15517 |  | Nos | 186204
2 |  | Supply and Transportation of 48" ( 1200 mm) High Speed Fan Sweep Celing Fan with all accessories etc., complete. Make Havells S S 390
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 22 | 3885 |  | Nos | 85470
3 |  | Labour charges for fixing of ceiling fan and regulator including transportation and giving connections with twin core wire etc., complete. Makes : Finolex / RR Kabel / Havells / Polycab / GM / Million / V-Guard / Gold Medal / HPL / RPG.
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 22 | 167 |  | Nos | 3674
4 |  | Supply and fixing of Anchor fastner with fan hook / Providing MS Fan hook with grouting and cement plastering.
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 22 | 110 |  | Nos | 2420
5 |  | Supply & fixing of 2nos6A, 2 in one socket - 2 Nos with 6A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benz Plus
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 12 | 1060 |  | Nos | 12720
6 |  | Supply,Transportation of 15" (375mm) ISI, 900 RPM Heavy duty exhaust fan with metallic blades wiremesh with all accessories etc complete Makes : Crompton / Almonard / Havells Turbo Force SP.
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 1 | 3918 |  | Nos | 3918
7 |  | Labour charges for fixing the exhaust fan in wall with necessary connections and masonary work of making hole, finishing etc., complete.
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 1 | 709 |  | Nos | 709
8 |  | Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 1 | 146 |  | Nos | 146
9 |  | Supply and fixing of 12 Way SPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand and Supply and Fixing of 1 No., of 63A FP MCB as incomer and 8 Nos 6-32 A 10kA SP MCBs Makes: Legrand-DX3 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. (For UPS DBs)
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 2 | 8450 |  | Nos | 16900
10 |  | Supply and fixing of cable adopteres box with cover for DBs including, massanory work etc., complete.,
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 8 | 4577 |  | Nos | 36616
11 |  | Supply and fixing of FP Metal Enclosure with IP 20 Protection DB Make with 1 No 63A, 10 KA DP MCB including internal connection and labour charges for Flush Mounting etc.,complete. Makes of Enclousure : Legrand MCB Makes : Legrand-DX3
|  | Qty V.Pg.No:- of MB:- |  |  |  |  | 2 | 3783 | Nos |  | 7566
12 |  | Supply and fixing of suitable out door feeder piller box of size made with 14 SWG CRCA sheet with double door arrangement, making powder coating after processing of 7 Tank process, lock and key, hinges, rubber gasket, danger board,suitable angle iron stand for mounting the feeder pillar with cement concrete, including Supply and fixing of Legrand / Schnieder make as out goings, indication lamps, din channel, 6 Sqmm 3 core copper cable for invidual light control, connectors, bus bars, shroudings, gland plates and provision for 3 phase energy meter etc., complete for finished item of work and suitable wiring provision for connecting the nature switch with following.63A, 4 Pole MCB as incomer, 9 Nos 6-32A SP MCBs
[7 empty] | 1 | 27691 | Nos |  | 27691
384034
3936373.6
[9 empty] | GST @ 18% |  | 708547.248
4644920.848

## E-Datas (2)
Electrical Datas 2023-24 (To replace with 2022-23 SSR)
S.No | SSR Item No | Item Code | Description | Qty |  | Unit |  | Rate | Amount
Supply and Transportation 56W Clean room Light fixture, 2' x2' (600mm x600mm) LED luminaire CRCA powder coated white after phosphocreatine treatment provided as standard. with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% etc., complete. MAKE: Philips
a) Labour charges
| 1 |  | Skilled Electrician. | 0.05 | day | 1 | day | 660 | 33
| 3 |  | Helper (Electrical). | 0.125 | day | 1 | day | 550 | 68.75
|  |  | Labour for 1 No | [5 empty] | 101.75
b) Material
| ELEC-1.5.5 |  | Supply of 23 / 0060 twin core twisted / flat heavy Copper wire. | 2 | Mtr | 100 | Mtrs | 1200 | 24
|  |  | Alluminium Flat (As per requirement) | [5 empty] | 50
| As per Price list of Philips | a | Supply and Transportation of 56W Clean room fitting, 2' x 2' (600mm x 600mm) slim panel LED luminaire | 1 | Nos | 1 | Nos | 15000 | 15000
|  |  | Cost of Material | [5 empty] | 15074
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 15175
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 2066.0763
17241.0762
|  |  | Rate per Each | [5 empty] | 17241
Supply and Transportation of 48" ( 1200 mm) High Speed Fan Sweep Celing Fan with all accessories etc., complete. Make Havells S S 390
| As per price list |  | Supply and Transportation of 48" ( 1200 mm) High Speed Fan Sweep Celing Fan with all accessories etc., complete. Make Havells S S 390 | Each | 1 | 1 | Nos | 3800 | 3800
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 517.37
4317.37
|  |  | Rate per Each | [5 empty] | 4317
Labour charges for fixing of ceiling fan and regulator including transportation and giving connections with twin core wire etc., complete. Makes : Finolex / RR Kabel / Havells / Polycab / GM / Million / V-Guard / Gold Medal / HPL / RPG.
a) Labour charges
| 1 |  | Skilled Electrician. | 0.125 | day | 1 | day | 660 | 82.5
| 2 |  | Helper (Electrical). | 0.125 | day | 1 | day | 550 | 68.75
|  |  | Labour for 1 No | [5 empty] | 151.25
b) Material
| 1.5.5 |  | Supply of 23 / 0060 twin core twisted / flat heavy Copper wire. | 1 | Mtrs | 100 | Mtrs | 1200 | 12
|  |  | Cost of Material for fixing fan | [5 empty] | 12
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 163
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 22.1924
185.1925
|  |  | Rate per Each | [5 empty] | 185
Supply and fixing of Anchor fastner with fan hook / Providing MS Fan hook with grouting and cement plastering.
| ELEC-9.1.23 |  | Supply and fixing of Anchor fastner with fan hook / Providing MS Fan hook with grouting and cement plastering. | Each | 1 | 1 | Nos | 107 | 107
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 14.568
121.568
|  |  | Rate per Each | [5 empty] | 122
Supply and fixing of 6 / 10A 1 Way 1 Module Modular Switches - 2 Nos and 10A 3/2 Pin 2 Module Modular Socket with shutter - 2 Nos Modular type with cover plate and GI switch box fixing on separate board including all labour charges etc., complete. Makes of switches : Honeywell Blenge Plus
a) Labour charges :
| 1 |  | Skilled Electrician. | 0.1 | day | 1 | day | 660 | 66
| 2 |  | Helper (Electrical). | 0.1 | day | 1 | day | 550 | 55
|  |  | Labour for 1 No | [5 empty] | 121
b) Material
| 1.3.1 | d | Supply of 6 Module box | 1 | No | 1 | No | 164 | 164
| 1.3.2 | d | Supply of 6 Modular Cover Frame. | 1 | Nos | 1 | No | 164 | 164
| 1.9.1 | a | 6 / 10A 1 Way 1 Module Modular Switch | 2 | Nos | 1 | No | 116 | 232
| 1.9.1 | d | 10A 3/2 Pin 2 Module Modular Socket with shutter | 2 | Nos | 1 | No | 178 | 356
|  |  | Cost of Material for 1 No | [5 empty] | 916
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 1037
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 141.1875
1178.1876
|  |  | Rate per Each | [5 empty] | 1178
Supply,Transportation of 15" (375mm) ISI, 900 RPM Heavy duty exhaust fan with metallic blades wiremesh with all accessories etc complete Makes : Crompton / Almonard / Havells Turbo Force SP.
| 5.1.11 | b | Supply of 15" (375mm) ISI, 900 RPM Heavy duty exhaust fan | Each | 1 | 1 | Nos | 3756 | 3756
|  |  | Transportation | 0.02 |  |  |  |  | 75.12
3831.12
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 521.607
4352.727
|  |  | Rate per Each | [5 empty] | 4353
Labour charges for fixing the exhaust fan in wall with necessary connections and masonary work of making hole, finishing etc., complete. Makes : Finolex / RR Kabel / Havells / Polycab / GM / Million / V-Guard / Gold Medal / Kundancab / HPL / RPG / Nakoda / Payal / Finecab
a) Labour charges
| 1 |  | Skilled Electrician. | 0.25 | day | 1 | day | 660 | 165
| 2 |  | Lineman Electric / Telephone | 0.25 | day | 1 | day | 550 | 137.5
| 4 |  | Mason Cl- I / Brick layer Cl- I | 0.25 | day | 1 | day | 580 | 145
|  |  | Labour for 1 No | [5 empty] | 447.5
| 1.5.5 |  | Supply of 23 / 0060 twin core twisted / flat heavy Copper wire. | 1 | Mtrs | 100 | Mtrs | 1200 | 12
| 9.4.11 |  | Cement. | 25 | Kg | 1 | Kg | 9 | 225
|  |  | Sundries such as Sand, Bolt, Nuts etc. | 1 | Job | 1 | Job | 10 | 10
|  |  | Cost of Material for fixing fan | [5 empty] | 247
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 694
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 94.4881
788.4881
|  |  | Rate per Each | [5 empty] | 788
Supply and fixing of 12 Way SPN DB with IP 43 Protection as per IS:13032 with 1 No 63A FP MCB as Incommer, and 8 Nos of 6-32A SP MCB 10KA, C/D Curve ISI Mark as out goings, concealing in wall etc complete. DB Makes :Legrand MCB Makes : Legrand-DX3
LABOUR
| 1 |  | Skilled Electrician. | 0.5 | day | 1 | day | 660 | 330
| 2 |  | Lineman Electric / Telephone | 0.5 | day | 1 | day | 550 | 275
| 3 |  | Mason Cl- I / Brick layer Cl- I | 0.5 | day | 1 | day | 580 | 290
895
MATERIAL
| 2.16.1 | f | Supply of 12 Way SPN DB | 1 | Nos | 1 | No | 2302 | 2302
1 | ELEC-2.14.1 | h | Supply of 40-63A FP MCB | 1 | No | 1 | No | 2651 | 2651
| ELEC-2.14.1 | a | Supply of 20A 10KA SP MCB, C/D Curve ISI Mark. | 8 | Nos | 1 | No | 294 | 2352
| ELEC-9.4.11 |  | Cement. | 12.5 | Kg | 1 | Kg | 9 | 112.5
7417.5
|  |  | TOTAL COST OF MATERIAL + LABOUR FOR FLUSH MOUNTING | FLUSH |  |  |  |  | 8312.5
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 1131.7469
9444.2469
|  |  | Rate per Each | [5 empty] | 9444
Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete
a) Labour charges
| 3 |  | Helper (Electrical). | 0.1 | day | 1 | day | 550 | 55
|  |  | Labour for 1 No | [5 empty] | 55
b) Material
| 9.1.21 |  | 19/20mm steel tube down rod with bolts & nuts for fan with maching colour. | 1 | Mtrs | 1 | Mtrs | 110 | 110
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 165
|  |  | Less cost of fan down rod supplied with new fan of about 9" in length equal to 0.23 Metre at above rate | 0.23 | Mtrs | 1 | Mtrs | 110 | 25.3
139.7
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 22.4647
162.1647
|  |  | Rate per Each | [5 empty] | 162
Supply and fixing of cable adopteres box with cover for DBs including, massanory work etc., complete.,
| Approved rate in SOTC Gandhi Hospital |  | Supply and fixing of cable adopteres box with cover for DBs including, massanory work etc., complete., | Each | 1 | 1 | Nos | 4500 | 4500
4500
Supply and fixing of FP Metal Enclosure with IP 20 Protection DB Make with 1 No 63A, 10 KA DP MCB including internal connection and labour charges for Flush Mounting etc.,complete. Makes of Enclousure : Legrand MCB Makes : Legrand-DX3
LABOUR
| 1 |  | Skilled Electrician. | 0.25 | day | 1 | day | 660 | 165
| 2 |  | Lineman Electric / Telephone | 0.25 | day | 1 | day | 550 | 137.5
| 3 |  | Mason Cl- I / Brick layer Cl- I | 0.15 | day | 1 | day | 580 | 87
|  |  | COST OF LABOUR FOR FULSH MOUNTING | [5 empty] | 389.5
MATERIAL
| 2.17.11 |  | Supply of DP/TP/FP Metal Enclosure with IP 20 Protection. | 1 | Nos | 1 | No | 614 | 614
| 2.14.1 |  | Supply of 40-63A FP MCB, C/D Curve ISI Mark. | 1 | Nos | 1 | No | 2651 | 2651
| 9.4.11 |  | Cement. | 5 | Kg | 1 | Kg | 9 | 45
|  |  | COST OF MATERIAL FOR FULSH MOUNTING | [5 empty] | 3310
|  |  | TOTAL COST OF MATERIAL + LABOUR FOR FULSH MOUNTING | [5 empty] | 3699.5
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 503.6869
4203.1869
4203
Supply, Transportation and Run of 4core of 2.5 Sqmm copper cable in the existing cable tray/ conduit pipe and labour charges etc., complete. Makes :Polycab
b) Labour charges
| 1 |  | Skilled Electrician. | 0.7 | day | 1 | day | 660 | 462
| 2 |  | Lineman Electric / Telephone | 1 | day | 1 | day | 550 | 550
| 3 |  | Helper (Electrical). | 1 | day | 1 | day | 550 | 550
|  |  | Labour for 100 Mtrs | [5 empty] | 1562
|  |  | Labour for 1 Mtr | [5 empty] | 15.62
a) Material
| ELEC-1.5.6 | t | Supply of 2.5 Sqmm 4 Core PVC / XLPE Insulated Sheathed Multi Core Bright Annealed Bare Copper Conductor Heavy Duty Industrial Cables for Voltage Grade upto 1100 Volts as per IS: 694:1990 including all transportation charges etc complete. Makes :Polycab | 1 | Mtrs | 1 | Mtrs | 158 | 158
|  |  | Cost of Material for 1 Mtrs | [5 empty] | 158
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 173.6
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 23.6356
197.2356
|  |  | Rate per Meter | [5 empty] | 197
Supply, Transportation and Run of 2 core of 1.5 Sqmm copper cable in the existing cable tray/ conduit pipe and labour charges etc., complete. Makes : Polycab
b) Labour charges
| 1 |  | Skilled Electrician. | 0.7 | day | 1 | day | 660 | 462
| 2 |  | Lineman Electric / Telephone | 1 | day | 1 | day | 550 | 550
| 3 |  | Helper (Electrical). | 1 | day | 1 | day | 550 | 550
|  |  | Labour for 100 Mtrs | [5 empty] | 1562
|  |  | Labour for 1 Mtr | [5 empty] | 15.62
a) Material
| ELEC-1.5.6 | g | Supply of 1.5 Sqmm 2 Core PVC / XLPE Insulated Sheathed Multi Core Bright Annealed Bare Copper Conductor Heavy Duty Industrial Cables for Voltage Grade upto 1100 Volts as per IS: 694:1990 including all transportation charges etc complete. Makes :Polycab | 1 | Mtrs | 1 | Mtrs | 56 | 56
|  |  | Cost of Material for 1 Mtrs | [5 empty] | 56
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 71.6
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 9.7483
81.3483
|  |  | Rate per Meter | [5 empty] | 81
Supply and Fixing of ISI 25mm outer dia medium grade, with IS:9537 part 3 rigid PVC with all accessories fixing on chromium plated metallic base saddles including all labour charges etc., complete for run of mains. Makes:- Sudhakar / Finolex / Modi / VIP / Precision / Universal / Million Plast / Gold / Polycab / DEC.
a) Labour charges :
| 1 |  | Skilled Electrician. | 2 | day | 1 | day | 660 | 1320
| 2 |  | Lineman Electric / Telephone | 2 | day | 1 | day | 550 | 1100
| 3 |  | Helper (Electrical). | 2 | day | 1 | day | 550 | 1100
| 4 |  | Mason Cl- I / Brick layer Cl- I |  | day | 1 | day | 580 | 0
|  |  | Labour Rate Per 100 Rm | [5 empty] | 3520
|  |  | Labour Rate for 1 Mtr | [5 empty] | 35.2
b) Material
| 9.4.11 |  | Cement. | 25 | kg | 1 | Kg | 9 | 225
| 9.1.2 |  | Rawl Plugs | 200 | Nos | 100 | Nos | 43 | 86
| 1.4.4 | d | 35mm Screws | 200 | Nos | 100 | Nos | 128 | 256
| 1.1.11 | b | Chromium Plated saddles with base | 200 | Nos | 100 | Nos | 279 | 558
| 1.2.6 | b | Supply of 25mm PVC Junction Boxes Normal. | 12 | Nos | 1 | Nos | 25 | 300
| 1.2.8 | b | Supply of 25mm dia 1.5mm thick PVC Bends. | 12 | Nos | 1 | Nos | 10 | 120
| 1.2.2 | b | Supply of ISI 25mm outer dia medium grade FRLS with IS:9537 part 3 regid PVC pipe. | 100 | Mtr | 1 | Mtr | 30 | 3000
|  |  | Material Rate for 100 Mtrs | [5 empty] | 4545
|  |  | Material Rate for 1 Mtr | [5 empty] | 45.45
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 80.6
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 10.9737
91.5737
|  |  | Rate per Meter | [5 empty] | 92
Supply, Transportation and Run of 4 core of 1.5 Sqmm copper cable in the existing cable tray/ conduit pipe and labour charges etc., complete. Makes : Polycab
b) Labour charges
| 1 |  | Skilled Electrician. | 0.7 | day | 1 | day | 660 | 462
| 2 |  | Lineman Electric / Telephone | 1 | day | 1 | day | 550 | 550
| 3 |  | Helper (Electrical). | 1 | day | 1 | day | 550 | 550
|  |  | Labour for 100 Mtrs | [5 empty] | 1562
|  |  | Labour for 1 Mtr | [5 empty] | 15.62
a) Material
| ELEC-1.5.6 | g | Supply of 1.5 Sqmm 2 Core PVC / XLPE Insulated Sheathed Multi Core Bright Annealed Bare Copper Conductor Heavy Duty Industrial Cables for Voltage Grade upto 1100 Volts as per IS: 694:1990 including all transportation charges etc complete. Makes :Polycab | 1 | Mtrs | 1 | Mtrs | 56 | 56
|  |  | Cost of Material for 1 Mtrs | [5 empty] | 56
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 71.6
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 9.7483
81.3483
|  |  | Rate per Meter | [5 empty] | 81
Supply and fixing of suitable out door feeder piller box of size made with 14 SWG CRCA sheet with double door arrangement, making powder coating after processing of 7 Tank process, lock and key, hinges, rubber gasket, danger board,suitable angle iron stand for mounting the feeder pillar with cement concrete, including Supply and fixing of Legrand / Schnieder make as out goings, indication lamps, din channel, 6 Sqmm 3 core copper cable for invidual light control, connectors,bus bars, shroudings, gland plates and provision for 3 phase energy meter etc.,complete for finished item of work and suitable wirin provision for connecting the nature switch with following.63A, 4 Pole MCB as incomer, 9 Nos 6-32A SP MCBs
| ELEC-7.6.2 |  | Supply and fixing of suitable out door feeder piller box of size made with 14 SWG CRCA | 1 | No | 1 | No | 27081 | 27081
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 3687.0781
30768.0782