## seignorage (hidden)
S.No | Item S.No | Item Code | Item Name | UOM | QTY | QTY |  |  | Co-efficients |  |  | Rates |  |  | Amount |  |  | Total Amount
[6 empty] | Sand (QTY) | Metal (QTY) | Brick (QTY) | Sand | Metal | Bricks | Sand Rate | Metal Rate | Brick Rate | Sand Amount | Metal Amount | Brick Amount
1 | 49 | IVF049 | Dismantling, clearing away and carefully stacking useful materials for re- use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges, etc., complete. Brick Masonry at Gandhi Hospital | Cum | 32.677 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
2 | 50 | IVF050 | Dismantling doors, windows and clear storey windows, Ventilators etc., wood or steel shutters including Chowkhats, architraves, hold fasts and other attachments etc., and stacking them within 100m lead including labour charge etc., and complete for finished item of work. Not exceeding 3 sqm in area: Doors 1.00x2.60M at Gandhi Hospital | No | 2 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
3 | 51 | IVF051 | Dismantling doors, windows and clear storey windows, Ventilators etc., wood or steel shutters including Chowkhats, architraves, hold fasts and other attachments etc., and stacking them within 100m lead including labour charge etc., and complete for finished item of work. Exceeding 3 sqm in area: Doors 1.50x2.60M at Gandhi Hospital | No | 5 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
4 | 52 | IVF052 | Conveyance of un-useful excavated earth to a distance of 21 KM for disposal including hire charges of T and P, labour charges etc., complete for finished item of work. Dismantled Brick masonry at Gandhi Hospital | Cum | 48.7 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
5 | 53 | IVF053 | Brick masonry for panel walls in superstructure with CM 1:8 prop: Aerated Cellular Autoclaved Concrete Blocks conforming to IS:2185 Part-3 - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600 x 200 x 200 mm including cost and conveyance of all materials like cement, screened sand, bricks, water etc., to site, including sales and other taxes on all materials and such as labour charges, like mixing cement mortar, scaffolding charges, constructing masonry, lift charges, curing, etc.,complete for finished item of work. TSSS No.501 and 504. 5th Floor at Gandhi Hospital | Cum | 15.27 | 2.67 |  | 1084 | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 46.992 | 0 | 33.3005 | 80.2925
7 | 54 | IVF054 | Reinforced Masonry for partition walls 100 mm thick in CM 1:4 prop. Aerated Cellular Autoclaved Concrete Blocks conforming to IS:2185 Part-3 - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600 x 200 x 100 mm and placing 2Nos. of 6mm M.S plain rods in every third layer with free ends of the reinforcement pegged into mortar joints of main brick walls where applicable including cost and conveyance of all materials like cement, steel, sans, brick, water etc., to site, including sales and other taxes excluding GST on all materials, all operational, incidents charges, constructing masonry, lift charges, curing, complete for finished item of work. TSSS No. of 509.5th Floor at Gandhi Hospital | Sqm | 191.03 | 3.01 |  | 1356 | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 52.976 | 0 | 41.6563 | 94.6323
8 | 55 | IVF055 | Providing Mild steel MS steel bars Fe 250 grade as per IS 432 of different diameters including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying including sales and other taxes on all materials etc. , complete for finished item of work. TSSS No.126 For RBM walls 6mm dia: 5th Floor at Gandhi Hospital | MT | 0.1 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
9 | 56 | IVF056 | Plastering 20mm thick in two coats using screened sand with base coat of 16mm thick in CM1:6 and top coat of 4mm thick in CM1:4 with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales and other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., complete for finished item of work .SS 901,903and 904 5th Floor at Gandhi Hospital | Sqm | 11.04 | 0.248 |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 4.3648 | 0 | 0 | 4.3648
10 | 57 | IVF057 | Plastering 12mm thick in two coats using screened sand with base coat of 8mm thick in CM 1:6 and top coat of 4mm thick in CM 1:4 with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales and other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and complete for finished item of work. SS 901,903 and 904. 5th Floor at Gandhi Hospital | Sqm | 547.15 | 7.31 |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 128.656 | 0 | 0 | 128.656
12 | 59 | IVF059 | Providing and laying screed plain cement concrete as per site condition for floor bedding using high quality aggregates including base preparation, compaction, levelling, all lead and lifts, rough finishing at the top surface, curing, shuttering if necessary etc., complete as directed . at Gandhi Hospital | Cum | 0 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
39 | 15 | IVF015 | Dismantling of unreinforced cement concrete, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete | [5 empty] | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
40 | 16 | IVF016 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete Old Cement Mortor (Plaster) | [5 empty] | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
41 | 17 | IVF017 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete. Reinforced Cement Concrete | [5 empty] | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
42 | 18 | IVF018 | Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707) | [5 empty] | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
308
[6 empty] | Brick Masonary |  | Partition walls |  | Plastering 20 mm |  | Plastering 12 mm
[6 empty] | Proportion | 1:08 |  | 191.03 | QTY | 11.04 | Qty | 547.15
[6 empty] | QTY | 15.27 | QTY | 19.103 |  | 0.17664 |  | 4.3772
[6 empty] | V of 1 brick | 0.014091 | Ratio | 1:04 | dry v | 0.23493 | dry v | 5.8217
[6 empty] | no of bricks | 1083.6704 | V of 1 brick | 0.014091 | Ratio | 1:06 | Ratio | 1:06
[6 empty] | v of 1 brick | 0.012 | no of bricks | 1355.688 | cement | 0.033562 | cement | 0.83167
[6 empty] | qty | 13.004 | v of 1 brick | 0.012 | sand | 0.20137 | sand | 4.99
[6 empty] | mortor qty | 2.266 | qty | 16.2683 | Ratio | 1:04 | Ratio | 1:04
[6 empty] | dry v | 3.0137 | mortor qty | 2.8347 |  | 0.04416 |  | 2.1886
[6 empty] | Cement | 0.33486 | dry v | 3.7702 | dry v | 0.058733 | dry v | 2.9108
[6 empty] | Sand | 2.6789 | Cement | 0.75404 | cement | 0.011747 | cement | 0.58217
[8 empty] | Sand | 3.0162 | sand | 0.046986 | sand | 2.3287
[10 empty] | T sand qty | 0.24836 | T sand qty | 7.3187
555

## Revised Estimate-SECTIONS
REVISED ESTIMATE OF IVF-5TH FLOOR, MCH BUILDING, GANDHI HOSPITAL
S. No | Item S.No | Item Code | DESCRIPTION | As per Agreement |  |  |  | As per Work Done Estimate |  |  |  | EXCESS | LESS | REMARKS
|  |  |  | QTY | UNIT | RATE | AMOUNT RS. | QTY | UNIT | RATE | AMOUNT RS.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
Equipment Supplemental Works
1 |  |  | Fowler Two Function Bed with ABS Panel, ABS Side Railings, Wheels, Mattress Pillow, & Bed Fixing IV Road Features (Knee rest & Backrest) Size-L,84, W-42, H-24. The finished bed must be rust proof, pre-treated and treated with epoxy polyester antimicrobial powder coated to increase the bacteriostatic property. The bed must be quoted with washable cover of lasting quality. The mattress should be made of high-density PU foam of 100 mm thickness. | 0 | Nos |  |  | 5 | Nos | 39000 | 195000 | 195000 | 0 | This item is executed since it is required for ICMR Clearance. | EQPS
2 |  |  | Bed side Table with ABS Plastic body construction having 1 drawer and an adequated space with openable door with handle of size | 0 | Nos |  |  | 5 | Nos | 9000 | 45000 | 45000 | 0 | This item is executed since it is required for ICMR Clearance. | EQPS
3 |  |  | Corporate Deluxe Locker with SS 304 grade Top of size 508 x 406 x 762 mm having 1 drawer and an adequate storage space with openable door with SS handle. Equipped with wheels for easy movement. | 0 | Nos |  |  | 1 | Nos | 8400 | 8400 | 8400 | 0 | This item is executed since it is required for ICMR Clearance. | EQPS
4 |  |  | Bed side stand with full SS 304 grade constructionof size 406 x 203 x 762 mm equipped with SS Handles on top for carrying. | 0 | Nos |  |  | 1 | Nos | 9300 | 9300 | 9300 | 0 | This item is executed since it is required for ICMR Clearance. | EQPS
5 |  |  | Bed side stand with full GI Powder coated constructionof size 406 x 203 x 762 mm equipped with powder coated handles on top for carrying. | 0 | Nos |  |  | 1 | Nos | 4200 | 4200 | 4200 | 0 | This item is executed since it is required for ICMR Clearance. | EQPS
6 |  |  | Cryo Can 11 Ltr without wheels | 0 | Nos |  |  | 1 | Nos | 32000 | 32000 | 32000 | 0 | This item is executed since it is required for ICMR Clearance. | EQPS
7 |  |  | 3-Bay Surgical Scrub Station/Sink to be provided for use in the OT complex providing for pre-procedural scrub up with minimum three bay sink combination as suitable. The Scrub Station shall be made of Stainless Steel of 304 grade sheet with minimum thickness of 1.5mm and designed as per the high aesthetics of the theatre complex. Shall have smoothened surfaces & corners. The scrub sink shall be provided with a front access panel which shall be easily removed for access to the water-controlled valve, waste connections, stoppers & strainers. The Scrub station should be equipped with two foot operated and one elbow operated mechanisms. Shall have provision for fresh water and waste water piping ready for connections. | 0 |  |  |  | 1 | Nos | 97000 | 97000 | 97000 | 0 | This item is executed since it is required for ICMR Clearance. | EQPS
8 |  |  | Supply of Sample collection bed of size 1850x620x700 mm, featuring plain design equipped with 1 drawer and storage space with openable door type with SS-304 grade handles positioned at head side of the bed. The material of construction of the bed to be of Powder coated GI for entire body. All the legs of the bed to be capped with nylon bushes. The finished bed must be rust proof, pre-treated and treated with epoxy polyester antimicrobial powder coated to increase the bacteriostatic property. The bed must be quoted with washable cover of lasting quality. The mattress should be made of high-density PU foam of 100 mm thickness. | 0 | Nos |  |  | 1 | Nos | 29000 | 29000 | 29000 | 0 | This item is executed since it is required for ICMR Clearance. | EQPS
9 |  |  | Supply of a Sample collection chair of size 800x580x700 mm, meeting medical standards, featuring adjustable height and tilt padded armrests, and durable upholstery, suitable for comfortable patient positioning during blood donation or phlebotomy procedures. The chair is made from mild steel with good finish. The chair to be of easy to manoeuvre and transport and of light weight. | 0 | Nos |  |  | 1 | Nos | 16200 | 16200 | 16200 | 0 | This chair is mandatory for a patient and executed since it is required for ICMR Clearance. | EQPS
10 |  |  | Supply and installation of Stainless Steel 304 grade CSSD Rectangular Working table of size 1200x480x1050 mm with inbuilt sink of size 450x380x300 mm equipped with jali at bottom to stop any large particles entering into the drain to avoid drain clog. The table to be designed with raised front section and provision of SS sheet at foot level of the table forming a flat surface for storing/placing of items. The table to be of ready to use with all necessary fittings. | 0 | Nos |  |  | 1 | Nos | 46000 | 46000 | 46000 | 0 | An autoclave needs a CSSD table. Hence executed | EQPS
11 |  |  | Writing board made of Pressed wood coated with melamine surface. It has 900mm writing surface height, 1200mm writing surface wide, and 11mm deep, suitable for working on dry wipe board markers. It has an aluminium frame with dark grey plastic corner caps and maker tray. It is enabled with an easy wall mounting with a concealed slot system. It can be mounted either horizontally or vertically. IT consists of a complete mounting set, marker tray, and a board marker | 0 | Nos |  |  | 2 | Nos | 2100 | 4200 | 4200 | 0 | This is mandatory as per ICMR guidelines, hence work is executed as per the instructions of Enduser. | EQPS
12 |  |  | Providing MDF 18 mm thick wooden table of size 900x450 mm with 1 drawer at right side of the table. The table includes keyboard tray. Bottom equipped with nylone bushes for floor protection and easy movement. | 0 | Nos |  |  | 2 | Nos | 14500 | 29000 | 29000 | 0 | This table is necessary to place the computer for ultrasound machine.hence item is executed. | EQPS
13 |  |  | Supply of a 3-seater sofa upholstered with PU leather, with a high-quality finish. The sofa shall feature a kiln-dried hardwood frame for durability, reinforced with corner blocks for stability. The seat cushions to be constructed with high-density foam padding for comfort and resilience, while the backrests shall feature a combination of foam and fiberfill for optimal support. The sofa arms shall be padded for additional comfort, with sleek wooden or metal legs providing sturdy support. The leather upholstery shall be treated for resistance to stains and spills, ensuring longevity and ease of care. The dimensions of the sofa shall be suitable to accommodate three individuals comfortably, with ample seating space and ergonomic design considerations. | 0 | Nos |  |  | 2 | Nos | 24000 | 48000 | 48000 | 0 | Executed as per instructions of higher officials & enduser. | EQPS
14 |  |  | SS-304 working table of size 685x685x762 mm with I type support inner frame SS-304 pipe of size 40x40x1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. | 0 | Nos |  |  | 2 | Nos | 16300 | 32600 | 32600 | 0 | It is necessary to place the equipments hence, work is executed as per the instructions of Higher officials. | EQPS
15 |  |  | SS-304 working table of size 457x457x762 mm with I type support inner frame SS-304 pipe of size 40x40x1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. | 0 | Nos |  |  | 1 | Nos | 14500 | 14500 | 14500 | 0 | It is necessary to place the equipments hence, work is executed as per the instructions of Higher officials. | EQPS
16 |  |  | SS-304 working table of size 610x610x762 mm with I type support inner frame SS-304 pipe of size 40x40x1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. | 0 | Nos |  |  | 1 | Nos | 15100 | 15100 | 15100 | 0 | It is necessary to place the equipments hence, work is executed as per the instructions of Enduser. | EQPS
17 |  |  | SS-304 working table of size 660x610x762 mm with I type support inner frame SS-304 pipe of size 40x40x1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. | 0 | Nos |  |  | 1 | Nos | 15800 | 15800 | 15800 | 0 | It is necessary to place the equipments hence, work is executed as per the instructions of Higher officials. | EQPS
18 |  |  | Supply and fixing of Powder coated GI stand with 4 nos height adjustable racks of size 670x410x1570 mm connected to two big rods of rectangular hollow section type supported with 4 legs with wheels with brakes to restrict movement/easy movement. Equipped with frame for holding a cylinder. A lockable box type space to be provided at bottom rack. |  |  |  |  | 1 | Nos | 80000 | 80000 | 80000 | 0 | It is necessary to place the equipments hence, work is executed as per the instructions of Higher officials. this stand is necessary to place the Hysterscopy & Laproscopy set | EQPS
19 |  |  | The Multipurpose Electro Hydraulic Mobile OT Table is designed for gynecological surgical procedures, featuring a wide range of adjustments for optimal patient positioning. It offers precise control with movement controls at the side of the table and a wired remote control handset and features like S. S. Arm Rest, Anaesthetic Screen, Lithotomy Leg Holders with Stirr-Ups, Leather Wristlets, Padded Leg Rest, Anti-static mattress, and an additional Poly-urethane mattress. Built with a Stainless Steel 304 frame and bottom, it ensures durability. The table top, reinforced with three-section stainless steel and radiolucent capabilities, allows for comprehensive patient support. Its flexibility includes 360° rotation, adjustable Trendelenburg, Reversed Trendelenburg, Head Section, Back Section, and Leg Section. Physical specifications include a 1900 mm x 525 mm top with an elevation range of 640mm to 1040mm, supporting patients up to 140 kg. Environmental considerations ensure operational efficiency in various conditions. |  |  |  |  | 1 | Nos | 210000 | 210000 | 210000 | 0 | This work is executed as per the instructions of higher officials | EQPS
[7 empty] | 0 |  |  | PART-A | 931300 | 931300 | 0
CIVIL WORKS
20 | 51 | IVF051 | Dismantling doors, windows and clear storey windows, Ventilators etc., wood or steel shutters including Chowkhats, architraves, hold fasts and other attachments etc., and stacking them within 100m lead including labour charge etc., and complete for finished item of work. Exceeding 3 sqm in area: Doors 1.50x2.60M at Gandhi Hospital | 5 | No | 468 | 2340 | 7 | No | 468 | 3276 | 936 | 0 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
21 | 53 | IVF053 | Brick masonry for panel walls in superstructure with CM 1:8 prop: Aerated Cellular Autoclaved Concrete Blocks conforming to IS:2185 Part-3 - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600 x 200 x 200 mm including cost and conveyance of all materials like cement, screened sand, bricks, water etc., to site, including sales and other taxes on all materials and such as labour charges, like mixing cement mortar, scaffolding charges, constructing masonry, lift charges, curing, etc.,complete for finished item of work. TSSS No.501 and 504. 5th Floor at Gandhi Hospital | 12 | Cum | 16055 | 192660 | 15.27 | Cum | 16055 | 245160 | 52500 | 0 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
22 | 65 | IVF065 | Flooring with soluble salt porcelain vitrified tiles screen printed and polished of size 600 x 600 mm and thickness between 8 to 10mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630Parts 1 to 15 of any colour and finish in all shades and designs with borders and design as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM 1:8 prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread at the rate 3.3 kgs per Sqm. and jointed neatly with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site excluding cost of C.C. bed including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in- charge etc., and complete for finished item of work. TSSS No.701 and 707. 5th Floor at Gandhi Hospital | 225 | Sqm | 1725 | 388125 | 374.81 | Sqm | 1725 | 646547 | 258422 | 0 | As per the site condition & floor plans approved, the Qty. exceeded and hence proposed as AE | C
23 | 68 | IVF068 | Providing dadooing to walls with glazed full body porcelain wall tiles of size 300 x 600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. 5th Floor at Gandhi Hospital | 40 | Sqm | 1423 | 56920 | 103.77 | Sqm | 1423 | 147665 | 90745 | 0 | As per the site condition and instructions of Higher officials, daddoing provided at corridor area near the reception. Hence the qty is exceeded and hence proposed as AE | C
24 | 90 | IVF090 | Single leaf clean room Doors : 46mm thick flush doors made of 0.8mm thick Powder coated GI sheets on both sides, 90 plus or minus 2 kg/m3 density Honeycomb with stand upto 220 Deg.C Temperature, and compressible strength upto 400 Kg/Sqm, 1.2 mm thick GPSP . door frames, double glazed vision panel with necessary adhesive tapes and silicon sealant, necessary hardware like SS304 ball bearing butt hinges, D- handles, push plates, Dorma make door closure, concealed tower bolt, drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms, Both side lock and keys etc. complete. Size 900 X 2100 mm with 300 mm x 300 mm View panel at Gandhi Hospital | 1 | No | 28700 | 28700 | 3 | No | 28700 | 86100 | 57400 | 0 | As per the instructions of Higher officials Autoclave Room & UPS Room Mandates the scientific door, the Qty. exceeded and now proposed as AE | C
Civil Supplementary Works
25 |  |  | Supply and application of one coat water based cement primer of interior grade I for internal walls including cost and conveyance of all materials to site, sales and other taxes, incidental, operational and all labour charges etc., and complete for finished item of work in 5th floor (for Ceiling) at Gandhi Hospital |  |  |  |  | 536.11 | Sqm | 85 | 45569 | 45569 | 0 | This work is executed as per the instructions of higher officials | CS
26 |  |  | Dismantling of unreinforced cement concrete, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete |  |  |  |  | 3.89 | Cum | 4036 | 15700 | 15700 | 0 | The work was taken up as per approved floor plan drawings and in contingent with the main work and hence proposed as supplemental item. | CS
27 |  |  | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete - Old Cement Mortor (Plaster) |  |  |  |  | 37.13 | Sqm | 13 | 483 | 483 | 0 | The work was taken up as per approved floor plan drawings and in contingent with the main work and hence proposed as supplemental item. | CS
28 |  |  | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete. Reinforced Cement Concrete |  |  |  |  | 0.7 | Cum | 4424 | 3097 | 3097 | 0 | The work was taken up as per approved floor plan drawings and in contingent with the main work and hence proposed as supplemental item. | CS
29 |  |  | Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707) |  |  |  |  | 107.18 | Rmt | 162 | 17363 | 17363 | 0 | This work was executed as per the requirement and instructions from higher officials | CS
30 |  |  | Providing of Factory made prelaminated FPVC (Foamed Polyvinyl Chloride) Door frame of the size 105x40mm with a wall thickness of 10mm made out of extruded rigid FPVC profile mitre joined with 6 Nos. of 50mm long screw. The door frame shall be fixed to the wall by using 80mm long screws through the frame with the help of PVC fasteners of 3 no's to be provided for each vertical member, GI stiffeners of ("U" channel of size 29x9x1mm, 150mm long) -3 no's at hinge point, Frame reinforcement of("U" GI channel of size 46x22x.06mm),Bottom tie rod of ("U" GI channel size of 15x15x1mm) etc. complete as per manufacturers specification for finished item of work. Maximum door frame size : 980 x 2070 including providing of 35mm thick Factory made Prelaminated ABS (Acrylonitrile Butadiene Styrene) Door shutter moulded in different designs, consisting of all round Frame made out of water proof solid foam PVC bar of size 20x32mm, reinforced by 32x 32mm - 2 nos. for vertical made out of LVL (Laminated Veneer Lumber), core material of 32 mm thick high density craft paper honey comb board, sandwiched on both sides with prelaminated ABS sheet thickness of 1.5mm . PVC edge banding of size 0.45mm on the vertical sides. Hardware made out of steel coated butterfly hinges - 3 Nos. for each shutter and ISI make S.S round lock completes for finished item of work. Maximum shutter size of : 910 x 2030 mm |  |  |  |  | 23.463 | Sqm | 9241 | 216822 | 216822 | 0 | To maitain low VOC in Fertility center, wooden doors are replaced with ABS doors as per MOM dated: 01-08-2023. (copy Attached) | CS
31 |  |  | Flooring with 16 to 18 mm thick high polished granite stone slabs black colour as approved by the Engineer-in-Charge of length not less than 2.43 mts set over base coat of cement mortar (1:8) , 20mm thick using screened sand over CC bed already laid or RCC roof slab including neat grey cement slurry of honey like consistency spread @ 3.3 Kg per sqm and jointed neatly with white cement paste mixed with pigment of matching shade to full depth including cost and conveyance of all materials like cement , sand , water , granite slabs etc., to work site and all operational, incidental labour & lift charges, half rounding the edge , polishing charges and all other taxes on all materials, cost of base coat and overheads & contractors profit complete for finished item of work for platforms (S.S.701 & special) (for Reception Table). |  |  |  |  | 10.17 | Sqm | 5839 | 59383 | 59383 | 0 | This work is executed as per the TSMSIDC Higher officials in lieu of reception table. | CS
32 |  |  | 50 LPH storage type RO of dimensions 525 x 425 x 1450 mm (WxDxH) of approx. weight 75Kg consists of 4 nos of 80 GPD 3-layer Thin Film Composite (TFC) membrane with 0.0001-micron pore size which can prevent TDS, heavy metals and equipped with 6 stage purification process which reduces pesticides in the water for reducing scale formation when water is heated. The RO should take min input pressure of 0.6 kg/cm2, 2000 ppm of TDS in Water, 500 ppm of Hardness, 6.5 to 8.5 PH of water which can give output of 20 to 25 % recovery in purified water and can run on 230V AC, 50 Hz supply with operating temp of 5oC-45oC. |  |  |  |  | 1 | Nos | 75000 | 75000 | 75000 | 0 | Autoclave needs clean water as per ICMR guidelines, hence this item is takenup. | CS
33 |  |  | Supply and placing of the Design Mix Concrete M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Weight Batcher / Concrete mixer with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials, centering using Casurina Ballies, Bamboos, Wooden Reapers, Runners, Wood Posts, Steel Plates etc., including all operational, incidental and labour charges such as weigh batching, machine mixing, lifting of concrete manually, laying concrete, curing , overheads & contractors profit etc., complete but excluding cost of steel and its fabrication charges for finished item of work (APSS No. 402) (for Lintels) |  |  |  |  | 0.43 | Cum | 15969 | 6867 | 6867 | 0 | This work is exectued as per site conditions. | CS
34 |  |  | Supply and fixing of Dress Hangers of size 450mm length with 8 Nos hooks, each capped with plastic protective cap (in change rooms). |  |  |  |  | 5 | Nos | 510 | 2550 | 2550 | 0 | This item is executed as requested by the Enduser. | CS
35 |  |  | Supplying and fixing Rectangular Mirror Frameless of size 457 .2 mm x 609.6 mm (For Change room) |  |  |  |  | 5 | Nos | 1775 | 8875 | 8875 | 0 | This item is executed as requested by the Enduser. | CS
36 |  |  | Supply of Venetian blinds Vertical blinds 100 mm wide with all accessories. (For semen collection room & Counselling room Windows) |  |  |  |  | 5.01 | Sqm | 2187 | 10957 | 10957 | 0 | This item is executed as requested by the Enduser. | CS
37 |  |  | Name Plates (Room Names) as approved by the Engineer In-charge. |  |  |  |  | 31 | Nos | 600 | 18600 | 18600 | 0 | This item is executed as requested by the Enduser. | CS
38 |  |  | Supply and fixing of High Quality IVF Procedural photos placed between two transparent acrylic boards fixed with studs at four corners to the PVC frame placed on DBs. (2' x 2' and above) |  |  |  |  | 14 | Nos | 9000 | 126000 | 126000 | 0 | This work is executed as per the instructions of Enduser & TSMSIDC Higher Officials. | CS
39 |  |  | Providing, Fabricating and fixing full height V-board partitions of overall thickness of 75mm Partition frame work to be formed out of 50 X 25mm aluminium frame work placed vertically and horizontally at required centre to centre and cross braced with floor and ceiling channels. The cross bracing channels shall be provided also at above and below the partition framework and to be secured to floor at bottom and to any nearest structural member using galvanized metal screws and wooden / PVC rawl plugs. Partition framework to be cladded with 12.5mm thick tapered edge board on both sides of the partition in line and level fixed with drywall screws @ 300mm c/c with staggered joints to avoid through joints and finished with proprietary supplied jointing tape and compound. |  |  |  |  | 89.11 | Sqm | 1625 | 144804 | 144804 | 0 | This work is mandatory in contigent to the main work. Hence, executed. | CS
40 |  |  | Supply and fixing of doors as per approved drawings with (WPC) single extruded Door Frame section of 100*65 MM and30mm thick Wood Plastic Composite (WPC) Door shutter, comprising of 70% virgin polymer, 15% wood powder (fiber), and the remaining 15% additives, the door shutter shall be water resistant, fire resistant and termite resistant,with Tensile Strength not less than 170Kgf/cm2 and the door shutters surface finished deco paint including cost and conveyance to site of teak wood frame, WPC shutter including supply and fixing 6 nos MS Z hold fasts of size 300 mm x 40 mm x 5mm including cost of ISI marked brass fixtures of 6 Nos butt hinges (IS:205) 150mm long , 1 No. aldrop (IS:2681) 300mm long, 2 Nos tower bolts- 10mm (IS:204) of 200 mm long at top, 1 No. tower bolt- 10mm bolt (IS:204) 150mm long at bottom, 2 Nos. 150mm long fancy handles (IS:208), 2 Nos door stopper and 2 Nos rubber bushes including fixing the fixtures to door with required number of screws, bolt and nuts including labour charges for fixing the frame in position, fixing the shutter to the frame, fixing glass in fan light portion etc., including overheads & contractors profit complete for finished item of work as per APSS 1001 & 1002 The vertical frame of door shall be embedded in flooring for a depth of not less than 10 mm) (800mm x 2100mm) (For Wash Rooms). |  |  |  |  | 6.72 | Sqm | 6734 | 45252 | 45252 | 0 | To maitain low VOC in Fertility center, wooden doors are replaced with WPC doors as per MOM dated: 01-08-2023. (copy Attached) | CS
41 |  |  | Wall Paneling 14mm thick Indoor WPC louvers providing & Fixing full height said 12mm SHERA Board panneling till slab with wooden framing in line and level including fling joints and joint calls and neccesary hardware |  |  |  |  | 18.58 | Sqm | 15500 | 287990 | 287990 | 0 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
42 |  |  | 2 WPC Louvers Ceiling Praviding and fixing WPC Louvers to the Celling of which includes G Perimeter Channels of size 0.55mm thick (having One Flange of 20mm and another flange of 30mm and a web of 27mm) along with perimeter of ceiling screw fixed to brick wall/partition with the help of Nylon sleeves and screws at 610mm centres. Then suspending G1 intermediate channels of size 45mm 10. 9mm thick with 2 flanges of 15mm each) from the soffis at 1220mm centres with ceiling angle of width 25mm x 10mm X0.55mm thick fixed to saffit with GI. cleat and steel expansion fasteners. Ceiling section of 0.55mm thick having knurled web of 51.5mm and 2 flanges of 26mm each with lips of 10.5mm are Soft then fixed to the intermediate channel with the help of connecting clips and in direction perpendicular to the intermediate channel at 450 mm centres IN ULTRA GI CHANNELS Rute to be included all kinds of profiles and cut outs required for light fixtures Speakers. Smoke detector, trao doors and AC grill in the ceiling |  |  |  |  | 7.58 | Sqm | 17450 | 132271 | 132271 | 0 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
43 |  |  | Providing and fixing of wooden box celling at the top of Reception table with Imm thick laminate with wooden framing of BWP 710 Gurjan Ply support from the top slab end to end with neccesary cutouts for lighting and hardware |  |  |  |  | 2.58 | Sqm | 11335 | 29244 | 29244 | 0 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
44 |  |  | Back Pannelling with laminate Finish of 1 mm thick Providing & Fixing full height solid 12mm BWF 710 GURIAN PLY Board panneling till slab with wooden framing in line and level including the neccesary hardware and cutouts |  |  |  |  | 7.5 | Sqm | 10500 | 78750 | 78750 | 0 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
45 |  |  | Providing and fixing ISI marked Magnetic 25mm Block Board door shutters, core of block board construction with frame of 1st class hard wood and fixing 1 MM laminate on both faces of shutters, including ISI marked Stainless Steel butt hinges with necessary screws and tower bait complete |  |  |  |  | 1 | Nos | 13800 | 13800 | 13800 | 0 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
46 |  |  | Providing and fixing PVC frames on the walls for covering the area over DB Boxes with 12 mm PVC sheets in a box section of 60mm thick including neccesary accessories. |  |  |  |  | 4.45 | Sqm | 6473 | 28805 | 28805 | 0 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
47 |  |  | Providing and Fixing of (25X25) mm WPC corner L-Patties at the topper edge of the wall tile cladding |  |  |  |  | 38 | Rmt | 230 | 8740 | 8740 | 0 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
48 |  |  | Providing and Fixing of SS-ROSE GOLD corner & L-Patties at the SIDE edge of the wall tile cladding |  |  |  |  | 7 | Nos | 1500 | 10500 | 10500 | 0 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
49 |  |  | Providing and fixing of Door Frame panneling with 18mm BWP 710 Gurjan Ply and 8mm thick beeding half rounded on the both sides with 1mm thick laminate Finish with necessary handware and Polishing. |  |  |  |  | 11.58 | Rmt | 2166 | 25082 | 25082 | 0 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
50 |  |  | Providing and fixing the 60mm Thick Box framing as the back support for the name plate installed of 18mm BWP 710 Gurjan and 1mm thick high glossy laminate finish |  |  |  |  | 1.32 | Sqm | 11012 | 14536 | 14536 | 0 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
51 |  |  | Providing and Fixing of 32mm Double Flush Door with frame 8mm beeding on its edges on four sides with polishing finish and 1 mm thick laminate on the both sides of which including ISI marked Stainless Steel centre lock and butt hinges with necessary screws and tower bolt complete for (1500 x 200 mm door) |  |  |  |  | 1 | Nos | 50400 | 50400 | 50400 | 0 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
52 |  |  | Providing and fixing of Side wall decor Frame for photo hangings panneling with 18mm BWP 710 Gurjan Ply and 8mm thick beeding half rounded on the both sides with 1mm thick laminate finish with necessary hardware and Polishing. |  |  |  |  | 10.97 | Rmt | 2170 | 23805 | 23805 | 0 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
53 |  |  | Supply and fixing of Wall paper as approved by the Engineer In-charge. (1. 1 x 2 x 4350 x 85 mm & 2. 1 x 2 x 820 x 85 mm) |  |  |  |  | 2 | Nos | 5175 | 10350 | 10350 | 0 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
54 |  |  | Supply and fixing of Main IVF logo with LED arcylic board fixed with LEDs inside and electrical connections as approved by the Engineer In-charge ( 520 mm dia & 50 mm thick) |  |  |  |  | 1 | Nos | 11475 | 11475 | 11475 | 0 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
55 |  |  | Supply and fixing of Main Entrance LED 3D Arcylic letter board fixed with LEDs inside and electrical connections as approved by the Engineer In-charge (2890 mm x 465 mm) |  |  |  |  | 1 | Nos | 44250 | 44250 | 44250 | 0 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
56 |  |  | Providing and fixing Aluminium Extruded Section Body Tubular Type Hydraulic Door Closer (IS: 3564) with double speed adjustment with necessary accessories and screws etc. complete. Make: Haffele |  |  |  |  | 8 | Nos | 2819 | 22552 | 22552 | 0 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
57 |  |  | Supplying and fixing of windows / in open court yards using 25mm x 6mm MS flat alround and 10mm MS square bars horizontally at 125mm centre to centre and vertically at 300mm centre to centre including fixing with 4 Nos of MS Z holdfasts (2 on each side) duly making cutting brick masonry, fixing and making to original surface neatly and painting grill with one coat of red oxide primer including cost all taxes and conveyance of all materials including cutting, bending, welding including all operational charges and all labour charges etc., complete for finished item of work. (for Window Grills) |  |  |  |  | 10.8435 | Sqm | 1569 | 17013 | 17013 | 0 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
58 |  |  | AHU shed with provision for fencing, door with lock- key arrangement shall be provided with Framework vertically made of MS Square Pipe frame: 2 Inches X 2 Inches, 16Gauge M S Fencing with wire mesh: ½ inch X ½inch. Supporting Structure M S Angle: 50 X 5mm GI pre-coated corrugated profile roof sheet: 0.5 mm thick duly supported with JHook 10 SWG with provision of door with lock and key AHU Shed with fencing should be duly enamel painted and with anti-rust coating from both sides. |  |  |  |  | 1 | Iob | 300000 | 300000 | 300000 | 0 | This work is proposed as safety measure for AHU's keeping in view of temparature of outdoor and weather conditions. Technically 5° to 6° C temprature will be reduced which will decrease the power bill also. | CS
59 |  |  | Supply of Sun Control film to the glazed windows (For Windows & Door view Windows) |  |  |  |  | 14.55 | Sqm | 381 | 5544 | 5544 | 0 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | cs
[7 empty] | 668745 |  |  | PART-A | 3041177 | 2372432 | 0
PLUMBING WORKS
60 | 75 | IVF075 | Supply and fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings SDR 13.5 to meet the requirement of ASTM-D 2846 and are produced in CTS Copper Tube Sizes 1/2inches to 2inches for hot and cold water IS 15778:2007 including cost and conveyance of all materials to site, labour charges for fixing,complete for finished item of work at all floor levels. 22.20mm OD pipe at Gandhi Hospital | 75 | Rmt | 229 | 17175 | 105.4 | Rmt | 229 | 24137 | 6962 | 0 | The qty is not utilised as per site condition. Hence savings | P
Plumbing Supplemental Works
61 |  |  | Supplying and fixing of 3" (75mm) Nahany trap with jali - UPVC/SWR pipe fittings as per site requirements with standard practice for all floors including cost and conveyance of all materials to site, labour charges , overheads & contractors profit etc., complete for finished item of work. | 0 |  |  |  | 5 | Nos | 133 | 665 | 665 | 0 | This work is executed as per Site Conditions. | PS
62 |  |  | Supplying and fixing 50 mm Nominal Bore GI pipe Medium Grade properties & weight as per IS 1239 in ground or on wall with GI fittings such as elbows tees couplings, nipples, plugs including excavation for trenches and refilling the trenches ,chiselling masonry walls and making good the walls & floors to the original surface and fixing MS clamps on TW blocks on walls including cost and conveyance of all materials and labour charges , overheads & contractors profit complete for finished item of work except for GI bends union and GI connectors with checkout and socket Tata or Zenith make or equivalent. (For Autoclave) |  |  |  |  | 35.1 | Rmt | 599 | 21025 | 21025 | 0 | This work is mandatory for autoclave to let out the steam outside the premises. Hence executed. | PS
[7 empty] | 17175 |  |  | PART-A | 45827 | 28652 | 0
ELECTRICAL WORKS
63 | 96 | IVF096 | Supply and laying of ISI 25mm outer dia medium grade with IS:9537-part 3 rigid PVC pipe concealed in wall with all required PVC / Metallic Junction Boxes including masonry work and labour charges etc., Makes: Sudhakar / Precision /Universal/ Modi / Million Plast. at Gandhi Hospital | 200 | Rmt | 116 | 23200 | 415.5 | Rmt | 116 | 48198 | 24998 | 0 | Item quantiy was increased to provide and lay main circuits for Switch boards and sockets in IVF | E
64 | 97 | IVF097 | Supply and laying of ISI 25mm outer dia medium grade with IS:9537-part 3 rigid PVC pipe surface on wall with all required PVC / Metallic Junction Boxes including masonry work and labour charges etc., Makes: Sudhakar / Precision /Universal/ Modi / Million Plast. at Gandhi Hospital | 500 | Rmt | 107 | 53500 | 1060.2 | Rmt | 107 | 113441 | 59941 | 0 | Item quantiy was increased to provide and lay main circuits for Switch boards and sockets in IVF | E
65 | 98 | IVF098 | Wiring with 2 runs of 22/0.3mm 1.5 Sq.mm FRLS / HFFR P.V.C. insulated flexible copper cable ISI MARK in existing pipe with 6A Modular switch, Ceiling rose/BH/SBH Modular switches with cover plate and GI switch box including all labour charges etc., complete. for Non- Residential Building Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. Makes of switches: - GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/Gold Medal curve. at Gandhi Hospital | 110 | Pts | 945 | 103950 | 146 | Pts | 945 | 137970 | 34020 | 0 | Item quanity was increased so as to provide electrical points in corridor, wards, rooms and OT's of IVF | E
66 | 99 | IVF099 | Supply and fixing of 6A ISI Mark 3/2 pin Modular socket with 6A 1way Modular switch, 3 Module box with cover frame and GI switch box on common switch board with connections etc., complete. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. Makes of switches: - GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/Gold Medal curve. at Gandhi Hospital | 12 | No | 675 | 8100 | 30 | No | 675 | 20250 | 12150 | 0 | Item quanity was increased so as to provide common sockets to the siwtch boards in corridor, rooms, wards and OT's of IVF | E
67 | 104 | IVF104 | Supply and run of 3 of 2.5 sq.mm 36/0.3mm phase neutral and earth FRLS / HFFR PVC insulated flexible copper cable in existing conduit pipe for individual lighting circuits including labour charges etc., complete as required for switch boards. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at Gandhi Hospital | 600 | Rmt | 177 | 106200 | 637.1 | Rmt | 177 | 112767 | 6567 | 0 | Item quanity was increased so as to provide and laying of 2.5 sqmm 3 runs wire from Distribution boards to Switch boards and sockets in corridor, rooms, wards and OT's of IVF | E
68 | 105 | IVF105 | Supply and 3 runs of 4.0 sq mm 56/0.3 mm phase neutral and earth FRLS / HFFR PVC insulated flexible copper cable in existing conduit pipe including labour charges etc., complete for 16A sockets. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at Gandhi Hospital | 1200 | Rmt | 255 | 306000 | 1349.1 | Rmt | 255 | 344021 | 38021 | 0 | Item quanity was increased so as to provide and laying of 4 sqmm 3 runs wire from Distribution boards to power sockets and air consitioners points in corridor, rooms, wards and OT's of IVF | E
69 | 106 | IVF106 | Supply and run of 5 of 6.0 Sqmm 90/0.3 mm 3 phases, neutral and earth FRLS / HFFR PVC insulated flexible copper cable in the existing conduit pipe for run of mains from Power panel board to TPN DBs with pin type lugs and connections etc., complete. for LDBs Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at Gandhi Hospital | 60 | Rmt | 606 | 36360 | 333.3 | Rmt | 606 | 201980 | 165620 | 0 | Qty increased as the no. of DB's increased and the main circuits from Main VTPN to DB increased | E
70 | 107 | IVF107 | Supply and run of 5 of 10.0 Sqmm 140/0.3 mm 3 phases, neutral and earth FRLS / HFFR PVC insulated flexible copper cable in the existing conduit pipe for run of mains from Power panel board to TPN DBs with pin type lugs and connections etc., complete. for PDBs Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at Gandhi Hospital | 40 | Rmt | 967 | 38680 | 145.1 | Rmt | 967 | 140312 | 101632 | 0 | Qty increased as the no. of DB's increased and the main circuits from Main VTPN to DB increased | E
71 | 109 | IVF109 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand / Schneider and Supply and Fixing of 1 No., of 40A FP 30mA RCCB as incomer and 12 Nos 6-32 A 10kA SP MCBs Makes: Legrand-DX3 / Schneider-Acti9 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. For Lighting DBs at Gandhi Hospital | 3 | No | 18325 | 54975 | 8 | No | 18325 | 146600 | 91625 | 0 | Qty increased to accomadate all the circuits of switch board, sockets, power sockets and air condition points in the DB | E
72 | 115 | IVF115 | Supply and Transportation 36W Edge lit, 2 feet x2 feet 600mm x600mm slim panel LED luminaire Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor greater than 0.9, Surge protection greater than 2KV, System efficacy of greater than100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI greater than80, and THD is less than 15percentage etc., complete. Makes: Phillips / OSRAM / Wipro / Crompton / Bajaj / Havells At Gandhi Hospital | 30 | No | 4350 | 130500 | 40 | No | 4350 | 174000 | 43500 | 0 | Qty increased so as to provide adequate lighting in corridor, ward, Minor OT, change room, Entrance area, Reception,Andrology lab and Cryo room | E
73 | 119 | IVF119 | Supply and fixing of Modular type Stepped electronic regulator Makes : GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/ Cabtree Verna/ Million logus / Gold Medal Curve for sweep AC ceiling fans of 1200mm / 1400mm complete with connections. At Gandhi Hospital | 12 | No | 827 | 9924 | 14 | No | 827 | 11578 | 1654 | 0 | Qty increased as the no of fans executed are 14. hence 2 nos AE increased. | E
74 | 122 | IVF122 | SITC of Hot dip galvanized perforated cable tray of 300 mm Wide sizes for to run the cable from Floor Panel to Lab Panel and electrical room to AC panel and AC panel to Units. All necessary supports and accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. At Gandhi Hospital | 80 | Rmt | 1310 | 104800 | 85.4 | Rmt | 1310 | 111874 | 7074 | 0 | Qty increased as per site condition for laying of main cables over the false ceiling | E
75 | 124 | IVF124 | Supply and fixing of 12V 65 AH SMF battery including wire leads. Makes: Quanta / Racket / Exide. At Gandhi Hospital | 20 | No | 20584 | 411680 | 32 | No | 20584 | 658688 | 247008 | 0 | As the UPS with isolation transformer requires min 32 nos of batteries to increase uptime of 60 minutes from 30 minutes considering the load. hence the Qty. exceeded and proposed as AE | E
76 | 129 | IVF129 | Supply and installation of 25x3 GI flat for body earthing of DBs and Cable tray which is laid in 100mm cable tray At Gandhi Hospital | 100 | Rmt | 163 | 16300 | 168.7 | Rmt | 163 | 27498 | 11198 | 0 | Qty increased as the earthing flat is running from ground floor to 5th Floor of MCH Block. Hence quantity increased | E
77 | 131 | IVF131 | Supply and installation of 4 sqmm Copper wire for Earthing of DBs Equipment At Gandhi Hospital | 80 | Rmt | 83 | 6640 | 286 | Rmt | 83 | 23738 | 17098 | 0 | Qty increased so as to connect earthing from panel to VTPN and from VTPN to DB's | E
78 | 136 | IVF136 | Supply, Lying and testing of 4Cx4 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc. Make of Cable: Polycab/ KEI/Universal/ Glostar/Finolex. Make of gland and Lungs: HMI/Commet/Dowell’s at Gandhi Hospital | 80 | Rmt | 356 | 28480 | 125 | Rmt | 356 | 44500 | 16020 | 0 | Qty increased to provide cables to AHU 67 mts and Heater 58mts | E
Electrical Supplemental Works
79 |  |  | Supply and Transportation 56W Clean room Light fixture, 2' x2' (600mm x600mm) LED luminaire CRCA powder coated white after phosphocreatine treatment provided as standard. with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% including all accessories and labour charges etc., complete. |  |  |  |  | 12 | Nos | 17241 | 206892 | 206892 | 0 | During site inspection, EE (Electrical) has instructed to provide 56W lights to attain required illumination. Hence executed. | ES
80 |  |  | Supply and Transportation of 48" ( 1200 mm) High Speed Fan Sweep Celing Fan with all accessories etc., complete. Make Havells S S 390 |  |  |  |  | 14 | Nos | 4317 | 60438 | 60438 | 0 | The EE (Electrical) during site inspection instructed to provide regular high speed fans since maintaining BLDC fans in governement instutions is not viable. Hence executed | ES
81 |  |  | Labour charges for fixing of ceiling fan and regulator including transportation and giving connections with twin core wire etc., complete. Makes : Finolex / RR Kabel / Havells / Polycab / GM / Million / V-Guard / Gold Medal / HPL / RPG. |  |  |  |  | 14 | Nos | 185 | 2590 | 2590 | 0 | As per Instructions of EE (Electrical) during site inspection, regular high speed fans were provided. Hence executed | ES
82 |  |  | Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete |  |  |  |  | 14 | Nos | 162 | 2268 | 2268 | 0 | As difference in false ceilling one meter down rods are used as per site conditions | ES
83 |  |  | Supply & fixing of 2nos6A, 2 in one socket - 2 Nos with 6A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benz Plus |  |  |  |  | 30 | Nos | 1178 | 35340 | 35340 | 0 | 6Amp socket was required as per site conditions. Hence executed | ES
84 |  |  | Supply,Transportation of 15" (375mm) ISI, 900 RPM Heavy duty exhaust fan with metallic blades wiremesh with all accessories etc complete Makes : Crompton / Almonard / Havells Turbo Force SP. |  |  |  |  | 1 | Nos | 4310 | 4310 | 4310 | 0 | It is essential to provide heavy duty exhaust fan in Autoclave room. Hence executed | ES
85 |  |  | Labour charges for fixing the exhaust fan in wall with necessary connections and masonary work of making hole, finishing etc., complete. Makes : Finolex / Havells / Polycab / Finecab |  |  |  |  | 1 | Nos | 788 | 788 | 788 | 0 | As it is mandatory in Autoclave room hence executed | ES
86 |  |  | Supply and fixing of 12 Way SPN DB with IP 43 Protection as per IS:13032 with 1 No 63A FP MCB as Incommer, and 8 Nos of 6-32A SP MCB 10KA, C/D Curve ISI Mark as out goings, concealing in wall etc complete. DB Makes :Legrand MCB Makes : Legrand-DX3 |  |  |  |  | 1 | No | 9444 | 9444 | 9444 | 0 | It is mandatory to provide 12 Way SPN DB for UPS. Hence executed | ES
87 |  |  | Supply and fixing of cable adapteres box with cover for DBs including, massanory work etc., complete., |  |  |  |  | 8 | Nos | 5085 | 40680 | 40680 | 0 | It is mandatory to provide cable adapters to connect RAW power with UPS power. Hence executed | ES
88 |  |  | Supply and Installation of control cum transmission wiring of size 4C x 2.5 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing and accessories as At Gandhi Hospital |  |  |  |  | 20 | Rmt | 289 | 5780 | 5780 | 0 | It is mandatory required for VRV Sysytem | ES
89 |  |  | Supply and Installation of control cum transmission wiring of size 2C x 1.5 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing and accessories as At Gandhi Hospital Makes : Polycab |  |  |  |  | 190 | Rmt | 173 | 32870 | 32870 | 0 | It is mandatory required for VRV System | ES
90 |  |  | 4C x 1.5 Sqmm Copper Flexible Cable For Condensing Unit to Electrical Panel Makes : Polycab |  |  |  |  | 74.1 | Rmt | 130 | 9633 | 9633 | 0 | It is mandatory required for AHU's connection System | ES
91 |  |  | Supply and fixing of FP Metal Enclosure with IP 20 Protection DB Make with 1 No 63A, 10 KA FP MCB including internal connection and labour charges for Flush Mounting etc.,complete. Makes of Enclousure : Legrand MCB Makes : Legrand-DX3 |  |  |  |  | 1 | Nos | 4203 | 4203 | 4203 | 0 | It is mandatory required to connect Powre supply to autoclave | ES
92 |  |  | POINT WIRING and LIGHT FIXTURES & FITTINGS Providing Point wiring for Light Concealed Type with 2 x 1.0 Sq.mm. Copper. PVC Insulated wire 1.1 KV grade ISI marked in rigid ISI mark PVC conduit minimum 20mm (1.6 mm thick) dia. with necessary accessories and Pannel and Spot LED lights of Havells/Wipro company. |  |  |  |  | 13 | Nos | 1200 | 15600 | 15600 | 0 | work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | ES
93 |  |  | Proving and fixing Profile lights at wpc Louvers |  |  |  |  | 10.66 | Rmt | 1182 | 12600.12 | 12600.12 | 0 | work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | ES
94 |  |  | Proving and fixing Track lights at side wall décor frame with 4 fixtures and 2 tracks |  |  |  |  | 1 | Job | 9600 | 9600 | 9600 | 0 | work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | ES
95 |  |  | External Profile light at Name Plate |  |  |  |  | 2.89 | Rmt | 1182 | 3415.98 | 3415.98 | 0 | work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | ES
[7 empty] | 1439289 |  |  | PART-A | 2773867.1 | 1334578.1 | 0
Fire Fighting Supplimental Works
96 |  |  | Supply, Installation, testing and commissioning of EN54-2 Listed and LPCB approved based analog addressable fire control panel expandable by minimum 2 additional loops with minimum 80 character LCD display 4 access levels 1000 events, historical logging, flash E-PROM, 240 volts A C Power supply, automatic battery charger, 24V SLA batteries suitable for operating the entire system including tack back units and the hooters / strobes for a minimum of 4 hours in battery condition the panel shall have suitable power amplifiers for hooter / strobes the panel shall be capable beeing integrated with the BMS system and shall include cost of supply, installation of any additional modules or interfaces required for the same. The panel shall be completed as per the specification and as required for fixing of above Micro processor based Fire Alarm control panel with zonal indictions and battery back up as per detailed specifications. Makes: Ravel |  | Nos |  |  | 1 | Nos | 291366 | 291366 | 291366 | 0 | It is necessary to monitor fire alaram detectors in case of emergency. This work is executed as per the instructions of TSMSIDC Higher officials | FFS
[7 empty] | 0 |  |  | PART-A | 291366 | 291366 | 0
Air Conditioning Works
97 | 149 | IVF149 | Supply, transportation and installation of split AC unit 1.5 TR inverter type 3 Star capable of delivering 18000 BTU/hr and above with high wall mounted indoor unit and outdoor condensing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord , built-in stabilizer Voltage range 160- 264 volts and cordless remote control. Makes : Daikin / Thoshiba / O General at Gandhi Hospital | 1 | No | 48000 | 48000 | 2 | No | 48000 | 96000 | 48000 | 0 | Qty increased so as to provide AC in UPS room and Andrology lab | AC
98 | 153 | IVF153 | SITC of air cooled condensing units with two scroll compressors, air cooled condenser, power panel, vibration isolating pads, stand for ODU, thermostat, etc. of the following capacities. The nominal capacity of the condensing unit shall be as under. Air cooled condensing unit shall have horizontal discharge. All refrigerant piping accessories sight glass, drier, expansion valve, etc. shall be supplied with the condensing units and suitable to connect above AHUs. Refrigerant shall be R 407C / R 410A. Necessary thermostat, control wiring, etc. shall be included. Derating of the unit shall not be more than 15percentage under 45 deg. C ambient temperature. Condensing unit shall be capable of operating up 50 deg. C ambient temperature. 8.5 TR capacity At Gandhi Hospital | 1 | No | 182000 | 182000 | 2 | No | 182000 | 364000 | 182000 | 0 | Qty increased as one AHU unit has been placed for Backup to IVF center | AC
99 | 163 | IVF163 | SITC of SS perforated return raiser grilles with 10 microns filters with collar dampers At Gandhi Hospital | 2 | Sqm | 26300 | 52600 | 3.29 | Sqm | 26300 | 86527 | 33927 | 0 | Qty increased as per site condition | AC
100 | 164 | IVF164 | Extruded Al. powder coated EXHAUST / RETURN discrete grilles At Gandhi Hospital | 1 | Sqm | 8125 | 8125 | 1.25 | Sqm | 8125 | 10156 | 2031 | 0 | Qty increased as per site condition | AC
101 | 166 | IVF166 | SITC of Magnehelic gauges across pre and fine filter at AHUs including mounting arrangement, SS nozzles, food grade PVC tubing, etc. At Gandhi Hospital | 2 | No | 10500 | 21000 | 3 | No | 10500 | 31500 | 10500 | 0 | Qty increased as per site condition | AC
102 | 171 | IVF171 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Supply air duct running inside the building. at Gandhi Hospital | 40 | Sqm | 785 | 31400 | 75.04 | Sqm | 785 | 58906 | 27506 | 0 | Qty increased so as to provide proper covering from Dampness and moisture to copper pipe of IVF units and AHU units | AC
103 | 176 | IVF176 | VRF Indoor Units : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.5 TR At Gandhi Hospital | 4 | No | 35000 | 140000 | 5 | No | 35000 | 175000 | 35000 | 0 | Qty increased to provide 1 no VRF AC in UPS Room | AC
104 | 179 | IVF179 | Supply, Installation , Testing and Commissioning of Refnet joints to be provided in refrigerant pipe line. Material of construction for fittings shall be similar to refrigerant piping. At Gandhi Hospital | 10 | Set | 6191 | 61910 | 11 | Set | 6191 | 68101 | 6191 | 0 | Qty increased as per site condition | AC
105 | 180 | IVF180 | Supply and Installation of control cum transmission wiring of size 3C x 1.5 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing and accessories as At Gandhi Hospital | 150 | Rmt | 320 | 48000 | 165 | Rmt | 320 | 52800 | 4800 | 0 | Qty increased as per site condition | AC
106 | 181 | IVF181 | Supply and Installation of cabling of size 2C x 1 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing and accessories as per the approved routing. At Gandhi Hospital | 100 | Rmt | 255 | 25500 | 120 | Rmt | 255 | 30600 | 5100 | 0 | As per the site requirement, Qty. exceeded and hence proposed as AE | AC
Air Conditioning Supplimental Works
107 |  |  | Supply and installation of 2.2 TR 3 Star capable of delivering 21600 BTU/hr and above with operating on refrigerant R-32 / R-410 with condeser stand, layoing copper pipe of 15mm size of length 15 mt including Nitrile rubber insulation connected with 2.5 sqm x 4 core cable for power supply and equipped with drain pump. Makes : Daikin / Toshibha / Carrier / BlueStar / Hitachi or equivalent |  |  |  |  | 1 | Nos | 72225 | 72225 | 72225 | 0 | The item is provided in the reception area as per the instructions issued by the End user and TSMSIDC higher officials. Hence executed | ACS
108 |  |  | SITC of CPVC drain piping with supports, clamps of the following size. 25mm Dia at Gandhi Hospital |  |  |  |  | 66 | Rmt | 200 | 13200 | 13200 | 0 | This work is executed as contingency work to the above 2.2 TR AC. | ACS
109 |  |  | Supply & Installation of MS Angle for Duct Support, Cable Tray Support and Condensing Unit Stand of size 40 X 40 x 5 mm Thick. |  |  |  |  | 92.2 | Kg | 190 | 17518 | 17518 | 0 | It is mandatorly required for support duct hence this work is executed as per the instructions of TSMSIDC Higher officials. | ACS
110 |  |  | Supply & Installation of MS Angle for Duct Support, Cable Tray Support and Condensing Unit Stand of size 25 X 25 x 5 mm Thick. |  |  |  |  | 25.5 | Kg | 190 | 4845 | 4845 | 0 | It is mandatorily required to support the duct & cable tray. Hence this work is executed as per the instructions of TSMSIDC Higher officials. | ACS
111 |  |  | Supply and installation of Canvas Connections For AHUS |  |  |  |  | 2 | Nos | 6500 | 13000 | 13000 | 0 | Its mandatorly required for support duct hence this work is executed as per the instructions of TSMSIDC Higher officials. | ACS
[7 empty] | 618535 |  |  | PART-A | 1094378 | 475843 | 0
MGPS WORKs
112 | 183 | IVF183 | SITC of Oxygen Outlets with matching probes, as per HTM-2022/02-01 of UK/NFPA99C of USA as per enclosed technical specifications - Imported At Gandhi Hospital | 4 | each | 2506 | 10024 | 6 | each | 2506 | 15036 | 5012 | 0 | Qty. increased as per the site requirement hence proposed as AE | G
113 | 184 | IVF184 | SITC of Oxygen Flow meter with Humidifier, CE Certified with four digit number as per enclosed technical specifications - Imported At Gandhi Hospital | 4 | each | 1805 | 7220 | 6 | each | 1805 | 10830 | 3610 | 0 | Qty. increased as per the site requirement hence proposed as AE | G
114 | 187 | IVF187 | SITC of C02 Manifold for 2 Cylinders, with high pressure Regulator, NRV, tailpipes etc. as per technical specifications At Gandhi Hospital | 1 | Set | 20750 | 20750 | 2 | Set | 20750 | 41500 | 20750 | 0 | Additional Manifold is provided to supply CO2 at 2-3 bar pressure to IVF OT. | G
115 | 188 | IVF188 | SITC of C02 Outlets with matching probes, as per HTM-2022102- 01ofUK/NFPA99C of USA as per enclosed technical specifications - Imported At Gandhi Hospital | 4 | each | 2506 | 10024 | 6 | each | 2506 | 15036 | 5012 | 0 | Qty. increased as per the site requirement hence proposed as AE | G
116 | 189 | IVF189 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 12mm COPPER PIPE at Gandhi Hospital | 24 | Rmt | 642 | 15408 | 38.3 | Rmt | 642 | 24589 | 9181 | 0 | Qty. increased as per the site requirement hence proposed as AE | G
117 | 190 | IVF190 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 15mm COPPER PIPE at Gandhi Hospital | 114 | Rmt | 824 | 93936 | 157.7 | Rmt | 824 | 129945 | 36009 | 0 | Qty. increased as per the site requirement hence proposed as AE | G
118 | 191 | IVF191 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 22mm COPPER PIPE at Gandhi Hospital | 36 | Rmt | 1191 | 42876 | 79.5 | Rmt | 1191 | 94685 | 51809 | 0 | Qty. increased as per the site requirement hence proposed as AE | G
119 | 192 | IVF192 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 28mm COPPER PIPE at Gandhi Hospital | 18 | Rmt | 1473 | 26514 | 27 | Rmt | 1473 | 39771 | 13257 | 0 | Qty. increased as per the site requirement hence proposed as AE | G
120 | 195 | IVF195 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 15mm 0D at Gandhi Hospital | 3 | each | 1938 | 5814 | 8 | each | 1938 | 15504 | 9690 | 0 | Qty. increased as per the site requirement hence proposed as AE | G
MGPS Supplemental Works
121 |  |  | Fully Automatic Control Panel for Oxygen System: Supply, installation and commissioning of Fully Automatic control panel for unintrupted Oxygen supply | 0 | Set |  |  | 1 | Set | 175180 | 175180 | 175180 | 0 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
122 |  |  | Trigas Emergency Manifold: SITC of Emergency Trigas Manifold maximum for 1+1 D-type Gas Cylinders complete with separate NRVs, tail pipes and brass fittings for each cylinders. | 0 | Set |  |  | 1 | Set | 9620 | 9620 | 9620 | 0 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user. | GS
123 |  |  | Fully Automatic Control Panel for Trigas System: Supply, installation and commissioning of Fully Automatic control panel for unintrupted Nirous Oxide supply. | 0 | Set |  |  | 1 | Set | 175180 | 175180 | 175180 | 0 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user. | GS
124 |  |  | Fully Automatic Control Panel for CO2 System: Supply, installation and commissioning of Fully Automatic control panel for unintrupted Nirous Oxide supply. | 0 | Set |  |  | 1 | Set | 175180 | 175180 | 175180 | 0 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user. | GS
125 |  |  | SITC of Medical Air-4 Outlet with matching probe as per HTM-2022/02-01 of UK/ NFPA 99C of USA as per enclosed technical Specification. | 0 | Nos |  |  | 6 | Nos | 12470 | 74820 | 74820 | 0 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user. | GS
126 |  |  | 12 mm Valve for 12 mm OD Pipe Note: New item added | 0 | Nos. |  |  | 3 | Nos. | 930 | 2790 | 2790 | 0 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user. | GS
127 |  |  | Supply and installation of 46.7 liter size CO2 cylinders confirming to IS:7285 Part-2 (2017). The cylinder shall have an outer diameter of 232mm, a nominal length of 1365mm, and a minimum wall thickness of 5.3mm, ensuring robustness and safety during handling and storage. The cylinders shall have a capacity of 46.7 liters and comply with the standards set forth by the Indian Standards Institute. They shall be constructed from high-quality 37 Mn (Carbon Manganese) material, guaranteeing durability and reliability. The design shall feature a concave bottom and neck threading conforming to IS 3224:2002 14 TPI Type 4 - Size 2 specifications, facilitating secure connections and ease of use. The cylinder shall be capable of withstanding a test pressure of 250 BAR and have a working pressure of 150 BAR. The nominal tare weight of each cylinder shall be 51 kg. The cylinder includes first fill. | 0 | Nos. |  |  | 2 | Nos | 20850 | 41700 | 41700 | 0 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user. | GS
128 |  |  | Supply and installation of 46.7 liter size O2 cylinders confirming to IS:7285 Part-2 (2017). The cylinder shall have an outer diameter of 232mm, a nominal length of 1365mm, and a minimum wall thickness of 5.3mm, ensuring robustness and safety during handling and storage. The cylinders shall have a capacity of 46.7 liters and comply with the standards set forth by the Indian Standards Institute. They shall be constructed from high-quality 37 Mn (Carbon Manganese) material, guaranteeing durability and reliability. The design shall feature a concave bottom and neck threading conforming to IS 3224:2002 14 TPI Type 4 - Size 2 specifications, facilitating secure connections and ease of use. The cylinder shall be capable of withstanding a test pressure of 250 BAR and have a working pressure of 150 BAR. The nominal tare weight of each cylinder shall be 51 kg. The cylinder includes first fill. | 0 | Nos. |  |  | 2 | Nos | 17850 | 35700 | 35700 | 0 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user. | GS
129 |  |  | Supply and installation of 46.7 liter size Trigas cylinders confirming to IS:7285 Part-2 (2017). The cylinder shall have an outer diameter of 232mm, a nominal length of 1365mm, and a minimum wall thickness of 5.3mm, ensuring robustness and safety during handling and storage. The cylinders shall have a capacity of 46.7 liters and comply with the standards set forth by the Indian Standards Institute. They shall be constructed from high-quality 37 Mn (Carbon Manganese) material, guaranteeing durability and reliability. The design shall feature a concave bottom and neck threading conforming to IS 3224:2002 14 TPI Type 4 - Size 2 specifications, facilitating secure connections and ease of use. The cylinder shall be capable of withstanding a test pressure of 250 BAR and have a working pressure of 150 BAR. The nominal tare weight of each cylinder shall be 51 kg. The cylinder includes first fill. | 0 | Nos. |  |  | 2 | Nos | 29250 | 58500 | 58500 | 0 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user. | GS
130 |  |  | Supply and installation of 46.7 liter size N2O cylinders confirming to IS:7285 Part-2 (2017). The cylinder shall have an outer diameter of 232mm, a nominal length of 1365mm, and a minimum wall thickness of 5.3mm, ensuring robustness and safety during handling and storage. The cylinders shall have a capacity of 46.7 liters and comply with the standards set forth by the Indian Standards Institute. They shall be constructed from high-quality 37 Mn (Carbon Manganese) material, guaranteeing durability and reliability. The design shall feature a concave bottom and neck threading conforming to IS 3224:2002 14 TPI Type 4 - Size 2 specifications, facilitating secure connections and ease of use. The cylinder shall be capable of withstanding a test pressure of 250 BAR and have a working pressure of 150 BAR. The nominal tare weight of each cylinder shall be 51 kg. The cylinder includes first fill. | 0 | Nos. |  |  | 2 | Nos | 33000 | 66000 | 66000 | 0 | This work is executed as per the Necessity of medical gases in IVF Center under the instructions of Enduser letter enclosed | GS
[7 empty] | 232566 |  |  | PART-A | 1201566 | 969000 | 0
[6 empty] | TOTAL (PART-A) | 2976310 |  |  |  | 9379481.1 | 6403171.1 | 0
EQUIPMENT
131 | 38 | IVF038 | Reception Table at Gandhi Hospital | 1 | No | 110000 | 110000 | 0 | No | 110000 | 0 | 0 | 110000 | This item was not executed as it was requested by the higher officials to provide granite reception table instead of this item. Hence savings. | EQP
[7 empty] | 110000 |  |  |  | 0 | 0 | 110000
CIVIL WORKS
132 | 49 | IVF049 | Dismantling, clearing away and carefully stacking useful materials for re- use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges, etc., complete. Brick Masonry at Gandhi Hospital | 110 | Cum | 398 | 43780 | 32.677 | Cum | 398 | 13005 | 0 | 30775 | The qty is utilised as per site condition and hence savings | C
133 | 50 | IVF050 | Dismantling doors, windows and clear storey windows, Ventilators etc., wood or steel shutters including Chowkhats, architraves, hold fasts and other attachments etc., and stacking them within 100m lead including labour charge etc., and complete for finished item of work. Not exceeding 3 sqm in area: Doors 1.00x2.60M at Gandhi Hospital | 16 | No | 350 | 5600 | 0 | No | 350 | 0 | 0 | 5600 | The qty is utilised as per site condition and hence savings | C
134 | 52 | IVF052 | Conveyance of un-useful excavated earth to a distance of 21 KM for disposal including hire charges of T and P, labour charges etc., complete for finished item of work. Dismantled Brick masonry at Gandhi Hospital | 110 | Cum | 454 | 49940 | 48.7 | Cum | 454 | 22110 | 0 | 27830 | The qty is utilised as per site condition and hence savings | C
135 | 54 | IVF054 | Reinforced Masonry for partition walls 100 mm thick in CM 1:4 prop. Aerated Cellular Autoclaved Concrete Blocks conforming to IS:2185 Part-3- 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600 x 200 x 100 mm and placing 2Nos. of 6mm M.S plain rods in every third layer with free ends of the reinforcement pegged into mortar joints of main brick walls where applicable including cost and conveyance of all materials like cement, steel, sans, brick, water etc., to site, including sales and other taxes excluding GST on all materials, all operational, incidents charges, constructing masonry, lift charges, curing, complete for finished item of work. TSSS No. of 509.5th Floor at Gandhi Hospital | 395 | Sqm | 1952 | 771040 | 191.03 | Sqm | 1952 | 372891 | 0 | 398149 | The qty is utilised as per site condition and hence savings | C
136 | 55 | IVF055 | Providing Mild steel MS steel bars Fe 250 grade as per IS 432 of different diameters including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying including sales and other taxes on all materials etc. , complete for finished item of work. TSSS No.126 For RBM walls 6mm dia: 5th Floor at Gandhi Hospital | 2.15 | MT | 116500 | 250475 | 0.103 | MT | 116500 | 12000 | 0 | 238475 | The qty is utilised as per site condition and hence savings | C
137 | 56 | IVF056 | Plastering 20mm thick in two coats using screened sand with base coat of 16mm thick in CM1:6 and top coat of 4mm thick in CM1:4 with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales and other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., complete for finished item of work .SS 901,903and 904 5th Floor at Gandhi Hospital | 45 | Sqm | 1077 | 48465 | 11.04 | Sqm | 1077 | 11890 | 0 | 36575 | The qty is utilised as per site condition and hence savings | C
138 | 57 | IVF057 | Plastering 12mm thick in two coats using screened sand with base coat of 8mm thick in CM 1:6 and top coat of 4mm thick in CM 1:4 with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales and other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and complete for finished item of work. SS 901,903 and 904. 5th Floor at Gandhi Hospital | 905 | Sqm | 1041 | 942105 | 547.15 | Sqm | 1041 | 569583 | 0 | 372522 | The qty is utilised as per site condition and hence savings | C
139 | 58 | IVF058 | Supply and Installing change room Cubicles, at Gandhi Hospital. GENERALSPECIFICATIONS: Thickness of Compact Laminate: 12 mm Thick Colour of HPL Boards: In Single Colour, Size of Cubicle : As per DWG, Door Size for Normal Cubicle : As per DWG, Overall Height Of Cubicle : 2105 mm Including bottom gap of 100mm, Accessories: Manufacturers standard makes of Aluminium, SS Accessories. a Aluminium H Top Rail b SS Hinges c SS Privacy Thumb turn c/w Occupancy Indicator d SS Coat Hook e SS Door Knob f Aluminium U channel g Aluminium Door Stopper channel h Rubber Lining i SS Screws and PVC Wall Plugs | 19.5 | Sqm | 9055 | 176573 | 16.83 | Sqm | 9055 | 152396 | 0 | 24177 | The qty is utilised as per site condition and hence savings | C
140 | 59 | IVF059 | Providing and laying screed plain cement concrete as per site condition for floor bedding using high quality aggregates including base preparation, compaction, levelling, all lead and lifts, rough finishing at the top surface, curing, shuttering if necessary etc., complete as directed . at Gandhi Hospital | 25 | Cum | 4700 | 117500 | 0 | Cum | 4700 | 0 | 0 | 117500 | The qty is utilised as per site condition and hence savings | C
141 | 60 | IVF060 | Supply and fixing powder coated aluminium fully glazed swing door as per the approved drawing with fixed fan light of 500mm height at top door using aluminium sections of 101.60 mm x44.45mm , 3.18 mm thick for frame and door shutter made of styles , top and middle rail of 47.62mm x 44.45mm, 3.18 mm thick and bottom rail of 96.00mm x 44.45 mm,3.18mm thick, powder coating of aluminium sections 25mm microns thick, 5 mm thick plain glass fitted with suitable aluminium glazing clips and rubber beading in fan light portion, double shutters fitted with 5mm thick frosted glass in the top half and 12mm thick Prelaminated particle board One side choice colour and other side balancing white lamination in the bottom half fitted with suitable aluminium glazing clips and rubber beading, as approved by Engineer-in-Charge including supply and fixing ISI marked powder coated aluminium fixtures of 2 Nos. tower bolts 10mm bolt IS:204 300mm long, 4 Nos. aluminium handles IS:208 150mm dia and 1 Nos. aldrops IS:2681 250mm, 1 No. door closure, Al. Butt hinges 125mm long 6Nos including labour charges for manufacturing door , fixing the door with required No. of screws etc., complete for finished item of work. The Aluminium section used shall be standard make confirming to IS 1948-1961 and as approved by the Engineer 1200mmx2100mm at Gandhi Hospital | 5 | Sqm | 13713 | 68565 | 0 | Sqm | 13713 | 0 | 0 | 68565 | As per the instructions issued during site visit Dt. 01.08.2023. ABS doors were proposed hence qty not utilised | C
142 | 61 | IVF061 | Supplying and fixing of Unplasticised Poly Vinyl Chloride UPVC 3 track sliding windows with mesh shutter – 2-glass shutters and 1-mesh shutter duly manufactured using UPVC reinforced profiles Composition of profile shall consists a minimum of 5.5 PHR of TiO2 and not more than 12 PHR of CaCo3 for every 100 parts of PVC resin of 94mm x 45 mm/80 mm x 52 mm x 2.20 mm for outer frames, 58 mm x 39 mm/54 mm x 38 mm x 2.20mm for sliding shutter frames capable of mounting single glazing system structurally reinforced with hot dip galvanized up to 50 microns of minimum thickness of 1.0/1.2 mm prefabricated and welded through fusion welding. The window sash shall be fitted with 5 mm thick clear float glass of reputed make and mesh shutter frame shall be 42 mm x 25mm/52 mm x 21.5 mm x 2.0 mm fitted with Vinyl Coated Fiber mesh- on rollers/ pulley duly fixed with Grey colour TPV Gasket for sash and Glazing bead shall be co- extruded with Grey colour soft PVC. System shall have single point locking with Touch Lock and the system is to be installed at the site using anchor fasteners, silicon rubber sealant, easy glazing/deglazing at site etc., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site includingetc., complete for finished item of work. at Gandhi Hospital | 15 | Sqm | 9517 | 142755 | 7.88 | Sqm | 9517 | 74994 | 0 | 67761 | The qty is utilised as per site condition and approved layouts hence savings. | C
143 | 62 | IVF062 | Providing, supplying and fixing of Fixed Louvered Ventilator made out of multi chambered uPVC sections with Glazing bead shall be co-extruded with Grey colour soft PVC. having isolated drainage and reinforced with Galvanized Iron profiles throughout the window. The outer frame having an overall size of 60 mm x 55 mm x 2.40 with reinforcement of 1 mm thickness and Mullion with overall size of 74 mm x 60 mm x 2.40 mm with reinforcement of 1 mm thickness. Composition of profile shall consists a minimum of 5.5 PHR of TiO2 and not more than 12 PHR of CaCo3 for every 100 parts of PVC resin. Ventilator shall be provided with 4.5 mm Pin Head glass, standard hardware. Wall thickness of frame and Mullion shall be 2.4 mm., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site etc., complete for finished item of work hinges IS:205 150mm long, 1 No. aldrop IS:2681 300mm long, 1 No. tower bolt IS:204 of 200 mm x 10 mm dia at top, 2 Nos. 150 mm at Gandhi Hospital | 5 | Sqm | 8564 | 42820 | 1.53 | Sqm | 8564 | 13103 | 0 | 29717 | The qty is utilised as per site condition and hence savings.part of the qty is executed by other agency before handing over of site. | C
144 | 63 | IVF063 | Supply and fixing doors as per drawings with medium teak wood frame of section 100mm x 65 mm and ISI marked flush door shutters of 30 mm thick single shutter with bond wood solid block board type Core having cross bands and face veneers, hot pressed bonded with water proof phenol formaldehyde synthetic resin factory made conforming to IS 2202-1991 Part- I both sides commercial ply with internal lipping on all sides including cost and conveyance to site of teak wood frame, flush shutter including supply and fixing 6 Nos. MS Z hold fasts of size 300 mm x 40 mm x 5mm including cost of ISI marked Aluminium fixtures of 3 Nos. butt long handles IS:208, 1 No. door stopper and 1 No. rubber bush including fixing the fixtures to door with required number of screws, bolt and nuts including labour charges for fixing the frame in position, fixing the shutter to the frame etc., complete for finished item of work as per APSS 1001 and 1002 The vertical frame of door shall be embedded in flooring for a depth of not less than 10 mm 1000mm x 2100mm at Gandhi Hospital | 30 | Sqm | 5593 | 167790 | 0 | Sqm | 5593 | 0 | 0 | 167790 | As per the instructions issued during site visit Dt. 01.08.2023. ABS doors were proposed hence qty not utilised | C
145 | 64 | IVF064 | Supply and fixing doors as per drawings with medium teak wood frame of section 100mm x 65mm and ISI marked flush door shutter of 30mm thick single shutter with bond wood solid block board type Core having cross bands and face veneers, hot pressed bonded with water proof phenol formaldehyde synthetic resin factory made conforming to IS 2202-1991 Part- I both sides commercial ply with internal lipping on all sides including cost and conveyance to site of medium teak wood door frame, flush shutter, including suply and fixing 6 Nos. MS Z hold fasts of size 300mm x 40mm x 5mm including ISI marked Aluminium fixtures 3 Nos. butt hinges IS:205 of 150mm long, 1 No. aldrop IS:2681 250 mm long, 1 No. tower bolt IS:204 of 150 mm x 10mm dia, 2 Nos. 125mm long handles IS:208,1 No. rubber bush including supplying and fixing 1.20mm thick PVC sheet to full height of the shutter inside including labour charges for fixing the frame in position, fixing the shutter to the frame etc., complete for finished item of work as per APSS 1001 and 1002. The vertical frame of door shall be embedded in flooring for depth of not less than 10mm 750mm x 2100mm. at Gandhi Hospital | 12 | Sqm | 6510 | 78120 | 0 | Sqm | 6510 | 0 | 0 | 78120 | As per the instructions issued during site visit Dt. 01.08.2023. WPC doors were proposed instead of wooden doors. Hence savings | C
146 | 66 | IVF066 | Flooring with non-skid full body ceramic floor tiles of size 300mm x 300mm and thickness between 7 - 8mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630 Part 1 to 15 of any colour and finish in all shades and designs as approved by Engineer-in-charge, set over base coat of cement mortar 1:8, 12mm thick using screened sand over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread at the rate 3.3 Kgs per Sqm and jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, screened sand , water and tiles etc., complete for finished item of work. TSSS No.701 and 707 at Gandhi Hospital | 15 | Sqm | 1525 | 22875 | 14.62 | Sqm | 1525 | 22296 | 0 | 579 | The qty is utilised as per site condition and hence savings | C
147 | 67 | IVF067 | Providing and fixing in true horizontal level 14 mm - Mineral Fiber sheet 595 x 595 Square / Tegular Fissura fine model edge tiles with a Humidity Resistance of 90percentage RH, Average NRC 0.50, Light Reflectance greater than80percentage, Thermal Conductivity equal to 0.052 to 0.057 w/mk, Fire Performance Class 0/Class 1 using hot dipped Galvanized Steel section exposed surface with pre-coated capping, main Tee of size 24 x 32 mm at every 1200 mm c/c maximum and rotary stitched cross tee of size 24 x 27 mm at every 600 mm c/c and sub-cross tee of size 24 mm x 25 mm at 1200 mm c/c and wall angle of size 19 x 19 mm fixed to periphery of the wall and the above grid is suspended at every 1200 mm c/c in both directions using 2.0 mm thick pre-straightened GI Wire including cost and conveyance of all materials and labour charges such as cutting , fixing of standing of frame work exposing roof making etc., complete for finished item of work in 5th floor. at Gandhi Hospital | 375 | Sqm | 1636 | 613500 | 316.08 | Sqm | 1636 | 517107 | 0 | 96393 | The qty is utilised as per site condition and hence savings | C
148 | 69 | IVF069 | Providing and applying Wall putty of White Cement or Polymer or Cement based of average 1 to 2 mm thickness over plastered surface to prepare the surface even and smooth after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, applying emery paper, Sand the surface, clean and wipe off loose dust, applying knifing paste filler by putty knife / muslin pad, air dry for 2 - 3 hrs, sand with 180 and 320 No., emery paper for the surface preparation including cost and conveyance of all materials to work site and all operational, incidental, labour charges, over heads and etc., complete for finished item of work in 5th floor Internal walls. at Gandhi Hospital | 1050 | Sqm | 315 | 330750 | 1007.4 | Sqm | 315 | 317331 | 0 | 13419 | The qty is utilised as per site condition and hence savings | C
149 | 70 | IVF070 | Painting to new wood work and flush shutters with lappam finish, over a primary coat and painting two coats of synthetic enamel paint Grade-II VOC Volatile Organic Compound content less than 50 grams/litre of approved shade including cost and conveyance of all materials to site cost of primer coat and all labour charges etc. complete including applying sand paper on lappam coats for neat finish including sales and other taxes on cost of all materials etc., complete in all floors APSS No.1200, 1207 and 1211. at Gandhi Hospital | 80 | Sqm | 281 | 22480 | 0 | Sqm | 281 | 0 | 0 | 22480 | In view of Sterility, wood work was not executed. Hence savings | C
150 | 71 | IVF071 | Supply and application of one coat water based cement primer of interior grade I and two coats of water based PU paint having anti-bacterial applications content less than 50 grams/litre for internal walls including cost and conveyance of all materials to site, sales and other taxes, incidental, operational and all labour charges etc., and complete for finished item of work in 5th floor. at Gandhi Hospital | 1050 | Sqm | 260 | 273000 | 872.13 | Sqm | 260 | 226754 | 0 | 46246 | The item executed as per site conditions. Hence Savings. | C
151 | 72 | IVF072 | Painting to old walls with 2 coats of water proof cement paint of shade as approved by the Engineer-In-Charge to give an even shade after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, scaffolding charges, incidental, labour charges etc., and overheads and contractors profit complete for finished item of work as per SS 912 in 5th floor. at Gandhi Hospital | 150 | Sqm | 229 | 34350 | 0 | Sqm | 229 | 0 | 0 | 34350 | The qty is not utilised as per site condition hence savings | C
152 | 87 | IVF087 | Supply and installation of 80mm thick double skin modular wall Panels made of 0.8 mm thick powder coated GI on both the sides, with 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, flush on both sides with maximum allowable gap of 3- 4mm filled with food grade silicon sealant and placed on cold rolled galvanised bottom tracks with a recess to provide floor to wall coving flush with the wall panel. This includes all required harware for completion Panels to be covered with a protective film to avoid any damages during transportation and installation at Gandhi Hospital | 125 | sqm | 5620 | 702500 | 96.75 | sqm | 5620 | 543735 | 0 | 158765 | The qty is utilised as per site condition and approved floor plans. hence savings. | C
153 | 88 | IVF088 | Supply and installation of 50mm thick double skin ceiling system made of 0.8 mm thick Powder Coated GI sheets on both sides, 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, panels flush towards room side with maximum allowable gap of 3-4mm at panel to panel joints filled with silicon sealant. Ceiling panels are suspended from the RCC slab by using concealed AL ceiling grid with tie rod and adjustable turn buckle arrangement etc. This includes all required hardware for completion. Panels to be covered with a protective film to avoid any damages during transportation and installation at Gandhi Hospital | 65 | sqm | 5135 | 333775 | 48.02 | sqm | 5135 | 246583 | 0 | 87192 | The qty is utilised as per site condition and approved floor plans. hence savings. | C
154 | 92 | IVF092 | Supply and installation of Extruded Aluminium Coving at Gandhi Hospital | 120 | Rmt | 585 | 70200 | 63.61 | Rmt | 585 | 37212 | 0 | 32988 | The qty is utilised as per approved layout and hence savings | C
155 | 93 | IVF093 | Providing, laying of scratch proof PVC/Vinyl flooring of 2mm thickness with proper welded joints air tight, along with leveling compound to match the existing flooring levels as per engineer in charge instructions. Sub floor preparation with self leveling compound. After the sub floor preparation, it should be suitable for ESD flooring. Rate inclusive of sifting of material and labour charges. at Gandhi Hospital | 155 | Sqm | 4070 | 630850 | 124.84 | Sqm | 4070 | 508099 | 0 | 122751 | The qty is utilised as per approved layout and hence savings | C
[7 empty] | 5939808 |  |  |  | 3661089 | 0 | 2278719
|  |  | PLUMBING WORKS | [14 empty] | #REF!
156 | 73 | IVF073 | Supplying and fixing 15 mm brass body CP finish bib tap of not less than 300 grams weight screw type full turn with internal/external threaded connection conforming to IS 8931 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, overheads and contractors profit complete for finished item of work in all floors. at Gandhi Hospital | 5 | No | 881 | 4405 | 1 | No | 881 | 881 | 0 | 3524 | The qty is utilised as per site condition and hence savings | P |  | 0.63
157 | 74 | IVF074 | Supply and fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings SDR 13.5 to meet the requirement of ASTM-D 2846 and are produced in CTS Copper Tube Sizes 1/2inches to 2inches for hot and cold water IS 15778:2007 including cost and conveyance of all materials to site, labour charges for fixing, complete for finished item of work at all floor levels. 15.90mm OD pipe at Gandhi Hospital | 75 | Rmt | 199 | 14925 | 39.5 | Rmt | 199 | 7861 | 0 | 7064 | The qty is utilised as per site condition and Hence savings | P
158 | 76 | IVF076 | Supplying and fixing of SWR PVC pipes Prince/Sudhakar/ Kisan /Supreme or any ISI brand 4 Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, complete for finished item of work at all floor levels. APSS No. 1302 1319 and 1326 - 75mm dia at Gandhi Hospital | 90 | Rmt | 327 | 29430 | 0 | Rmt | 327 | 0 | 0 | 29430 | The qty is not utilised as per site condition. Hence savings | P
159 | 77 | IVF077 | Supplying and fixing of SWR PVC pipes Prince/Sudhakar/Kisan /Supreme or any ISI brand 4 Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, complete for finished item of work at all floor levels. APSS No. 1302 1319 and 1326- 110mm dia at Gandhi Hospital | 75 | Rmt | 444 | 33300 | 26.63 | Rmt | 444 | 11824 | 0 | 21476 | The qty is not utilised as per site condition. Hence savings | P
160 | 78 | IVF078 | Supplying and fixing Bronze Gate/ Globe valve as per IS - 778 Class - I, Indian make heavy type including cost and conveyance of all materials , labour charges , overheads and contractors profit complete for finished item of work. 25mm Nominal bore at Gandhi Hospital | 5 | No | 1750 | 8750 | 3 | No | 1750 | 5250 | 0 | 3500 | The qty is utilised as per site condition and hence savings | P
161 | 79 | IVF079 | Supplying and fixing of 4inches 101.6mm multi floor trap with jali - UPVC/SWR pipe fittings as per site requirements with standard practice for all floors including cost and conveyance of all materials to site, labour charges ,etc., complete for finished item of work. at Gandhi Hospital | 10 | No | 220 | 2200 | 5 | No | 220 | 1100 | 0 | 1100 | The qty is utilised as per site condition and hence savings | P
162 | 80 | IVF080 | Supplying and fixing Indian make Flat Back Wash Hand Basin 1st quality conforming to IS:2556-Part-4:1972 of size 550mm x 400mm with 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963- 1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make heavy duty complete with standard CI brackets including wooden blocks ,1 No.12.70mm PVC connection with brass union nuts CP coated , angle stop cock 12.70mm dia. first quality Indian make heavy duty, 30mm dia. PVC flexible waste pipe 914.4mm length of 1st quality including cost and conveyance of all materials to site, labour charges, for finished item of work at Gandhi Hospital | 5 | No | 3800 | 19000 | 4 | No | 3800 | 15200 | 0 | 3800 | The qty is utilised as per approved layout and hence savings | P | 4.17
163 | 81 | IVF081 | Supply, Installation and commissioning approved make floor mounted Anglo Indian wash down EWC conforming to IS:2556 Part 8-2004 suit with P or S trap with dual flush porcelain cistern fixed on wash down EWC with all internal parts of dual flush cistern, ultra solid seat cover of approved make with rubber buffer and cap and 15 mm angle stop cock and 450 mm long PVC inter connection pipe wall flanges all of approved make etc. complete for finished item of work in all respects: TBSP-E.II-03 at Gandhi Hospital | 5 | No | 7590 | 37950 | 4 | No | 7590 | 30360 | 0 | 7590 | The qty is utilised as per approved layout and hence savings. | P
164 | 82 | IVF082 | Supplying and fixing Chromium plated finish brass body quarter turn Bibcock cum Health Faucet with 1m long tube and wall hook with necessary fittings etc., complete including cost and conveyance of all materials, labour charges, complete for finished item of work in all floors. at Gandhi Hospital | 5 | No | 4580 | 22900 | 4 | No | 4580 | 18320 | 0 | 4580 | The qty is utilised as per approved layout and hence savings. | P
165 | 83 | IVF083 | Supplying and fixing CP finish brass soap dish of approved make ISI quality including cost and conveyance of all materials, labour charges for fixing, for finished item of work in all floors at Gandhi Hospital | 5 | No | 872 | 4360 | 4 | No | 872 | 3488 | 0 | 872 | The qty is utilised as per approved layout and hence savings. | P
166 | 84 | IVF084 | Supplying and fixing TV shape mirror with plastic frame of size 609.6mm x 457.2mm, plywood back with NP screws 1st quality including cost and conveyance of all materials, labour charges, for finished item of work in all floors. at Gandhi Hospital | 5 | No | 727 | 3635 | 4 | No | 727 | 2908 | 0 | 727 | The qty is utilised as per approved layout and hence savings. | P
167 | 85 | IVF085 | Supplying and fixing of CP finish brass wall mounted towel ring at Gandhi Hospital | 5 | No | 872 | 4360 | 4 | No | 872 | 3488 | 0 | 872 | The qty is utilised as per approved layout and hence savings. | P
168 | 86 | IVF086 | Supplying and fixing 15 mm brass body CP finish self closing tap push type conforming to IS 1711 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, complete for finished item of work in all floors. at Gandhi Hospital | 5 | No | 418 | 2090 | 4 | No | 418 | 1672 | 0 | 418 | The qty is utilised as per approved layout and hence savings. | P
[7 empty] | 187305 |  |  | PART-B | 102352 | 0 | 84953
ELECTRICAL WORKS
169 | 100 | IVF100 | Supply and fixing of 16A switches - 1Nos and 6/16A 2 in one socket - 1Nos Modular type with cover plate and GI switch box fixing on separate board including all labour charges etc., complete. Makes of switches: - GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/Gold Medal curve. at Gandhi Hospital | 40 | No | 1040 | 41600 | 14 | No | 1040 | 14560 | 0 | 27040 | The qty is utilised as per site condition and hence savings | E
170 | 101 | IVF101 | Supply and fixing of 16A/6A, 2 in one socket - 2 Nos with 16A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: - GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/Gold Medal curve. at Gandhi Hospital | 60 | No | 1755 | 105300 | 53 | No | 1755 | 93015 | 0 | 12285 | The qty is utilised as per site condition and hence savings | E
171 | 102 | IVF102 | Supply and fixing of 16A/6A, 2 in one socket - 4 Nos with 16A switch control - 4 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: - GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/Gold Medal curve. at Gandhi Hospital | 10 | No | 3092 | 30920 | 0 | No | 3092 | 0 | 0 | 30920 | Not executed as not required at site. | E
172 | 103 | IVF103 | Supply and run of 1 of 22 /0.3mm 1.5 Sq.mm FRLS / HFFR P.V.C. insulated flexible copper cable in existing conduit pipe for earth continuity including all labour charges etc., complete. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at Gandhi Hospital | 350 | Rmt | 40 | 14000 | 0 | Rmt | 40 | 0 | 0 | 14000 | Not executed as not required at site. | E
173 | 108 | IVF108 | Supply and fixing of DP Metal Enclosure with IP 20 Protection DB Make with 1 No 20A, 10 KA DP MCB Make: Legrand / Schneider including internal connection and labour charges for Flush Mounting etc., complete. Makes: Legrand / Schneider. at Gandhi Hospital | 5 | No | 2562 | 12810 | 1 | No | 2562 | 2562 | 0 | 10248 | The qty is utilised as per site requirement and hence savings | E
174 | 110 | IVF110 | Supply and fixing of 8 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand / Schneider and Supply and Fixing of 1 No., of 63A FP 100mA RCCB as incomer and 24 Nos 6-32 A 10kA SP MCBs Makes: Legrand-DX3 / Schneider-Acti9 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. For Lighting DBs At Gandhi Hospital | 2 | No | 28460 | 56920 | 0 | No | 28460 | 0 | 0 | 56920 | Not Executed as not required at site. | E
175 | 113 | IVF113 | Providing and fixing of 100A 10KA FP MCB and Terminal Spreaders in IP 43 isolator Box Making connections etc, as required. Makes: Legrand / Schneider/ABB/LandT/CandS At Gandhi Hospital | 2 | No | 3260 | 6520 | 0 | No | 3260 | 0 | 0 | 6520 | Not Executed as not required at site. | E
176 | 114 | IVF114 | Supply, transportation and fixing of 24W edge lit LED Down light Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser Square with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor greater than 0.9, Surge protection: greater than 2KV, System efficacy of greater than100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI greater than80, and THD is less than 15percentage etc., with BIS Certification. Makes: Phillips / OSRAM / Wipro / Crompton / Bajaj / Havells At Gandhi Hospital | 50 | No | 2652 | 132600 | 44 | No | 2652 | 116688 | 0 | 15912 | The qty is utilised as per site requirement and hence savings | E
177 | 116 | IVF116 | Supply and Transportation 42W Clean room Light fixture, 2 feet x2 feet 600mm x600mm LED luminaire CRCA powder coated white after phosphocreatine treatment provided as standard. with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor greater than 0.9, Surge protection greater than 2KV, System efficacy of greater than100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI greater than80, and THD is less than 15percentage etc., complete. MAKE: OSRAM / Wipro / Crompton / Bajaj / Havells At Gandhi Hospital | 12 | No | 4762 | 57144 | 0 | No | 4762 | 0 | 0 | 57144 | During site inspection, EE (Electrical) has instructed to provide 56W lights to attain required illuminance. Hence savings | E
178 | 117 | IVF117 | Supply and fixing of ISI mark batten holder / slanting holder Makes : Anchor/ Gold Medal Olive / Million Zoom in lieu of ceiling rose of light point complete with all connections and all labour charges with 5.0W LED Lamp MAKE: OSRAM / Wipro / Crompton / Bajaj / Havells At Gandhi Hospital | 5 | No | 184 | 920 | 0 | No | 184 | 0 | 0 | 920 | Not executed as not required at site. | E
179 | 118 | IVF118 | Supply, Transportation of energy efficient fan, 1200 mm sweep, aluminium body, consuming 28 W, BEE 5 star rated, ceiling fan with Brush Less Direct Current BLDCmotor, class of insulation: B, 3 nos blades, 30 cm long down rod, 2 nos canopies, shackle ‘kit, safety rope, copper winding, Power Factor greater than 0.90, Service Value CMMAV greater than 8.5, Air delivery minimum 235 CMM,350 RPM tolerance as per IS:374-2019, THD less than 10percentage. with remote or compatible to electronic step type regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise equal to75 degree Cmax, insulation resistance more than 2 mega ohm, suitable for 230V, 50 HZ, single phase AC supply, earthing etc., including all standard accessories etc., complete. Makes : Atomberg Efficio / Havells /Orient At Gandhi Hospital | 12 | No | 4090 | 49080 | 0 | No | 4090 | 0 | 0 | 49080 | As per Instructions of EE (Electrical) during site inspection, regular high speed fans were provided. Hence savings | E
180 | 120 | IVF120 | Supply and installation of 225mm Light duty exhaust fan with metal blades etc complete Makes: Crompton / Havells Ventilair-DB/ Orient hill air. At Gandhi Hospital | 5 | No | 2203 | 11015 | 4 | No | 2203 | 8812 | 0 | 2203 | The qty is utilised as per site requirement and hence savings | E
181 | 121 | IVF121 | SITC of Hot dip galvanized perforated cable tray of 100 mm Wide sizes for to run the cable from DBs to SBs and sockets and AC panel to Units units. All necessary supports and accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. At Gandhi Hospital | 70 | Rmt | 429 | 30030 | 36.2 | Rmt | 429 | 15530 | 0 | 14500 | The qty is utilised as per site requirement and hence savings | E
182 | 128 | IVF128 | Supply and installation of 50x6 GI flat for body earthing of electrical panel and AC Panel which is laid in 300mm cable tray At Gandhi Hospital | 200 | Rmt | 329 | 65800 | 184.9 | Rmt | 329 | 60832 | 0 | 4968 | The qty is utilised as per site condition and hence savings | E
183 | 130 | IVF130 | Supply and installation of 25x3 Copper flat for Neutral earthing of UPS and Equipment which is laid in 100mm cable tray At Gandhi Hospital | 200 | Rmt | 902 | 180400 | 65.3 | Rmt | 902 | 58901 | 0 | 121499 | The qty is utilised as per site condition and hence savings. | E
184 | 132 | IVF132 | Supply, Laying and testing of 3.5Cx95 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc. Make of cable:Polycab/KEI/Universal/Glostar/Finolex Make of gland and Lungs: HMI/Commet/Dowell’s At Gandhi Hospital | 120 | Rmt | 1207 | 144840 | 83 | Rmt | 1207 | 100181 | 0 | 44659 | The qty is utilised as per site condition and hence savings | E
185 | 133 | IVF133 | Supply, Laying and testing of 3.5CX50 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc.. Make of Cable: Polycab/KEI/Universal/Glostar/ Finolex Make of gland and Lungs: HMI/Commet/Dowell’s At Gandhi Hospital | 70 | Rmt | 722 | 50540 | 40 | Rmt | 722 | 28880 | 0 | 21660 | The qty is utilised as per site condition and hence savings | E
186 | 134 | IVF134 | Supply, Laying and testing of 4Cx16 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc..Make of Cable: Polycab/KEI/Universal/Glostar/Finolex Make of gland and Lungs: HMI/Commet/Dowell’s At Gandhi Hospital | 100 | Rmt | 1483 | 148300 | 60 | Rmt | 1483 | 88980 | 0 | 59320 | The qty is utilised as per site condition and hence savings | E
187 | 135 | IVF135 | Supply, Laying and testing of 4Cx6 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc. Make of Cable: Polycab/KEI/Universal/Glostar/Finolex Make of gland and Lungs: HMI/Commet/Dowell’s At Gandhi Hospital | 120 | Rmt | 484 | 58080 | 53 | Rmt | 484 | 25652 | 0 | 32428 | The qty is utilised as per site condition and hence savings | E
[7 empty] | 1196819 |  |  | PART-B | 614593 | 0 | 582226
Air Conditioning Works
188 | 150 | IVF150 | Supply, transportation and installation of split AC unit 1.0 TR inverter type minimum 3 Star capable of delivering 12000 BTU/hr and above with high wall mounted indoor unit and outdoor condensing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord , built-in stabilizer Voltage range 160- 264 volts and cordless remote control. Makes: Daikin / Thoshiba/ O General at Gandhi Hospital | 1 | No | 40000 | 40000 | 0 | No | 40000 | 0 | 0 | 40000 | In place of 1.0 ton, provided with 1.5 ton AC | AC
189 | 155 | IVF155 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Liquid Line at Gandhi Hospital | 20 | Rmt | 1020 | 20400 | 10 | Rmt | 1020 | 10200 | 0 | 10200 | The qty is utilised as per site condition and hence savings | AC
190 | 156 | IVF156 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Suction Line at Gandhi Hospital | 20 | Rmt | 1190 | 23800 | 12 | Rmt | 1190 | 14280 | 0 | 9520 | The qty is utilised as per site condition and hence savings | AC
191 | 157 | IVF157 | SITC of CPVC drain piping with supports, clamps and 9 mm thk. Nitrile rubber tube insulation of the following sizes. Insulation shall have factory laminated glass cloth. 32mm Dia at Gandhi Hospital | 50 | Rmt | 670 | 33500 | 0 | Rmt | 670 | 0 | 0 | 33500 | Not executed as not required at site. | AC
192 | 158 | IVF158 | SITC of CPVC drain piping with supports, clamps and 9 mm thk. Nitrile rubber tube insulation of the following sizes. Insulation shall have factory laminated glass cloth. 25mm Dia at Gandhi Hospital | 50 | Rmt | 515 | 25750 | 12 | Rmt | 515 | 6180 | 0 | 19570 | The qty is utilised as per site condition and hence savings | AC
193 | 159 | IVF159 | SITC of Factory fabricated and boxed ducting using Aluminium Sheets / coils, should be fabricated as per SMACNA, galvanised hardware and supports, silicon sealant at all longitudinal joints, Galvanized /GI Electroplated iron angle flanges for all the joints, bracing angles and minimum 5mm thick neoprene rubber gasket.- Duct pressure testing at 75mm to be carried out before insulatiting the duct. pressure testing to be done as per SMACNA. Procedure to be approved by consultant. 20G - 1.0 mm Thick at Gandhi Hospital | 30 | Sqm | 2600 | 78000 | 0 | Sqm | 2600 | 0 | 0 | 78000 | The entire ducting was executed with 22G Thickness. Hence savings. | AC
194 | 160 | IVF160 | SITC of Factory fabricated and boxed ducting using Aluminium Sheets / coils, should be fabricated as per SMACNA, galvanised hardware and supports, silicon sealant at all longitudinal joints, Galvanized /GI Electroplated iron angle flanges for all the joints, bracing angles and minimum 5mm thick neoprene rubber gasket.- Duct pressure testing at 75mm to be carried out before insulatiting the duct. pressure testing to be done as per SMACNA. Procedure to be approved by consultant. 22G - 0.8 mm Thick at Gandhi Hospital | 250 | Sqm | 2325 | 581250 | 230.24 | Sqm | 2325 | 535308 | 0 | 45942 | The qty is utilised as per site condition and hence savings | AC
195 | 161 | IVF161 | Aluminium low leakage aerofoil design volume control dampers Suitable for manual and motorised operation At Gandhi Hospital | 2 | Sqm | 15800 | 31600 | 1.24 | Sqm | 15800 | 19592 | 0 | 12008 | The qty is utilised as per site condition and hence savings | AC
196 | 162 | IVF162 | CBRI approved 16G GI Spring return actuated fire dampers rated for 90 minutes with limit switch. At Gandhi Hospital | 2 | Sqm | 25900 | 51800 | 0.84 | Sqm | 25900 | 21756 | 0 | 30044 | The qty is utilised as per site condition and hence savings | AC
197 | 165 | IVF165 | SITC of Collar Dampers made of Al. extrusions with black powder coating for Grilles / Diffusers At Gandhi Hospital | 1 | Sqm | 7550 | 7550 | 0.72 | Sqm | 7550 | 5436 | 0 | 2114 | The qty is utilised as per site condition and hence savings | AC
198 | 168 | IVF168 | SITC of Aluminium powder coated Fresh air and Exhaust Louvers of non- vision type with nylon mosquito net etc. At Gandhi Hospital | 1 | Sqm | 10300 | 10300 | 0.12 | Sqm | 10300 | 1236 | 0 | 9064 | The qty is utilised as per site condition and hence savings | AC
199 | 169 | IVF169 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 32mm Thick for Exposed Supply Air duct and finished with UV Protective Paint. at Gandhi Hospital | 130 | Sqm | 1225 | 159250 | 119.84 | Sqm | 1225 | 146804 | 0 | 12446 | The qty is utilised as per site condition and hence savings | AC
200 | 170 | IVF170 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Exposed Return Air Duct and finished with UV Protective Paint. at Gandhi Hospital | 130 | Sqm | 1075 | 139750 | 84.41 | Sqm | 1075 | 90741 | 0 | 49009 | The qty is utilised as per site condition and hence savings | AC
201 | 172 | IVF172 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 19mm Thick for Return air running inside the building. at Gandhi Hospital | 40 | Sqm | 660 | 26400 | 19.24 | Sqm | 660 | 12698 | 0 | 13702 | The qty is utilised as per site condition and hence savings | AC
202 | 174 | IVF174 | VRF Indoor Units : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 0.8 TR At Gandhi Hospital | 2 | No | 30700 | 61400 | 1 | No | 30700 | 30700 | 0 | 30700 | The qty is utilised as per site condition and hence savings | AC
[7 empty] | 1290750 |  |  | PART-B | 894931 | 0 | 395819
[6 empty] | TOTAL (PART-B) | 8724682 |  |  |  | 5272965 | 0 | 3451717
|  |  | GRAND TOTAL (Part A+Part B) |  |  |  | 11700992 |  |  |  | 14652446.1 | 6403171.1 | 3451717
[10 empty] | TOTAL EXCESS | 2951454.1
As Per Agreement |  |  | 11700992 |  |  | Excess | 6403171.1
As Per RE |  |  | 14652446.1 |  |  | Less | 3451717
Difference |  |  | 2951454.1 |  |  | Difference | 2951454.1

## CS
Comparitive statement
Name of the work: Design, fabrication, establishing & commissioning of In-Vitro Fertility Center (IVFC) along with allied services on Turnkey basis at Gandhi Hospital, Secunderabad. | [7 empty] | +
S.No | Description |  | As per Agreement | As per workdone | Excess | Less | Net difference
Agreement works (Part-A)
1 | Equipment |  | #REF! | #REF! | 931300 | 0
2 | Civil Works |  | #REF! | #REF! | #REF! | #REF!
3 | Plumbing works |  | #REF! | #REF! | #REF! | #REF!
4 | Electrical works |  | #REF! | #REF! | #REF! | #REF!
5 | ELV works |  | #REF! | #REF! | #REF! | #REF!
6 | Fire Fighting works |  | #REF! | #REF! | #REF! | #REF!
7 | Air Conditioning works |  | #REF! | #REF! | #REF! | #REF!
8 | MGPS works |  | #REF! | #REF! | 969000 | 0
| Sub Total (Part-A) |  | #REF! | #REF! | #REF! | #REF!
Supplemental works (Part-B)
9 | Equipment |  | #REF! | #REF! | #REF! | #REF!
10 | Civil works |  | #REF! | #REF! | #REF! | #REF!
11 | Plumbing works |  | #REF! | #REF! | #REF! | #REF!
12 | Electrical works |  | #REF! | #REF! | #REF! | #REF!
13 | Fire Fighting works |  | #REF! | #REF! | #REF! | #REF!
14 | Air Conditioning works |  | #REF! | #REF! | #REF! | #REF!
15 | MGPS works |  | #REF! | #REF! | #REF! | #REF!
| Sub Total (Part-B) |  | #REF! | #REF! | #REF! | #REF!
| Total (Part-A+Part-B) |  | #REF! | #REF! | #REF! | #REF! | #REF!
16 | Provision towards Engineering Supervision Charges @ 4% on RE Value | 4% | #REF! | #REF! | #REF! | #REF!
| GST @ 18% |  | #REF! | #REF! | #REF! | #REF!
| Total |  | #REF! | #REF! | #REF! | #REF!
17 | Labour Cess @ 1% on Basic Price of Revised Estimate | 1% |  | #REF! | #REF! | #REF!
18 | NAC @ 0.1% on Basic Price of Revised estimate | 0.1% |  | #REF! | #REF! | #REF!
19 | Provision towards seigniorage Charges on Civil Component |  |  | 308 | 308 | 0
20 | Provision towards DMF Charges 30% on Seniorage Charges | 30% |  | 92.4 | 92.4 | 0
21 | Provision towards SMFT Charges 2% on seigniorage Charges | 2% |  | 6.16 | 6.16 | 0
22 | Provision towards Haritha Nidhi @ 0.01% | 0.01% |  | #REF! | #REF! | #REF!
23 | Subtotal of S. No 17 to 22 |  |  | #REF! | #REF! | #REF!
24 | Provision towards GST 18% on Subtotal @ S. No. 23 | 18% |  | #REF! | #REF! | #REF!
25 | Provision towards Inauguration charges |  |  | 200000 | 200000 | 0
26 | Provision towards Unforeseen items and rounding off (LS) |  | 1181324 |  | 0 | 1181324
| Sub total of S.No 23 to 26 |  |  | #REF! | #REF! | #REF!
| Grand Total |  | #REF! | #REF! | #REF! | #REF! | #REF!
|  | As per Admn. Sanction |  | #REF! | Excess | #REF!
|  | As per Work done |  | #REF! | Less | #REF!
|  | Difference |  | #REF! | Difference | #REF!
//APPROVED//
Sd/- (04.03.2024)
CHIEF ENGINEER
//T.C.F.B.O//
CHIEF ENGINEER
EXECUTIVE ENGINEER Spl. Projects

## CS-1 (hidden)
Comparitive statement
Name of the work: Design, fabrication, establishing & commissioning of In-Vitro Fertility Centers (IVFCs) along with allied services on Turnkey basis at Gandhi Hospital, Secunderabad.
S.No | Description |  | As per Agreement | As per workdone | Excess | Less | Net difference
Agreement works (Part-A)
1 | Equipment |  | #REF! | #REF! | #REF! | #REF!
2 | Civil Works |  | #REF! | #REF! | #REF! | #REF!
3 | Plumbing works |  | #REF! | #REF! | #REF! | #REF!
4 | Electrical works |  | #REF! | #REF! | #REF! | #REF!
5 | ELV works |  | #REF! | #REF! | #REF! | #REF!
6 | Fire Fighting works |  | #REF! | #REF! | #REF! | #REF!
7 | Air Conditioning works |  | #REF! | #REF! | #REF! | #REF!
8 | MGPS works |  | #REF! | #REF! | #REF! | #REF!
| Sub Total (Part-A) |  | #REF! | #REF! | #REF! | #REF!
Supplemental works (Part-B)
9 | Equipment |  | #REF! | #REF! | #REF! | #REF!
10 | Civil works |  | #REF! | #REF! | #REF! | #REF!
11 | Plumbing works |  | #REF! | #REF! | #REF! | #REF!
12 | Electrical works |  | #REF! | #REF! | #REF! | #REF!
13 | Fire Fighting works |  | #REF! | #REF! | #REF! | #REF!
14 | Air Conditioning works |  | #REF! | #REF! | #REF! | #REF!
15 | MGPS works |  | #REF! | #REF! | #REF! | #REF!
| Sub Total (Part-B) |  | #REF! | #REF! | #REF! | #REF!
| Total (Part-A+Part-B) |  | #REF! | #REF! | #REF! | #REF! | #REF!
16 | Provision towards Engineering Supervision Charges @ 4% on RE Value | 4% | #REF! | #REF! | #REF! | #REF!
| GST @ 18% |  | #REF! | #REF! | #REF! | #REF!
| Total |  | #REF! | #REF! | #REF! | #REF!
17 | Labour Cess @ 1% on Basic Price of Revised Estimate | 1% |  | #REF! | #REF! | #REF!
18 | NAC @ 0.1% on Basic Price of Revised estimate | 0.1% |  | #REF! | #REF! | #REF!
19 | Provision towards seigniorage Charges on Civil Component |  |  | 308 | 308 | 0
20 | Provision towards DMF Charges 30% on Seniorage Charges | 30% |  | 92.4 | 92.4 | 0
21 | Provision towards SMFT Charges 2% on seigniorage Charges | 2% |  | 6.16 | 6.16 | 0
22 | Provision towards Haritha Nidhi @ 0.01% | 0.01% |  | #REF! | #REF! | #REF!
23 | Subtotal of S. No 17 to 22 |  |  | #REF! | #REF! | #REF!
24 | Provision towards GST 18% on Subtotal @ S. No. 23 | 18% |  | #REF! | #REF! | #REF!
25 | Provision towards Inauguration charges |  |  | 200000 | 200000 | 0
26 | Provision towards Unforeseen items and rounding off (LS) |  | 1181324 |  | 0 | 1181324 |  | 55000000
| Sub total of S.No 23 to 26 |  |  | #REF! | #REF! | #REF! |  | #REF!
| Grand Total |  | #REF! | #REF! | #REF! | #REF! | #REF!
#REF!
|  | As per Admn. Sanction |  | #REF! | Excess | #REF!
|  | As per Work done |  | #REF! | Less | #REF!
|  | Difference |  | #REF! | Difference | #REF!
T.A DY. EXECUTIVE ENGINEER EXECUTIVE ENGINEER CHIEF ENGINEER
1938 nos bricks

## GA
Name of the work: Design, fabrication, establishing & commissioning of In-Vitro Fertility Centers (IVFCs) along with allied services on Turnkey basis at Gandhi Hospital.
GENERAL ABSTRACT
S.No | Description | As per workdone
1 | Equipment | #REF!
2 | Civil Works | #REF!
3 | Plumbing works | #REF!
4 | Electrical works | #REF!
5 | ELV works | #REF!
6 | Fire Fighting works | #REF!
7 | Air Conditioning works | #REF!
8 | MGPS works | #REF!
| Sub Total (Agreement Part-A) | #REF!
9 | Equipment supplemental | #REF!
10 | Civil supplemental works | #REF!
11 | Plumbing supplemental works | #REF!
12 | Electrical supplemental works | #REF!
13 | Fire Fighting supplemental works | #REF!
14 | Air Conditioning supplemental works | #REF!
15 | MGPS supplemental works | #REF!
| Sub Total (Supplemental Part-B) | #REF!
| Total (Part-A+Part-B) | #REF!
16 | Provision towards Engineering Supervision Charges @ 4% on RE Value | #REF!
| GST @ 18% | #REF!
| Total | #REF!
17 | Labour Cess @ 1% on Basic Price of Revised Estimate | #REF!
18 | NAC @ 0.1% on Basic Price of Revised estimate | #REF!
19 | Provision towards Seniorage Charges on Civil Component | 308
20 | Provision towards DMF Charges 30% on Seniorage Charges | 92.4
21 | Provision towards SMFT Charges 2% on seniorage Charges | 6.16
22 | Provision towards Haritha Nidhi | #REF!
23 | Sub total of S.No 17 to 22 | #REF!
24 | Provision towards GST 18% on Seniorage Charges | #REF!
25 | Provision towards Inauguration Charges | 200000
| Sub total of S.No 23 to 25 | #REF!
| Grand Total | #REF!
//APPROVED//
Sd/- (04.03.2024)
CHIEF ENGINEER
//T.C.F.B.O//
EXECUTIVE ENGINEER Spl. Projects
1938 nos bricks

## ABSTRACT-1 (hidden)
Name of the work: Design, fabrication, establishing & commissioning of In-Vitro Fertility Centers (IVFCs) along with allied services on Turnkey basis at Gandhi Hospital, Secunderabad, MGM Hospital, Warangal & MGMH Petlaburj, Hyd.
COMPARITIVE STATEMENT FOR GENERAL ABSTRACT
S.No | Description |  | As per Agreement | As per workdone | Excess | Less | Remarks
Agreement works (Part-A)
1 | Equipment |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
2 | Civil Works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
3 | Plumbing works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
4 | Electrical works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
5 | ELV works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
6 | Fire Fighting works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
7 | Air Conditioning works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
8 | MGPS works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
| Sub Total (Agreement Part-A) |  | #REF! | #REF! | #REF! | #REF!
Supplimental works (Part-B)
9 | Equipment supplimental |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
10 | Civil supplimental works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
11 | Plumbing supplimental works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
12 | Electrical supplimental works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
13 | Fire Fighting supplimental works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
14 | Air Conditioning supplimental works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
15 | MGPS supplimental works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
| Sub Total (Supplimental Part-B) |  | #REF! | #REF! | #REF! | #REF!
| Total (Part-A+Part-B) |  | #REF! | #REF! | #REF! | #REF!
| GST @ 18% |  | #REF! | #REF! | #REF! | #REF!
| Total |  | #REF! | #REF! | #REF! | #REF!
16 | Labour Cess @ 1% on Basic Price of Revised Estimate | 1% |  | #REF! | #REF! | #REF!
17 | NAC @ 0.1% on Basic Price of Revised estimate | 0.1% |  | #REF! | #REF! | #REF!
18 | Provision towards Seniorage Charges on Civil Component |  |  | 308 | 308 | 0
19 | Provision towards DMF Charges 30% on Seniorage Charges | 30% |  | 92.4 | 92.4 | 0
20 | Provision towards SMFT Charges 2% on seniorage Charges | 2% |  | 6.16 | 6.16 | 0
21 | Provision towards Haritha Nidhi | 0.01% |  | #REF! | #REF! | #REF!
22 | Sub total of S.No 14 to 18 |  |  | #REF! | #REF! | #REF!
23 | Provision towards GST 18% on Seniorage Charges | 18% |  | #REF! | #REF! | #REF!
24 | Provision towards Engineering Supervision Charges @ 4% on RE Value | 4% | #REF! | #REF! | #REF! | #REF!
25 | Provision towards Unforseen items and rounding off (LS) |  |  |  | 0 | 0
| Sub total of S.No 22 to 25 |  |  | #REF! | #REF! | #REF!
| Grand Total |  | #REF! | #REF! | #REF! | #REF!
|  | As Per Agreement |  | #REF! | Excess | #REF!
|  | As Per RE |  | #REF! | Less | #REF!
|  | Difference |  | #REF! | Difference | #REF!
| DY.EXECUTIVE ENGINEER |  | EXECUTIVE ENGINEER |  |  | SUPERINTENDING ENGINEER
| TSMSIDC, MEDCHAL MALKAJGIRI |  | TSMSISDC, HYDERAVAD DIVISION |  |  | TSMSISDC, HYDERABAD CIRCLE
1938 nos bricks

## C-DATAS
CIVIL DATAS (2022-23 SSR)
20 | Supply and application of one coat water based cement primer of interior grade I for internal walls including cost and conveyance of all materials to site, sales and other taxes, incidental, operational and all labour charges etc., and complete for finished item of work in 5th floor (for Ceiling) at Gandhi Hospital
(BLD-CSTN-12-5)
| Cost of cement primer interior grade I TBSC-G.I-01 | 1 | Kg | 173 | 1 | Kg | 173
| Painter 1st class | 0.21 | Nos. | 665 | 1 | Each | 139.65
| Painter 2nd class | 0.49 | Nos. | 550 | 1 | Each | 269.5
| Acrylic emulsion paint TBSC-G.III-01 |  | Kgs |  | 1 | Kgs | 0
| Painter 1st class |  | Nos. |  | 1 | Each | 0
| Painter 2nd class |  | Nos. |  | 1 | Each | 0
| Add for MA @ 40% |  | Nos. |  | 1 | Each | 0
| Add for MA @ 40% | 0.4 |  | 409.15 |  |  | 163.66
| Sundries including brushes, ladders etc., @ 1% | 0.01 |  | 745.81
745.81
| Overheads & Contractors Profit @ 13.615% | 0.13615 |  | 745.81 |  |  | 101.542
| Rate per 10 sqm | [5 empty] | 847.352
| Rate per 1 sqm | [5 empty] | 84.7352
[6 empty] | Say | 85
21 | Dismantling of unreinforced cement concrete, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete
(BLD-CSTN-14-8/297)
| Mazdoor(unskilled) | 4.88 | Nos. | 520 | 1 | Each | 2537.6
| Add for MA @ 40% | 0.4 |  | 2537.6 |  |  | 1015.04
| Rate per 1 cum | [5 empty] | 3552.64
| Overheads & Contractors Profit @ 13.615% | 0.13615 |  | 3552.64 |  |  | 483.6919
| Rate per 1 cum |  |  |  |  | Total Rs. | 4036.3319
[6 empty] | Or Say | 4036
22 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete - Old Cement Mortor (Plaster)
| Rate as per SSR TBSC-U.I-08 | 10 | sqm | 8 | 1 | sqm | 80
| Add for MA @ 40% | 0.4 |  | 80 |  |  | 32
| Rate per 10 sqm | [5 empty] | 112
| Rate per 1 sqm | [5 empty] | 11.2
| Overheads & Contractors Profit @ 13.615% | 0.13615 |  | 11.2 |  |  | 1.5249
| Rate per 1 sqm |  |  |  |  | Total Rs. | 12.7249
[6 empty] | Or Say | 13
23 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete. Reinforced Cement Concrete
(BLD-CSTN-14-8/298)
| Mazdoor(unskilled) | 4.32 | Nos. | 520 | 1 | Each | 2246.4
| Add for MA @ 40% | 0.4 |  | 2246.4 |  |  | 898.56
for cutting steel bars (BLD-CSTN-14-10/300)
| Blacksmith 2nd class | 0.5 | Nos. | 550 | 1 | Each | 275
| Mazdoor(Male) | 0.5 | Nos. | 520 | 1 | Each | 260
| Add for MA @ 40% | 0.4 |  | 535 |  |  | 214
| Rate per 1 cum | [5 empty] | 3893.96
| Overheads & Contractors Profit @ 13.615% | 0.13615 |  | 3893.96 |  |  | 530.1627
| Rate per 1 cum |  |  |  |  | Total Rs. | 4424.1227
[6 empty] | Or Say | 4424
25 | Providing of Factory made prelaminated FPVC (Foamed Polyvinyl Chloride) Door frame of the size 105x40mm with a wall thickness of 10mm made out of extruded rigid FPVC profile mitre joined with 6 Nos. of 50mm long screw. The door frame shall be fixed to the wall by using 80mm long screws through the frame with the help of PVC fasteners of 3 no's to be provided for each vertical member, GI stiffeners of ("U" channel of size 29x9x1mm, 150mm long) -3 no's at hinge point, Frame reinforcement of("U" GI channel of size 46x22x.06mm),Bottom tie rod of ("U" GI channel size of 15x15x1mm) etc. complete as per manufacturers specification for finished item of work. Maximum door frame size : 980 x 2070 including providing of 35mm thick Factory made Prelaminated ABS (Acrylonitrile Butadiene Styrene) Door shutter moulded in different designs, consisting of all round Frame made out of water proof solid foam PVC bar of size 20x32mm, reinforced by 32x 32mm - 2 nos. for vertical made out of LVL (Laminated Veneer Lumber), core material of 32 mm thick high density craft paper honey comb board, sandwiched on both sides with prelaminated ABS sheet thickness of 1.5mm . PVC edge banding of size 0.45mm on the vertical sides. Hardware made out of steel coated butterfly hinges - 3 Nos. for each shutter and ISI make S.S round lock completes for finished item of work. Maximum shutter size of : 910 x 2030 mm
| Rate as per SSR -2022-23 - TBSC-L.III-28 | 1 | Sqm | 8134 | 1 | Sqm | 8134
| Overheads & Contractors Profit @ 13.615% | 0.13615 |  | 8134 |  |  | 1107.4441
| Rate for 1 Sqm | [5 empty] | 9241.4441
[5 empty] | Or Say |  | 9241
24 | Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707)
(BLD-CSTN-9-20)
Unit = 10 sqm
| Cost of vitrified tiles 8-10mm thick | 10.5 | sqm | 578 | 1 | sqm | 6069
| Sand for CM(1:5) base coat | 0.12 | cum | 2453.91 | 1 | cum | 294.4692
| Cement for CM(1:5) base coat | 34.56 | Kgs | 5200 | 1000 | Kgs | 179.712
| Cement for slurry | 33 | Kgs | 5200 | 1000 | Kgs | 171.6
| White cement for jointing & pointing | 2 | Kgs | 34 | 1 | Kg | 68
B.LABOUR
| Mason 1st class | 0.96 | Nos. | 580 | 1 | Each | 556.8
| Mason 2nd class | 2.24 | Nos. | 550 | 1 | Each | 1232
| Mazdoor(unskilled) | 3.3 | Nos. | 520 | 1 | Each | 1716
| Add for MA @ 40% | 0.4 |  | 3504.8 |  |  | 1401.92
| Add water charges 1% | 0.01 |  | 11689.5012 |  |  | 116.895
| Rate for 10 sqm | [5 empty] | 11806.3962
| Rate for other Floors | FF (G.F) | SF | TF | 4 F | 5 F | 6 F
| Rate as worked out above | 11806.3962 | 11806.3962 | 11806.3962 | 11806.3962 | 11806.3962 | 11806.3962
| Lift charges ( Page 131 of Std. Data ) | 0 | 350.48 | 700.96 | 1051.44 | 1401.92 | 1752.4
| Add for MA @ 40% | 0 | 140.192 | 280.384 | 420.576 | 560.768 | 700.96
|  | 11806.3962 | 12297.0682 | 12787.7402 | 13278.4122 | 13769.0842 | 14259.7562
| Overheads & Contractors Profit @ 13.615% | 1607.44 | 1674.25 | 1741.05 | 1807.86 | 1874.66 | 1941.47
| Rate per 10 Sqm | 13413.8362 | 13971.3182 | 14528.7902 | 15086.2722 | 15643.7442 | 16201.2262
| Rate per 1 RM | 134.1384 | 139.7132 | 145.2879 | 150.8627 | 156.4374 | 162.0123
| Or Say | 134 | 140 | 145 | 151 | 156 | 162
26 | Flooring with 16 to 18 mm thick high polished granite stone slabs black colour as approved by the Engineer-in-Charge of length not less than 2.43 mts set over base coat of cement mortar (1:8) , 20mm thick using screened sand over CC bed already laid or RCC roof slab including neat grey cement slurry of honey like consistency spread @ 3.3 Kg per sqm and jointed neatly with white cement paste mixed with pigment of matching shade to full depth including cost and conveyance of all materials like cement , sand , water , granite slabs etc., to work site and all operational, incidental labour & lift charges, half rounding the edge , polishing charges and all other taxes on all materials, cost of base coat and overheads & contractors profit complete for finished item of work for platforms (S.S.701 & special) (for Reception Table).
(BLD-CSTN-9-7)
Unit = 10 sqm.
A. MATERIALS:
| High polished granite slabs black 16 to 18mm thick | 10.5 | Sqm | 2576 | 1 | Sqm | 27048
| Cement for CM(1:8) for base coat | 36 | Kgs | 5200 | 1000 | Kgs | 187.2
| Cement for slurry | 33 | Kgs | 5200 | 1000 | Kgs | 171.6
| White cement for jointing | 6 | Kgs | 34 | 1 | Kg | 204
| Sand for CM(1:8) | 0.2 | Cum | 2453.91 | 1 | Cum | 490.782
B .LABOUR
| Mason 1st class | 3 | Nos | 580 | 1 | Each | 1740
| Mason 2nd class | 1 | Nos | 550 | 1 | Each | 550
| Mazdoor(un skilled) | 8 | Nos | 520 | 1 | Each | 4160
| Add for MA @ 40% | 0.4 |  | 6450 |  |  | 2580
| Machine cutting charges | 16.67 | RM | 24 | 1 | RM | 400.08
| Half rounding the edges | 16.67 | RM | 456 | 1 | RM | 7601.52
| Add for MA @ 40% | 0.4 |  | 3200.64 |  |  | 1280.256
| Add water charges 1% | 0.01 |  | 46413.438 |  |  | 464.1344
| Rate for 10 sqm | [5 empty] | 46877.5724
| Rate for other Floors | FF (G.F) | SF | TF | 4 F | 5 F | 6 F
| Rate as worked out above | 46877.5724 | 46877.5724 | 46877.5724 | 46877.5724 | 46877.5724 | 46877.5724
| Lift charges ( Page 131 of Std. Data ) | 0 | 645 | 1290 | 1935 | 2580 | 3225
| Add for MA @ 40% | 0 | 258 | 516 | 774 | 1032 | 1290
|  | 46877.5724 | 47780.5724 | 48683.5724 | 49586.5724 | 50489.5724 | 51392.5724
| Overheads & Contractors Profit @ 13.615% | 6382.38 | 6505.32 | 6628.27 | 6751.21 | 6874.16 | 6997.1
| Rate per 10 Sqm | 53259.9524 | 54285.8924 | 55311.8424 | 56337.7824 | 57363.7324 | 58389.6724
| Rate per 1 Sqm | 5325.9952 | 5428.5892 | 5531.1842 | 5633.7782 | 5736.3732 | 5838.9672
| Or Say | 5326 | 5429 | 5531 | 5634 | 5736 | 5839
28 | Supply and placing of the Design Mix Concrete M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Weight Batcher / Concrete mixer with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials, centering using Casurina Ballies, Bamboos, Wooden Reapers, Runners, Wood Posts, Steel Plates etc., including all operational, incidental and labour charges such as weigh batching, machine mixing, lifting of concrete manually, laying concrete, curing , overheads & contractors profit etc., complete but excluding cost of steel and its fabrication charges for finished item of work (APSS No. 402) (for Lintels)
(BLD-CSTN-3-15)
COLUMNS, LINTELS, WATER TANKS, RCC WALL IN BUILDINGS:
A.MATERIALS :
| Cement | 380 | Kgs | 5200 | 1000 | Kgs | 1976
| 20mm HBG graded metal | 0.8 | Cum | 1447.96 | 1 | Cum | 1158.368
| Sand | 0.4 | Cum | 2253.91 | 1 | Cum | 901.564
B.LABOUR :
| 1st class Mason | 0.167 | Nos | 580 | 1 | Each | 96.86
| 2nd class Mason | 0.167 | Nos | 550 | 1 | Each | 91.85
| Mazdoor (both men&women) | 5.6 | Nos | 520 | 1 | Each | 2912
| Add for MA @ 40% | 0.4 |  | 3100.71 |  |  | 1240.284
C.MACHINERY :
| Concrete Mixer 10 / 7 cft (0.2 / 0.8 cum)capacity | 1.333 | hours | 192.9 | 1 | hour | 257.1357
| Crew charges | 1.333 | hours | 302.9 | 1 | hour | 403.7657
| Needle vibrator 40mm ( petrol ) | 1.333 | hours | 36.5 | 1 | hour | 48.6545
| Crew charges | 1.333 | hours | 218 | 1 | hour | 290.594
| Add MA on crew charges | 0.4 |  | 694.3597 |  |  | 277.7439
| Water(including for curing) | 1.2 | kl | 108 | 1 | kl | 129.6
| Rate per 1 cum | [5 empty] | 9784.4198
| LINTELS : | FF (G.F) | SF | TF | 4F | 5F | 6F
Lifting by Manual means
Rate for other Floors
| Rate as above | 9784.4198 | 9784.4198 | 9784.4198 | 9784.4198 | 9784.4198 | 9784.4198
| Hire charges of centering and scaffolding | 886 | 886 | 886 | 886 | 886 | 886
| Labour charges | 1489 | 1638 | 1787 | 1936 | 2085 | 2234
| Add for MA @ 40% | 595.6 | 655.2 | 714.8 | 774.4 | 834 | 893.6
| Lift charges of materials (Manual) | 0 | 310.071 | 620.142 | 930.213 | 1240.284 | 1550.355
| Add for MA @ 40% | 0 | 124.03 | 248.06 | 372.09 | 496.11 | 620.14
| Rate per 1 cum | 12755.0198 | 13397.7208 | 14040.4218 | 14683.1228 | 15325.8138 | 15968.5148
| Overheads & Contractors Profit @ 13.615% | 0 | 0 | 0 | 0 | 0 | 0
| Rate per 1 cum | 12755.0198 | 13397.7208 | 14040.4218 | 14683.1228 | 15325.8138 | 15968.5148
| Or Say | 12755 | 13398 | 14040 | 14683 | 15326 | 15969
30 | Supplying and fixing Rectangular Mirror Frameless of size 457 .2 mm x 609.6 mm (For Change room)
TBSP-J.I-41
| Cost of Vertical blinds 100 mm | 1 | No. | 1562 | 1 | Each | 1562
| Add for MA @ 40% | 0.4 |  | 0 |  |  | 0
| Rate per 1 No. | [5 empty] | 1562
| Overheads & Contractors Profit @ 13.615% | 0.13615 |  | 1562 |  |  | 212.6663
| Rate per 1 No. |  |  |  |  | Total Rs. | 1774.6663
[6 empty] | Or Say | 1775
52 | Supplying and fixing of windows / in open court yards using 25mm x 6mm MS flat alround and 10mm MS square bars horizontally at 125mm centre to centre and vertically at 300mm centre to centre including fixing with 4 Nos of MS Z holdfasts (2 on each side) duly making cutting brick masonry, fixing and making to original surface neatly and painting grill with one coat of red oxide primer including cost all taxes and conveyance of all materials including cutting, bending, welding including all operational charges and all labour charges etc., complete for finished item of work. (for Window Grills)
| For1.80mx1.80m size | 3.24 | Sqm
| Quantity Anailysis | [7 empty] | 1.62
| Cost of 25mm x 6mm MS flat alround | 2 ( 1.80+ 1.80 ) |  |  |  | 7.2 | RM | Cost of 25mm x 6mm MS flat alround | 2 ( 1.80+ 0.90 ) |  |  |  | 5.4 | RM
|  | 7.20 RM @ 1.80 Kgs/RM |  |  |  | 12.96 | Kgs |  | 7.20 RM @ 1.80 Kgs/RM |  |  |  | 9.72 | Kgs
| Cost of 10mm M.S square bars @0.785 kg /RM | [6 empty] | Cost of 10mm M.S square bars @0.785 kg /RM
| Vertical bars | 2 x 1.80 |  | 3.6 |  |  |  | Vertical bars | 2 x 1.80 |  | 3.6
| Horizontal bars | 16 x 1.80 |  | 28.8 |  |  |  | Horizontal bars | 16 x .9 |  | 14.4
|  |  |  | 32.4 | RM | 25.434 | Kgs |  |  |  | 18 | RM | 14.13 | Kgs
[6 empty] | 38.394 | Kgs | [5 empty] | 23.85 | Kgs
| Cost Analysis | [6 empty] | Cost Analysis
| Cost of 10mm MS squre bars (RMR) | 25.434 | Kgs | 61000 | 1000 | Kgs | 1551.474 | Cost of 10mm MS squre bars (RMR) | 14.13 | Kgs | 61000 | 1000 | Kgs | 861.93
| Cost of 25X 6mm MS Flat (RMR) | 12.96 | Kgs | 62000 | 1000 | Kgs | 803.52 | Cost of 25X 6mm MS Flat (RMR) | 9.72 | Kgs | 62000 | 1000 | Kgs | 602.64
| Cost of MS Z hold fasts | 4 | Nos. | 37 |  | Each | 148 | Cost of MS Z hold fasts | 4 | Nos. | 37 |  | Each | 148
| Labour charges for fabrication of steel TBSC-T.I-16 | 38.394 | Kgs | 37 | 1 | Kg | 1420.578 | Labour charges for fabrication of steel TBSC-T.I-16 | 23.85 | Kgs | 37 | 1 | Kg | 882.45
| Labour charges for fixing TBSC-T.I-17 | 38.394 |  | 6 |  |  | 230.364 | Labour charges for fixing TBSC-T.I-17 | 23.85 |  | 6 |  |  | 143.1
| Add for MA @ 40% | 0.4 |  | 798.5952 |  |  | 319.4381 | Add for MA @ 40% | 0.4 |  | 496.08 |  |  | 198.432
| Rate per 3.24 Sqm | [5 empty] | 4473.3741 | Rate per 3.24 Sqm | [5 empty] | 2836.552
[7 empty] | 1380.671 | [6 empty] | 1750.958
| Overheads & Contractors Profit @ 13.615% | 0.13615 |  | 1380.671 |  |  | 187.9784 | Overheads & Contractors Profit @ 13.615% | 0.13615 |  | 1750.958 |  |  | 238.3929
[7 empty] | 1568.6494 | [6 empty] | 1989.351
| Rate per 1 Sqm |  |  |  | Or Say |  | 1569 | Rate per 1 Sqm |  |  |  | Or Say |  | 1989
54 | Supply of Sun Control film to the glazed windows (For Windows & Door view Windows)
| Rate as per SSR TBSC-R.I-07 | 1 | Sqm | 335 | 1 | Sqm | 335
| Overheads & Contractors Profit @ 13.615% | 0.13615 |  | 335 |  |  | 45.6103
380.6103
| Rate per Sqm |  |  |  |  | say | 381
55 | Supplying and fixing of 3" (75mm) Nahany trap with jali - UPVC/SWR pipe fittings as per site requirements with standard practice for all floors including cost and conveyance of all materials to site, labour charges , overheads & contractors profit etc., complete for finished item of work.
| Rate as per SSR TBSP-H.II-73 | 1 | No. | 117 | 1 | Each | 117
| Overheads & Contractors Profit @ 13.615% | 0.13615 |  | 117 |  |  | 15.9295
132.9296
| Rate per Each |  |  |  |  | say | 133
56 | Supplying and fixing 50 mm Nominal Bore GI pipe Medium Grade properties & weight as per IS 1239 in ground or on wall with GI fittings such as elbows tees couplings, nipples, plugs including excavation for trenches and refilling the trenches ,chiselling masonry walls and making good the walls & floors to the original surface and fixing MS clamps on TW blocks on walls including cost and conveyance of all materials and labour charges , overheads & contractors profit complete for finished item of work except for GI bends union and GI connectors with checkout and socket Tata or Zenith make or equivalent. (For Autoclave)
| Rate as per SSR TBSP-G.I-13 | 1 | RM | 527 | 1 | RM | 527
| Overheads & Contractors Profit @ 13.615% | 0.13615 |  | 527 |  |  | 71.751
598.751
| Rate per 1 RM |  |  |  |  | say | 599
31 | Supply of Venetian blinds Vertical blinds 100 mm wide with all accessories. (For semen collection room & Counselling room Windows)
TBSC-R.I-10
| Cost of Vertical blinds 100 mm | 1 | Sqm | 1375 | 1 | Each | 1375
| Add for MA @ 40% | 0.4 |  | 1375 |  |  | 550
| Rate per 1 cum | [5 empty] | 1925
| Overheads & Contractors Profit @ 13.615% | 0.13615 |  | 1925 |  |  | 262.0888
| Rate per 1 Sqm |  |  |  |  | Total Rs. | 2187.0887
[6 empty] | Or Say | 2187
35 | Supply and fixing of doors as per approved drawings with (WPC) single extruded Door Frame section of 100*65 MM and30mm thick Wood Plastic Composite (WPC) Door shutter, comprising of 70% virgin polymer, 15% wood powder (fiber), and the remaining 15% additives, the door shutter shall be water resistant, fire resistant and termite resistant,with Tensile Strength not less than 170Kgf/cm2 and the door shutters surface finished deco paint including cost and conveyance to site of teak wood frame, WPC shutter including supply and fixing 6 nos MS Z hold fasts of size 300 mm x 40 mm x 5mm including cost of ISI marked brass fixtures of 6 Nos butt hinges (IS:205) 150mm long , 1 No. aldrop (IS:2681) 300mm long, 2 Nos tower bolts- 10mm (IS:204) of 200 mm long at top, 1 No. tower bolt- 10mm bolt (IS:204) 150mm long at bottom, 2 Nos. 150mm long fancy handles (IS:208), 2 Nos door stopper and 2 Nos rubber bushes including fixing the fixtures to door with required number of screws, bolt and nuts including labour charges for fixing the frame in position, fixing the shutter to the frame, fixing glass in fan light portion etc., including overheads & contractors profit complete for finished item of work as per APSS 1001 & 1002 The vertical frame of door shall be embedded in flooring for a depth of not less than 10 mm) (800mm x 2100mm) (For Wash Rooms).
(BLD-CSTN-13-16)
| Quantity analysis | Size : | 0.80m x 2.10 m |  |  | 1.68 | sqm
| Outer frame - Vertical | 2 x 2.1
|  | = 4.2 x 0.10 x 0.065 = |  |  | 0.0273 |  | cum
| Outer frame - Horizontal | 1x0.80
|  | = 0.80x 0.10 x 0.065 = |  |  | 0.0052 |  | cum
[5 empty] | 0.0325 |  | cum
| 30 mm thick WPC shutter | 0.8x 2.10 |  |  | 1.68 |  | sqm
Cost analysis
| Cost of best WPC frame Vertical As per SSR2022-23 -TBSC-L.I-17 | 4.2 | Rm | 749 | 1 | cum | 3145.8
| Cost of best WPC frame Horizontal As per SSR2022-23 TBSC-L.I-17 | 0.8 | Rm | 749 | 1 | cum | 599.2
| Cost of 30 mm thick WPC shutter TBSC-L.I-18 | 1.68 | sqm | 2063 | 1 | sqm | 3465.84
| Cost of Stainless Steel Tower Bolt-10 mm Bolt (IS:15833) 150 mm Long TBSC-P.I-21 | 1 | No. | 166 |  | Each | 166
| Cost of MS powder coated Butt hinges 150mm long TBSC-P.II-12 | 3 | Nos. | 45 |  | Each | 135
| Cost of Stainless Steel aldrop 250mm long TBSC-P.IV-11 | 2 | No. | 312 |  | Each | 624
| Cost of Stainless Steel fancy handle 150mm long TBSC-P.III-17 | 2 | Nos. | 157 |  | Each | 314
| Add for MA @ 40% | 0.4 |  | 488.41 |  |  | 195.364
| Labour charges for fixing flush door shutter to the frame, fixing the fixtures to the shutter TBSC-T.I-25 | 1.68 | sqm | 550 | 1 | sqm | 924
| Add for MA @ 40% | 0.4 |  | 971.04 |  |  | 388.416
Add for nails & screws etc.
| Rate for 1.68 sqm | [5 empty] | 9957.62
| Overheads & Contractors Profit @ 13.615% | 0.13615 |  | 9957.62 |  |  | 1355.73
11313.35
| Rate for 1 sqm | [5 empty] | 6734.1369
[5 empty] | Or Say |  | 6734

## ELE-Datas
Electrical Datas (2022-23 SSR)
S.No | SSR Item No | Item Code | Description | Qty |  | Unit |  | Rate | Amount
57 |  |  | Supply and Transportation 56W Clean room Light fixture, 2' x2' (600mm x600mm) LED luminaire CRCA powder coated white after phosphocreatine treatment provided as standard. with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% including all accessories and labour charges etc., complete.
a) Labour charges
| 1 |  | Skilled Electrician. | 0.05 | day | 1 | day | 660 | 33
| 3 |  | Helper (Electrical). | 0.125 | day | 1 | day | 550 | 68.75
|  |  | Labour for 1 No | [5 empty] | 101.75
b) Material
| ELEC-1.5.5 |  | Supply of 23 / 0060 twin core twisted / flat heavy Copper wire. | 2 | Mtr | 100 | Mtrs | 1200 | 24
|  |  | Alluminium Flat (As per requirement) | [5 empty] | 50
| As per Price list of Philips | a | Supply and Transportation of 56W Clean room fitting, 2' x 2' (600mm x 600mm) slim panel LED luminaire | 1 | Nos | 1 | Nos | 15000 | 15000
|  |  | Cost of Material | [5 empty] | 15074
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 15175
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 2066.0763
17241.0762
|  |  | Rate per Each | [5 empty] | 17241
58 |  |  | Supply and Transportation of 48" ( 1200 mm) High Speed Fan Sweep Celing Fan with all accessories etc., complete. Make Havells S S 390
| As per price list |  | Supply and Transportation of 48" ( 1200 mm) High Speed Fan Sweep Celing Fan with all accessories etc., complete. Make Havells S S 390 | Each | 1 | 1 | Nos | 3800 | 3800
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 517.37
4317.37
|  |  | Rate per Each | [5 empty] | 4317
59 |  |  | Labour charges for fixing of ceiling fan and regulator including transportation and giving connections with twin core wire etc., complete. Makes : Finolex / RR Kabel / Havells / Polycab / GM / Million / V-Guard / Gold Medal / HPL / RPG.
a) Labour charges
| 1 |  | Skilled Electrician. | 0.125 | day | 1 | day | 660 | 82.5
| 2 |  | Helper (Electrical). | 0.125 | day | 1 | day | 550 | 68.75
|  |  | Labour for 1 No | [5 empty] | 151.25
b) Material
| 1.5.5 |  | Supply of 23 / 0060 twin core twisted / flat heavy Copper wire. | 1 | Mtrs | 100 | Mtrs | 1200 | 12
|  |  | Cost of Material for fixing fan | [5 empty] | 12
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 163
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 22.1924
185.1925
|  |  | Rate per Each | [5 empty] | 185
60 |  |  | Supply and fixing of Anchor fastner with fan hook / Providing MS Fan hook with grouting and cement plastering.
| ELEC-9.1.23 |  | Supply and fixing of Anchor fastner with fan hook / Providing MS Fan hook with grouting and cement plastering. | Each | 1 | 1 | Nos | 107 | 107
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 14.568
121.568
|  |  | Rate per Each | [5 empty] | 122
61 |  |  | Supply & fixing of 2nos6A, 2 in one socket - 2 Nos with 6A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benz Plus
a) Labour charges :
| 1 |  | Skilled Electrician. | 0.1 | day | 1 | day | 660 | 66
| 2 |  | Helper (Electrical). | 0.1 | day | 1 | day | 550 | 55
|  |  | Labour for 1 No | [5 empty] | 121
b) Material
| 1.3.1 | d | Supply of 6 Module box | 1 | No | 1 | No | 164 | 164
| 1.3.2 | d | Supply of 6 Modular Cover Frame. | 1 | Nos | 1 | No | 164 | 164
| 1.9.1 | a | 6 / 10A 1 Way 1 Module Modular Switch | 2 | Nos | 1 | No | 116 | 232
| 1.9.1 | d | 10A 3/2 Pin 2 Module Modular Socket with shutter | 2 | Nos | 1 | No | 178 | 356
|  |  | Cost of Material for 1 No | [5 empty] | 916
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 1037
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 141.1875
1178.1876
|  |  | Rate per Each | [5 empty] | 1178
63 |  |  | Labour charges for fixing the exhaust fan in wall with necessary connections and masonary work of making hole, finishing etc., complete. Makes : Finolex / Havells / Polycab / Finecab
a) Labour charges
| 1 |  | Skilled Electrician. | 0.25 | day | 1 | day | 660 | 165
| 2 |  | Lineman Electric / Telephone | 0.25 | day | 1 | day | 550 | 137.5
| 4 |  | Mason Cl- I / Brick layer Cl- I | 0.25 | day | 1 | day | 580 | 145
|  |  | Labour for 1 No | [5 empty] | 447.5
| 1.5.5 |  | Supply of 23 / 0060 twin core twisted / flat heavy Copper wire. | 1 | Mtrs | 100 | Mtrs | 1200 | 12
| 9.4.11 |  | Cement. | 25 | Kg | 1 | Kg | 9 | 225
|  |  | Sundries such as Sand, Bolt, Nuts etc. | 1 | Job | 1 | Job | 10 | 10
|  |  | Cost of Material for fixing fan | [5 empty] | 247
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 694
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 94.4881
788.4881
|  |  | Rate per Each | [5 empty] | 788
62 |  |  | Supply,Transportation of 15" (375mm) ISI, 900 RPM Heavy duty exhaust fan with metallic blades wiremesh with all accessories etc complete Makes : Crompton / Almonard / Havells Turbo Force SP.
| 5.1.11 | b | Supply of 15" (375mm) ISI, 900 RPM Heavy duty exhaust fan | Each | 1 | 1 | Nos | 3756 | 3756
|  |  | Transportation | 0.01 |  |  |  |  | 37.56
3793.56
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 516.4932
4310.0532
|  |  | Rate per Each | [5 empty] | 4310
64 |  |  | Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete
a) Labour charges
| 3 |  | Helper (Electrical). | 0.1 | day | 1 | day | 550 | 55
|  |  | Labour for 1 No | [5 empty] | 55
b) Material
| 9.1.21 |  | 19/20mm steel tube down rod with bolts & nuts for fan with maching colour. | 1 | Mtrs | 1 | Mtrs | 110 | 110
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 165
|  |  | Less cost of fan down rod supplied with new fan of about 9" in length equal to 0.23 Metre at above rate | 0.23 | Mtrs | 1 | Mtrs | 110 | 25.3
139.7
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 22.4647
162.1647
|  |  | Rate per Each | [5 empty] | 162
65 |  |  | Supply and fixing of 12 Way SPN DB with IP 43 Protection as per IS:13032 with 1 No 63A FP MCB as Incommer, and 8 Nos of 6-32A SP MCB 10KA, C/D Curve ISI Mark as out goings, concealing in wall etc complete. DB Makes :Legrand MCB Makes : Legrand-DX3
LABOUR
| 1 |  | Skilled Electrician. | 0.5 | day | 1 | day | 660 | 330
| 2 |  | Lineman Electric / Telephone | 0.5 | day | 1 | day | 550 | 275
| 3 |  | Mason Cl- I / Brick layer Cl- I | 0.5 | day | 1 | day | 580 | 290
895
MATERIAL
| 2.16.1 | f | Supply of 12 Way SPN DB | 1 | Nos | 1 | No | 2302 | 2302
| ELEC-2.14.1 | h | Supply of 40-63A FP MCB | 1 | No | 1 | No | 2651 | 2651
| ELEC-2.14.1 | a | Supply of 20A 10KA SP MCB, C/D Curve ISI Mark. | 8 | Nos | 1 | No | 294 | 2352
| ELEC-9.4.11 |  | Cement. | 12.5 | Kg | 1 | Kg | 9 | 112.5
7417.5
|  |  | TOTAL COST OF MATERIAL + LABOUR FOR FLUSH MOUNTING | FLUSH |  |  |  |  | 8312.5
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 1131.7469
9444.2469
|  |  | Rate per Each | [5 empty] | 9444
66 |  |  | Supply and fixing of cable adapteres box with cover for DBs including, massanory work etc., complete.,
| Approved rate in SOTC Gandhi Hospital |  | Supply and fixing of cable adopteres box with cover for DBs including, massanory work etc., complete., | 1 | Each | 1 | Nos | 5085 | 5085
5085
67 |  |  | Supply and Installation of control cum transmission wiring of size 4C x 2.5 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing and accessories as At Gandhi Hospital
b) Labour charges
| 1 |  | Skilled Electrician. | 0.7 | day | 1 | day | 660 | 462
| 2 |  | Lineman Electric / Telephone | 1 | day | 1 | day | 550 | 550
| 3 |  | Helper (Electrical). | 1 | day | 1 | day | 550 | 550
|  |  | Labour for 100 Mtrs | [5 empty] | 1562
|  |  | Labour for 1 Mtr | [5 empty] | 15.62
a) Material
| ELEC-1.5.6 | t | Supply of 2.5 Sqmm 4 Core PVC / XLPE Insulated Sheathed Multi Core Bright Annealed Bare Copper Conductor Heavy Duty Industrial Cables for Voltage Grade upto 1100 Volts as per IS: 694:1990 including all transportation charges etc complete. Makes :Polycab | 1 | Mtrs | 1 | Mtrs | 158 | 158
|  |  | Cost of Material for 1 Mtrs | [5 empty] | 158
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 173.6
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 23.6356
197.2356
|  |  | Rate per Meter for Cable | [5 empty] | 197
|  |  | Rate per Meter PVC Pipe - 25mm | [5 empty] | 92
|  |  | Rate per Meter | [5 empty] | 289
68 |  |  | Supply and Installation of control cum transmission wiring of size 2C x 1.5 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing and accessories as At Gandhi Hospital Makes : Polycab
b) Labour charges
| 1 |  | Skilled Electrician. | 0.7 | day | 1 | day | 660 | 462
| 2 |  | Lineman Electric / Telephone | 1 | day | 1 | day | 550 | 550
| 3 |  | Helper (Electrical). | 1 | day | 1 | day | 550 | 550
|  |  | Labour for 100 Mtrs | [5 empty] | 1562
|  |  | Labour for 1 Mtr | [5 empty] | 15.62
a) Material
| ELEC-1.5.6 | g | Supply of 1.5 Sqmm 2 Core PVC / XLPE Insulated Sheathed Multi Core Bright Annealed Bare Copper Conductor Heavy Duty Industrial Cables for Voltage Grade upto 1100 Volts as per IS: 694:1990 including all transportation charges etc complete. Makes :Polycab | 1 | Mtrs | 1 | Mtrs | 56 | 56
|  |  | Cost of Material for 1 Mtrs | [5 empty] | 56
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 71.6
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 9.7483
81.3483
|  |  | Rate per Meter for Cable | [5 empty] | 81
|  |  | Rate per Meter PVC Pipe - 25mm | [5 empty] | 92
|  |  | Rate per Meter | [5 empty] | 173
67&68 |  |  | Supply and Fixing of ISI 25mm outer dia medium grade, with IS:9537 part 3 rigid PVC with all accessories fixing on chromium plated metallic base saddles including all labour charges etc., complete for run of mains. Makes:- Sudhakar / Finolex / Modi / VIP / Precision / Universal / Million Plast / Gold / Polycab / DEC.
a) Labour charges :
| 1 |  | Skilled Electrician. | 2 | day | 1 | day | 660 | 1320
| 2 |  | Lineman Electric / Telephone | 2 | day | 1 | day | 550 | 1100
| 3 |  | Helper (Electrical). | 2 | day | 1 | day | 550 | 1100
| 4 |  | Mason Cl- I / Brick layer Cl- I |  | day | 1 | day | 580 | 0
|  |  | Labour Rate Per 100 Rm | [5 empty] | 3520
|  |  | Labour Rate for 1 Mtr | [5 empty] | 35.2
b) Material
| 9.4.11 |  | Cement. | 25 | kg | 1 | Kg | 9 | 225
| 9.1.2 |  | Rawl Plugs | 200 | Nos | 100 | Nos | 43 | 86
| 1.4.4 | d | 35mm Screws | 200 | Nos | 100 | Nos | 128 | 256
| 1.1.11 | b | Chromium Plated saddles with base | 200 | Nos | 100 | Nos | 279 | 558
| 1.2.6 | b | Supply of 25mm PVC Junction Boxes Normal. | 12 | Nos | 1 | Nos | 25 | 300
| 1.2.8 | b | Supply of 25mm dia 1.5mm thick PVC Bends. | 12 | Nos | 1 | Nos | 10 | 120
| 1.2.2 | b | Supply of ISI 25mm outer dia medium grade FRLS with IS:9537 part 3 regid PVC pipe. | 100 | Mtr | 1 | Mtr | 30 | 3000
|  |  | Material Rate for 100 Mtrs | [5 empty] | 4545
|  |  | Material Rate for 1 Mtr | [5 empty] | 45.45
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 80.6
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 10.9737
91.5737
|  |  | Rate per Meter | [5 empty] | 92
69 |  |  | 4C x 1.5 Sqmm Copper Flexible Cable For Condensing Unit to Electrical Panel Makes : Polycab
b) Labour charges
| 1 |  | Skilled Electrician. | 0.7 | day | 1 | day | 660 | 462
| 2 |  | Lineman Electric / Telephone | 1 | day | 1 | day | 550 | 550
| 3 |  | Helper (Electrical). | 1 | day | 1 | day | 550 | 550
|  |  | Labour for 100 Mtrs | [5 empty] | 1562
|  |  | Labour for 1 Mtr | [5 empty] | 15.62
a) Material
| ELEC-1.5.6 | s | Supply of 1.5 Sqmm 2 Core PVC / XLPE Insulated Sheathed Multi Core Bright Annealed Bare Copper Conductor Heavy Duty Industrial Cables for Voltage Grade upto 1100 Volts as per IS: 694:1990 including all transportation charges etc complete. Makes :Polycab | 1 | Mtrs | 1 | Mtrs | 99 | 99
|  |  | Cost of Material for 1 Mtrs | [5 empty] | 99
|  |  | Total Cost of Material + Labour Charges | [5 empty] | 114.6
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 15.6028
130.2028
|  |  | Rate per Meter | [5 empty] | 130
70 |  |  | Supply and fixing of FP Metal Enclosure with IP 20 Protection DB Make with 1 No 63A, 10 KA FP MCB including internal connection and labour charges for Flush Mounting etc.,complete. Makes of Enclousure : Legrand MCB Makes : Legrand-DX3
LABOUR
| 1 |  | Skilled Electrician. | 0.25 | day | 1 | day | 660 | 165
| 2 |  | Lineman Electric / Telephone | 0.25 | day | 1 | day | 550 | 137.5
| 3 |  | Mason Cl- I / Brick layer Cl- I | 0.15 | day | 1 | day | 580 | 87
|  |  | COST OF LABOUR FOR FULSH MOUNTING | [5 empty] | 389.5
MATERIAL
| 2.17.11 | b | Supply of DP/TP/FP Metal Enclosure with IP 20 Protection. | 1 | Nos | 1 | No | 614 | 614
| ELEC-2.14.1h | c | Supply of 40-63A 10KA FP MCB, C/D Curve ISI Mark. | 1 | Nos | 1 | No | 2651 | 2651
| 9.4.11 |  | Cement. | 5 | Kg | 1 | Kg | 9 | 45
|  |  | COST OF MATERIAL FOR FULSH MOUNTING | [5 empty] | 3310
|  |  | TOTAL COST OF MATERIAL + LABOUR FOR FULSH MOUNTING | [5 empty] | 3699.5
|  |  | Add Contractors Profit | 13.61% |  |  |  |  | 503.6869
4203.1869
|  |  | Rate per Each | [5 empty] | 4203
75 | Supply, Installation, testing and commissioning of EN54-2 Listed and LPCB approved based analog addressable fire control panel expandable by minimum 2 additional loops with minimum 80 character LCD display 4 access levels 1000 events, historical logging, flash E-PROM, 240 volts A C Power supply, automatic battery charger, 24V SLA batteries suitable for operating the entire system including tack back units and the hooters / strobes for a minimum of 4 hours in battery condition the panel shall have suitable power amplifiers for hooter / strobes the panel shall be capable beeing integrated with the BMS system and shall include cost of supply, installation of any additional modules or interfaces required for the same. The panel shall be completed as per the specification and as required for fixing of above Micro processor based Fire Alarm control panel with zonal indictions and battery back up as per detailed specifications. Makes: Ravel
| Rate as per SSR -2022-23 - ELEC - 10.2.2 D |  | 1 | 256450 |  |  | 1 | No. | 256450
| Overheads & Contractors Profit @ 13.615% |  | 0.13615 | 256450 |  |  |  |  | 34915.6675
| Rate for 1 No. | [7 empty] | 291365.6675
[5 empty] | Or Say |  |  |  | 291366

## EQP_List
S.No | Item Code | Description | QTY | UOM
1 | IVF001 | Ovum Aspiration Pumps at Gandhi Hospital | 2 | No
2 | IVF002 | IVF Test tube Warmers at Gandhi Hospital | 2 | No
3 | IVF003 | DICOM compatible fully digital, compact, portable, Ultrasound Scan Machine Colour Doppler at Gandhi Hospital | 2 | No
4 | IVF004 | Multipurpose Electro hydraulic with manual override mobile OT Table, with divided leg section suitable for all Gynaecological surgical procedures, complete with 5cm Mattress and corded handset at Gandhi Hospital | 1 | No
5 | IVF005 | LED procedure Lights Double dome at Gandhi Hospital | 1 | No
6 | IVF006 | LED procedure Lights Single dome at Gandhi Hospital | 1 | No
7 | IVF007 | IVF Workstation with LAF at Gandhi Hospital | 1 | No
8 | IVF008 | IVF Ant vibration Table for procedure at Gandhi Hospital | 1 | No
9 | IVF009 | CO2 Incubators at Gandhi Hospital | 2 | No
10 | IVF010 | Trigas bench Top Incubators for Human Embryo culture at Gandhi Hospital | 1 | No
11 | IVF011 | Trinocular Stereozoom Microscope at Gandhi Hospital | 1 | No
12 | IVF012 | ICSI Micro manipulator with Inverted Microscope at Gandhi Hospital | 1 | No
13 | IVF013 | IVF Laser System at Gandhi Hospital | 1 | No
14 | IVF014 | IVF Thermometer at Gandhi Hospital | 1 | No
15 | IVF015 | CO2 Cylinder and Manifold at Gandhi Hospital | 2 | No
16 | IVF016 | CO2 and O2 Analyzer at Gandhi Hospital | 1 | No
17 | IVF017 | PH Meter at Gandhi Hospital | 1 | No
18 | IVF018 | VOC Meter for ART Lab at Gandhi Hospital | 1 | No
19 | IVF019 | Sperm Counting Makler Chamber at Gandhi Hospital | 1 | No
20 | IVF020 | Binocular Microscope for Semen Analysis at Gandhi Hospital | 1 | No
21 | IVF021 | Laminar flow cabinet with Andrology Work station at Gandhi Hospital | 1 | No
22 | IVF022 | Clinical Centrifuge machine for Andrology at Gandhi Hospital | 1 | No
23 | IVF023 | Dry Incubators at Gandhi Hospital | 1 | No
24 | IVF024 | Pipetter and Denudation system at Gandhi Hospital | 1 | No
25 | IVF025 | Pharmaceutical Refrigerator at Gandhi Hospital | 1 | No
26 | IVF026 | Cryocans with wheels at Gandhi Hospital | 2 | No
27 | IVF027 | Defibrillator at Gandhi Hospital | 1 | No
28 | IVF028 | 7 Para Patient Monitor at Gandhi Hospital | 2 | No
29 | IVF029 | Suction machine at Gandhi Hospital | 1 | No
30 | IVF030 | Anaesthesia Work station at Gandhi Hospital | 1 | No
31 | IVF031 | Autoclave at Gandhi Hospital | 1 | No
32 | IVF032 | Operative Hysteroscopy and Resectoscope Set Machine at Gandhi Hospital | 1 | No
33 | IVF033 | Operative Laparoscopy Set at Gandhi Hospital | 1 | No
34 | IVF034 | Multifunctional Printer at Gandhi Hospital | 1 | No
35 | IVF035 | Ultrasound Examination Couch at Gandhi Hospital | 1 | No
36 | IVF036 | UPS 20KVA with battery backup at Gandhi Hospital | 0 | No
37 | IVF037 | Laptop for Office usage at Gandhi Hospital | 2 | No
38 | IVF038 | Reception Table at Gandhi Hospital | 0 | No
39 | IVF039 | Reception chair at Gandhi Hospital | 2 | No
40 | IVF040 | Filing Cabinet at Gandhi Hospital | 2 | No
41 | IVF041 | Patient Seating 3 in 1 model at Gandhi Hospital | 3 | No
42 | IVF042 | Consultant Chair at Gandhi Hospital | 3 | No
43 | IVF043 | Patient Chair at Gandhi Hospital | 6 | No
44 | IVF044 | Small Trolley at Gandhi Hospital | 3 | No
45 | IVF045 | Big Trolley at Gandhi Hospital | 3 | No
46 | IVF046 | Wall Storage Cabinets at Gandhi Hospital | 8 | No
47 | IVF047 | Office Table at Gandhi Hospital | 3 | No
1 |  | Fowler Two Function Bed with ABS Panel, ABS Side Railings, Wheels, Mattress Pillow, & Bed Fixing IV Road Features (Knee rest & Backrest) Size-L,84, W-42, H-24. The finished bed must be rust proof, pre-treated and treated with epoxy polyester antimicrobial powder coated to increase the bacteriostatic property. The bed must be quoted with washable cover of lasting quality. The mattress should be made of high-density PU foam of 100 mm thickness. | 5 | Nos
2 |  | Bed side Table with ABS Plastic body construction having 1 drawer and an adequated space with openable door with handle of size | 5 | Nos
3 |  | Corporate Deluxe Locker with SS 304 grade Top of size 508 x 406 x 762 mm having 1 drawer and an adequate storage space with openable door with SS handle. Equipped with wheels for easy movement. | 1 | Nos
4 |  | Bed side stand with full SS 304 grade constructionof size 406 x 203 x 762 mm equipped with SS Handles on top for carrying. | 1 | Nos
5 |  | Bed side stand with full GI Powder coated constructionof size 406 x 203 x 762 mm equipped with powder coated handles on top for carrying. | 1 | Nos
6 |  | Cryo Can 11 Ltr without wheels | 1 | Nos
7 |  | 3-Bay Surgical Scrub Station/Sink to be provided for use in the OT complex providing for pre-procedural scrub up with minimum three bay sink combination as suitable. The Scrub Station shall be made of Stainless Steel of 304 grade sheet with minimum thickness of 1.5mm and designed as per the high aesthetics of the theatre complex. Shall have smoothened surfaces & corners. The scrub sink shall be provided with a front access panel which shall be easily removed for access to the water-controlled valve, waste connections, stoppers & strainers. The Scrub station should be equipped with two foot operated and one elbow operated mechanisms. Shall have provision for fresh water and waste water piping ready for connections. | 1 | Nos
8 |  | Supply of Sample collection bed of size 1850x620x700 mm, featuring plain design equipped with 1 drawer and storage space with openable door type with SS-304 grade handles positioned at head side of the bed. The material of construction of the bed to be of Powder coated GI for entire body. All the legs of the bed to be capped with nylon bushes. The finished bed must be rust proof, pre-treated and treated with epoxy polyester antimicrobial powder coated to increase the bacteriostatic property. The bed must be quoted with washable cover of lasting quality. The mattress should be made of high-density PU foam of 100 mm thickness. | 1 | Nos
9 |  | Supply of a Sample collection chair of size 800x580x700 mm, meeting medical standards, featuring adjustable height and tilt padded armrests, and durable upholstery, suitable for comfortable patient positioning during blood donation or phlebotomy procedures. The chair is made from mild steel with good finish. The chair to be of easy to manoeuvre and transport and of light weight. | 1 | Nos
10 |  | Supply and installation of Stainless Steel 304 grade CSSD Rectangular Working table of size 1200x480x1050 mm with inbuilt sink of size 450x380x300 mm equipped with jali at bottom to stop any large particles entering into the drain to avoid drain clog. The table to be designed with raised front section and provision of SS sheet at foot level of the table forming a flat surface for storing/placing of items. The table to be of ready to use with all necessary fittings. | 1 | Nos
11 |  | Writing board made of Pressed wood coated with melamine surface. It has 900mm writing surface height, 1200mm writing surface wide, and 11mm deep, suitable for working on dry wipe board markers. It has an aluminium frame with dark grey plastic corner caps and maker tray. It is enabled with an easy wall mounting with a concealed slot system. It can be mounted either horizontally or vertically. IT consists of a complete mounting set, marker tray, and a board marker | 2 | Nos
12 |  | Providing MDF 18 mm thick wooden table of size 900x450 mm with 1 drawer at right side of the table. The table includes keyboard tray. Bottom equipped with nylone bushes for floor protection and easy movement. | 2 | Nos
13 |  | Supply of a 3-seater sofa upholstered with PU leather, with a high-quality finish. The sofa shall feature a kiln-dried hardwood frame for durability, reinforced with corner blocks for stability. The seat cushions to be constructed with high-density foam padding for comfort and resilience, while the backrests shall feature a combination of foam and fiberfill for optimal support. The sofa arms shall be padded for additional comfort, with sleek wooden or metal legs providing sturdy support. The leather upholstery shall be treated for resistance to stains and spills, ensuring longevity and ease of care. The dimensions of the sofa shall be suitable to accommodate three individuals comfortably, with ample seating space and ergonomic design considerations. | 2 | Nos
14 |  | SS-304 working table of size 685x685x762 mm with I type support inner frame SS-304 pipe of size 40x40x1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. | 2 | Nos
15 |  | SS-304 working table of size 457x457x762 mm with I type support inner frame SS-304 pipe of size 40x40x1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. | 1 | Nos
16 |  | SS-304 working table of size 610x610x762 mm with I type support inner frame SS-304 pipe of size 40x40x1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. | 1 | Nos
17 |  | SS-304 working table of size 660x610x762 mm with I type support inner frame SS-304 pipe of size 40x40x1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. | 1 | Nos
18 |  | Supply and fixing of Powder coated GI stand with 4 nos height adjustable racks of size 670x410x1570 mm connected to two big rods of rectangular hollow section type supported with 4 legs with wheels with brakes to restrict movement/easy movement. Equipped with frame for holding a cylinder. A lockable box type space to be provided at bottom rack. | 1 | Nos
19 |  | The Multipurpose Electro Hydraulic Mobile OT Table is designed for gynecological surgical procedures, featuring a wide range of adjustments for optimal patient positioning. It offers precise control with movement controls at the side of the table and a wired remote control handset and features like S. S. Arm Rest, Anaesthetic Screen, Lithotomy Leg Holders with Stirr-Ups, Leather Wristlets, Padded Leg Rest, Anti-static mattress, and an additional Poly-urethane mattress. Built with a Stainless Steel 304 frame and bottom, it ensures durability. The table top, reinforced with three-section stainless steel and radiolucent capabilities, allows for comprehensive patient support. Its flexibility includes 360° rotation, adjustable Trendelenburg, Reversed Trendelenburg, Head Section, Back Section, and Leg Section. Physical specifications include a 1900 mm x 525 mm top with an elevation range of 640mm to 1040mm, supporting patients up to 140 kg. Environmental considerations ensure operational efficiency in various conditions. | 1 | Nos