## RE
REVISED ESTIMATE OF MGMH PETLABURJ
S. No | Item Code | DESCRIPTION | As Per Agreement |  |  |  | As Per Workdone Estimate |  |  |  | EXCESS | REMARKS
|  |  | QTY | UNIT | RATE (Rs.) | AMOUNT (Rs.) | QTY | UNIT | RATE (Rs.) | AMOUNT (Rs.)
MGMH Petlaburj Hospital
Equipment Supplemental Works
1 |  | 3-Bay Surgical Scrub Station/Sink to be provided for use in the OT complex | 0 |  |  |  | 1 | Nos | 97000 | 97000 | 97000 | This item is mandatorily required for ICMR Clearance, Hence Procured | EQPS
2 |  | Supply and installation of Stainless Steel 304 grade CSSD Rectangular Working table of size 1200 x 480 x 1050 mm with inbuilt sink of size 450 x 380 x 300 mm in Autoclaavoom | 0 | Nos |  |  | 1 | Nos | 46000 | 46000 | 46000 | An autoclave needs a CSSD table. Hence Procured | EQPS
3 |  | SS-304 working table of size 685 x 685 x 762 mm in Embryology Lab | 0 | Nos |  |  | 2 | Nos | 16300 | 32600 | 32600 | It is necessary to place the equipments, hence procured as per the instructions of Enduser & TSMSIDC Higher officials. | EQPS
4 |  | SS-304 working table of size 457 x 457 x 762 mm in Andrology Lab | 0 | Nos |  |  | 1 | Nos | 14500 | 14500 | 14500 | It is necessary to place the equipments, hence procured as per the instructions of Enduser & TSMSIDC Higher officials. | EQPS
5 |  | SS-304 working table of size 610 x 610 x 762 mm in Andrology Lab | 0 | Nos |  |  | 1 | Nos | 15100 | 15100 | 15100 | It is necessary to place the equipments, hence procured as per the instructions of Enduser & TSMSIDC Higher officials. | EQPS
6 |  | SS-304 working table of size 660 x 610 x 762 mm in Embryology Lab | 0 | Nos |  |  | 1 | Nos | 15800 | 15800 | 15800 | It is necessary to place the equipments, hence procured as per the instructions of Enduser & TSMSIDC Higher officials. | EQPS
[6 empty] | 0 |  |  | PART-A | 221000 | 221000
Civil Works
248 | IVF248 | Dismantling clearing away of existing Flooring at MGMH Petlaburj | 400 | Sqm | 20 | 8000 | 729.93 | Sqm | 20 | 14599 | 6599 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
249 | IVF249 | Dismantling doors, windows Not exceeding 3 sqm in area: Doors 1.00x2.60M at MGMH Petlaburj | 16 | No | 350 | 5600 | 32 | No | 350 | 11200 | 5600 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
251 | IVF251 | Conveyance of un-useful excavated earth to a distance of 21 KM Dismantled Brick masonry and existing flooring. at MGMH Petlaburj | 120 | Cum | 455 | 54600 | 226.24 | Cum | 455 | 102939 | 48339 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
252 | IVF252 | Brick masonry for panel walls in superstructure with CM 1:8 prop: Aerated Cellular Autoclaved Concrete Blocks in 3rd Floor at MGMH Petlaburj | 10.5 | Cum | 14558 | 152859 | 20.08 | Cum | 14558 | 292325 | 139466 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
253 | IVF253 | Reinforced Masonry for partition walls 100 mm thick in CM 1:4 prop. Aerated Cellular Autoclaved Concrete Blocks in 3rd Floor at MGMH Petlaburj | 215 | Sqm | 1716 | 368940 | 227.17 | Sqm | 1716 | 389824 | 20884 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
256 | IVF256 | Plastering 12mm thick in two coats in 3rd Floor at MGMH Petlaburj | 430 | Sqm | 906 | 389580 | 905.88 | Sqm | 906 | 820727 | 431147 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
259 | IVF259 | Supplying and fixing of Unplasticised Poly Vinyl Chloride UPVC 3 track sliding windows at MGMH Petlaburj | 15 | Sqm | 9517 | 142755 | 39.8 | Sqm | 9517 | 378777 | 236022 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
264 | IVF264 | Flooring with non-skid full body ceramic floor tiles of size 300mm x 300mm and thickness between 7 - 8mm at MGMH Petlaburj | 12 | Sqm | 1395 | 16740 | 12.93 | Sqm | 1395 | 18037 | 1297 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
265 | IVF265 | Providing and fixing in true horizontal level 14 mm - Mineral Fiber sheet 595 x 595 Square in 3rd floor. at MGMH Petlaburj (False Ceiling) | 300 | Sqm | 1636 | 490800 | 438.85 | Sqm | 1636 | 717959 | 227159 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
266 | IVF266 | Providing dadooing to walls with glazed full body porcelain wall tiles of size 300 x 600 mm in 3rd Floor at MGMH Petlaburj | 30 | Sqm | 1391 | 41730 | 258.54 | Sqm | 1391 | 359629 | 317899 | As per the site condition and instructions of Higher officials, dadoing provided in the corridor area. Hence the qty exceeded and proposed as AE | C
267 | IVF267 | Providing and applying Wall putty of White Cement or Polymer or Cement based of average 1 to 2 mm thickness in 3rd floor Internal walls. at MGMH Petlaburj | 975 | Sqm | 315 | 307125 | 1448.95 | Sqm | 315 | 456419 | 149294 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
269 | IVF269 | Supply and application of one coat water based cement primer of interior grade I and two coats of water based PU paint in 3rd floor. at MGMH Petlaburj | 975 | Sqm | 259 | 252525 | 1127.93 | Sqm | 259 | 292134 | 39609 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
286 | IVF286 | Supply and installation of 50mm thick double skin ceiling system made of 0.8 mm thick Powder Coated GI sheets on both sides, at MGMH Petlaburj | 60 | sqm | 5135 | 308100 | 62.66 | sqm | 5135 | 321759 | 13659 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
287 | IVF287 | Double leaf clean room Doors : Size 1500 X 2100 mm with 300mm X 300mm double glazed view panels at MGMH Petlaburj | 4 | No | 46000 | 184000 | 5 | No | 46000 | 230000 | 46000 | As per the instructions of Higher officials Access Control Door Mandates the scientific door, the Qty. exceeded and now proposed as AE | C
288 | IVF288 | Single leaf clean room Doors : Size 900 X 2100 mm with 300 mm x 300 mm View panelat MGMH Petlaburj | 2 | No | 28700 | 57400 | 5 | No | 28700 | 143500 | 86100 | As per the instructions of Higher officials Autoclave Room, UPS Room & Electrical Room Mandates the scientific door, the Qty. exceeded and now proposed as AE | C
289 | IVF289 | Supply and installation of Extruded Aluminium Coving at MGMH Petlaburj | 100 | Rmt | 585 | 58500 | 109.8 | Rmt | 585 | 64233 | 5733 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
290 | IVF290 | Providing, laying of scratch proof PVC/Vinyl flooring of 2mm thickness at MGMH Petlaburj | 140 | Sqm | 4070 | 569800 | 173.31 | Sqm | 4070 | 705372 | 135572 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
Civil Supplimental Items
7 |  | Dismantling, clearing away of Old Cement Mortar | 0 | Sqm |  |  | 289.14 | Sqm | 13 | 3759 | 3759 | The work was taken up as per approved floor plan drawings and in contingent with the main work and hence proposed as supplemental item. | CS
8 |  | Dismantling, clearing away of Reinforced Cement Concrete | 0 | Cum |  |  | 0.59 | Cum | 4424 | 2610 | 2610 | The work was taken up as per approved floor plan drawings and in contingent with the main work and hence proposed as supplemental item. | CS
9 |  | Supply and Installation change room Cubicles at Petlaburj Hospital GENERAL SPECIFICATIONS: Thickness of compact Laminate:12mm Thick Colour OF HPL Boards | 0 | Sqm |  |  | 11.3 | Sqm | 9055 | 102322 | 102322 | This work was executed as per the requirement and instructions from higher officials | CS
10 |  | Providing, Fabricating and fixing full height V-board partitions of overall thickness of 75mm Partition frame | 0 | Sqm |  |  | 13.7 | Sqm | 1625 | 22263 | 22263 | This work is mandatory in contigent to the main work. Hence, executed. | CS
11 |  | Emergency Fire Doors : Size 1500 X 2100 mm with 2 hours fire rated and panic push bar and accessories etc. at MGMH Petlaburj | 0 | Nos |  |  | 1 | Nos | 55000 | 55000 | 55000 | This work was executed as per the requirement and instructions from higher officials | CS
12 |  | Providing of Factory made prelaminated FPVC (Foamed Polyvinyl Chloride) Door frame of the size 105x40mm with Maximum shutter size of : 910 x 2030 mm (ABS Doors) | 0 | Sqm |  |  | 32.08 | Sqm | 9241 | 296451 | 296451 | To maitain low VOC in Fertility center, wooden doors are replaced with ABS doors as per MOM dated: 01-08-2023. (copy Attached) | CS
13 |  | Providing and fixing factory made solid Wood Polymer Composite (WPC) single extruded Door (For Toilets) | 0 | Sqm |  |  | 9.21 | Sqm | 6734 | 62020 | 62020 | To maitain low VOC in Fertility center, wooden doors are replaced with WPC doors as per MOM dated: 01-08-2023. (copy Attached) | CS
14 |  | 50 LPH storage type RO of dimensions 525 x 425 x 1450 mm (WxDxH) In Autoclave room | 0 | Nos |  |  | 1 | Nos | 75000 | 75000 | 75000 | Autoclave needs clean water as per ICMR guidelines, hence this item is procured | CS
15 |  | Supply of Sun Control film to the glazed windows (For Windows & Door view Windows) |  |  |  |  | 48 | Sqm | 381 | 18288 | 18288 | This work was taken up at Record room, P Change room, Pre/Post Operative wards, Embryologist room, Store room and Semen Collection room as per the instructions issued by the End user and TSMSIDC higher officials. | CS
16 |  | Providing and fixing Aluminium Extruded Section Body Tubular Type Hydraulic Door Closer For all ABS doors |  |  |  |  | 15 | Nos | 2819 | 42285 | 42285 | This work was executed as per the requirement and instructions from higher officials | CS
17 |  | Supply and fixing of Dress Hangers of size 450mm length with 8 Nos hooks, (in change rooms). |  |  |  |  | 5 | Nos | 510 | 2550 | 2550 | This work was executed as per the requirement and instructions from higher officials | CS
18 |  | Supplying and fixing Rectangular Mirror Frameless of size 457 .2 mm x 609.6 mm (For Change room) |  |  |  |  | 5 | Nos | 1775 | 8875 | 8875 | This work was executed as per the requirement and instructions from higher officials | CS
19 |  | Name Plates (Room Names) as approved by the Engineer In-charge. |  |  |  |  | 38 | Nos | 600 | 22800 | 22800 | This work was executed as per the requirement and instructions from higher officials | CS
21 |  | Providing and fixing PVC frames on the walls for covering the area over DB Boxes at Entrance |  |  |  |  | 0.74 | Sqm | 6473 | 4790 | 4790 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
20 |  | AHU shed with provision for fencing, door with lock- key arrangement on Terrace Floor |  |  |  |  | 1 | Job | 300000 | 300000 | 300000 | This work was executed as per the requirement and instructions from higher officials | CS
22 |  | Providing Thermo Mechanically Treated ( TMT) ( Fe-500/500D/550D from primery producer TATA, SAIL, VSP, JSW Steel, Goel steel, Jindal panther, X- Vega & balaji Shakthi as per IS 1786-2008) of Different Diameters RCC Works , (For Lintels) | 0 | MT |  |  | 0.3 | MT | 95386 | 28616 | 28616 | This work is exectued as per site conditions. | CS
23 |  | Supplying and fixing of to windows / in open court yards using 25mm x 6mm MS flat alround and 10mm MS square bars For Windows (Window Grills) | 0 | Sqm |  |  | 39.78 | Sqm | 1791 | 71246 | 71246 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
24 |  | Supply and placing of the Design Mix Concrete M 25 grade corresponding to IS 456 (For Lintels) | 0 | Cum |  |  | 0.75 | Cum | 14683 | 11012 | 11012 | This work is exectued as per site conditions. | CS
25 |  | Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free fullbody porcelain vitrified tiles | 0 | Rmt |  |  | 174.5 | Rmt | 151 | 26350 | 26350 | This work was executed as per the requirement and instructions from higher officials | CS
[6 empty] | 3409054 |  |  | PART-A | 6475670 | 3066616
PLUMBING WORKS
272 | IVF272 | Supply and fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes 15.90mm OD pipe at MGMH Petlaburj | 60 | Rmt | 199 | 11940 | 95.61 | Rmt | 199 | 19026 | 7086 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | P
Plumbing Supplimental Works
26 |  | Supplying and fixing 50 mm Nominal Bore GI pipe Medium Grade properties (For Autoclave) | 0 | Rmt |  |  | 15 | Rmt | 599 | 8985 | 8985 | This work is mandatory for autoclave to let out the steam outside the premises. Hence executed. | PS
[6 empty] | 11940 |  |  | PART-A | 28011 | 16071
ELECTRICAL WORKS
293 | IVF293 | Supply and laying of ISI 25mm outer dia medium grade with IS:9537-part 3 rigid PVC pipe concealed in wall . at MGMH Petlaburj | 200 | Rmt | 116 | 23200 | 463.5 | Rmt | 116 | 53766 | 30566 | Qty increased to provide point wiring in all the rooms and corridors. And also to lay and run 2.5,4,6,10 sqmm wire various places necessary and proposed as AE | E
294 | IVF294 | Supply and laying of ISI 25mm outer dia medium grade with IS:9537-part 3 rigid PVC pipe surface on wall at MGMH Petlaburj | 450 | Rmt | 107 | 48150 | 1352.8 | Rmt | 107 | 144750 | 96600 | Qty increased to provide point wiring in all the rooms and corridors. And also to lay and run 2.5,4,6,10 sqmm wire various places necessary and proposed as AE | E
295 | IVF295 | Wiring with 2 runs of 22/0.3mm 1.5 Sq.mm FRLS / HFFR P.V.C. insulated flexible copper cable at MGMH Petlaburj | 100 | Pts | 945 | 94500 | 258 | Pts | 945 | 243810 | 149310 | Qty increased to provide adequate lighitng in rooms and corridors including Major OT, Embriology, Andriology, Manifold room, reception area etc. hence proposed as AE | E
296 | IVF296 | Supply and fixing of 6A ISI Mark 3/2 pin Modular socket with 6A 1way Modular switch, 3 Module box at MGMH Petlaburj | 12 | No | 675 | 8100 | 33 | No | 675 | 22275 | 14175 | Qty is increased as no of points increased and to provide proper power sockets in all the rooms and proposed as AE | E
298 | IVF298 | Supply and fixing of 16A/6A, 2 in one socket - 2 Nos with 16A switch control - 2 Nos modular type at MGMH Petlaburj | 60 | No | 1755 | 105300 | 77 | No | 1755 | 135135 | 29835 | Qty is increased due to extra points are used in Embrology ,Minor OT and other necessary areas and proposed as AE | E
300 | IVF300 | Supply and run of 1 of 22 /0.3mm 1.5 Sq.mm FRLS / HFFR P.V.C. insulated flexible copper cable at MGMH Petlaburj | 350 | Rmt | 40 | 14000 | 379.6 | Rmt | 40 | 15184 | 1184 | Qty is increased to connect all the fans to earthing, for safety of the equipments and proposed as AE | E
301 | IVF301 | Supply and run of 3 of 2.5 sq.mm 36/0.mm phase neutral and earth FRLS / HFFR PVC insulated flexible copper cable at MGMH Petlaburj | 600 | Rmt | 177 | 106200 | 1713.1 | Rmt | 177 | 303219 | 197019 | Qty is increased due to separate emergency line system is used for emergency light point for conveience of uninterupted power supply and proposed as AE | E
302 | IVF302 | Supply and 3 runs of 4.0 sq mm 56/0.3 mm phase neutral and earth FRLS / HFFR PVC insulated flexible copper cable at MGMH Petlaburj | 1200 | Rmt | 255 | 306000 | 2421 | Rmt | 255 | 617355 | 311355 | Qty is increased due to separate emergency line system is used for emergency light point for conveience of uninterupted power supply and proposed as AE | E
303 | IVF303 | Supply and run of 5 of 6.0 Sqmm 90/0.3 mm 3 phases, neutral and earth FRLS / HFFR PVC insulated flexible copper cable . at MGMH Petlaburj | 60 | Rmt | 606 | 36360 | 240.1 | Rmt | 606 | 145501 | 109141 | Qty is increased due to distribution system are provided at different positions as per site condition and proposed as AE | E
304 | IVF304 | Supply and run of 5 of 10.0 Sqmm 140/0.3 mm 3 phases, neutral and earth FRLS / HFFR PVC insulated flexible copper cable at MGMH Petlaburj | 40 | Rmt | 967 | 38680 | 284 | Rmt | 967 | 274628 | 235948 | Qty is increased due to distribution boards are provided at different positions as per site condition and proposed as AE | E
306 | IVF306 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 For Lighting DBs at MGMH Petlaburj | 3 | No | 18325 | 54975 | 10 | No | 18325 | 183250 | 128275 | Qty is increased due to number of curcuit lines are increased hence it was essential to provide separate distribtion system for UPS line, and Raw Power line and proposed as AE | E
311 | IVF311 | Supply, transportation and fixing of 24W edge lit LED Down light at MGMH Petlaburj | 50 | No | 2652 | 132600 | 91 | No | 2652 | 241332 | 108732 | Qty increased for better illumination, as per site requirement and proposed as AE | E
312 | IVF312 | Supply and Transportation 36W Edge lit, 2 feet x2 feet 600mm x600mm slim panel LED luminaire at MGMH Petlaburj | 30 | No | 4350 | 130500 | 60 | No | 4350 | 261000 | 130500 | Qty increased for better illumination, as per site requirement and proposed as AE | E
316 | IVF316 | Supply and fixing of Modular type Stepped electronic regulator for sweep AC ceiling fans of 1200mm / 1400mm. at MGMH Petlaburj | 12 | No | 827 | 9924 | 28 | No | 827 | 23156 | 13232 | Qty increased due to extra fans that are provided in waiting area,UPS room, electrical room, Main fold , and Androgoly lab and proposed as AE | E
317 | IVF317 | Supply and installation of 225mm Light duty exhaust fan at MGMH Petlaburj | 6 | No | 2203 | 13218 | 8 | No | 2203 | 17624 | 4406 | Qty increaed since provided in auto clave room and proposed as AE | E
318 | IVF318 | SITC of Hot dip galvanized perforated cable tray of 100 mm Wide sizes at MGMH Petlaburj | 70 | Rmt | 429 | 30030 | 79 | Rmt | 429 | 33891 | 3861 | Qty increaed due to cable lines provdied on terrace for AHU units and proposed as AE | E
319 | IVF319 | SITC of Hot dip galvanized perforated cable tray of 300 mm Wide sizes at MGMH Petlaburj | 80 | Rmt | 1310 | 104800 | 102.5 | Rmt | 1310 | 134275 | 29475 | Qty increased due to separate line system is used for UPS line and proposed as AE | E
321 | IVF321 | Supply and fixing of 12V 65 AH SMF battery including wire leads. Makes: Quanta / Racket / Exide. at MGMH Petlaburj | 20 | No | 20584 | 411680 | 32 | No | 20584 | 658688 | 247008 | As the UPS with isolation transformer requires min 32 nos of batteries to increase uptime of 60 minutes from 30 minutes considering the load. hence the Qty. exceeded and proposed as AE | E
324 | IVF324 | Providing and Fixing maintenance free earthing which consists of copper. Earth station, with 600X600 X3.15mm Copper Plate at MGMH Petlaburj | 2 | No | 22283 | 44566 | 4 | No | 22283 | 89132 | 44566 | Qty increased since suitable Resistance value was not getting to UPS systems. Hence proposed as AE | E
325 | IVF325 | Supply and installation of 50x6 GI flat for body earthing of electrical panel and AC Panel which is laid in 300mm cable tray at MGMH Petlaburj | 200 | Rmt | 329 | 65800 | 217.3 | Rmt | 329 | 71492 | 5692 | Qty increased due to separate earthing line is laid on terrace for AHU units and proposed as AE | E
327 | IVF327 | Supply and installation of 25x3 Copper flat for Neutral earthing of UPS and Equipment which is laid in 100mm cable tray at MGMH Petlaburj | 200 | Rmt | 902 | 180400 | 207.3 | Rmt | 902 | 186985 | 6585 | Qty is increased due to distance of earthing to earthing were difference as per site condition hence proposed as AE | E
328 | IVF328 | Supply and installation of 4 sqmm Copper wire for Earthing of DBs Equipment at MGMH Petlaburj | 80 | Rmt | 83 | 6640 | 450.6 | Rmt | 83 | 37400 | 30760 | Qty increased due to Separate earthing used for Distribution board body as it is necessary for DB's hence qty increased and proposed as AE | E
329 | IVF329 | Supply, Lying and testing of 3.5Cx95 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable at MGMH Petlaburj | 120 | Rmt | 1207 | 144840 | 180 | Rmt | 1207 | 217260 | 72420 | Qty increased due to incomming supply is drawn from Hospital Main panel board rather than Sub distribution Panel. Which is at a longer distance from the IVF Center and proposed as AE | E
330 | IVF330 | Supply, Lying and testing of 3.5CX50 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable at MGMH Petlaburj | 70 | Rmt | 722 | 50540 | 180 | Rmt | 722 | 129960 | 79420 | Qty increased due to incomming supply is drawn from Hospital Main panel board rather than Sub distribution Panel. Which is at a longer distance from the IVF Center and proposed as AE | E
331 | IVF331 | Supply, Lying and testing of 4Cx16 sqmm PVC Insulated Cable 1100V grade armoured aluminium cable at MGMH Petlaburj | 100 | Rmt | 1483 | 148300 | 160.4 | Rmt | 1483 | 237873 | 89573 | Qty increased due to AC unit Control system is fixed in Electrical room for controlling the unit from the site and proposed as AE | E
Electrical Supplimental Items
27 |  | Supply and Transportation 56W Clean room Light fixture, 2' x2' (600mm x600mm) LED luminaire | 0 | Nos |  |  | 12 | Nos | 17241 | 206892 | 206892 | During site inspection, The TSMSIDC higher officials has instructed to provide 56W lights to attain required illumination. Hence executed. | ES
28 |  | Supply and Transportation of 48" ( 1200 mm) High Speed Fan Sweep Celing Fan | 0 | Nos |  |  | 28 | Nos | 4317 | 120876 | 120876 | During site inspection The TSMSIDC higher officials instructed to provide regular high speed fans since maintaining BLDC fans in governement instutions is not viable. Hence executed | ES
29 |  | Labour charges for fixing of ceiling fan and regulator including transportation and giving connections with twin core wire etc., complete. | 0 | Nos |  |  | 28 | Nos | 185 | 5180 | 5180 | As per Instructions of the TSMSIDC higher officials during site inspection, regular high speed fans were provided. Hence executed | ES
30 |  | Supply & fixing of 2nos6A, 2 in one socket - 2 Nos with 6A switch control - 2 Nos modular type | 0 | Nos |  |  | 20 | Nos | 1178 | 23560 | 23560 | 6Amp socket was required as per site conditions. Hence executed | ES
31 |  | Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete | 0 | Nos |  |  | 28 | Nos | 162 | 4536 | 4536 | As difference in false ceilling one meter down rods are used as per site conditions | ES
32 |  | Supply and fixing of 12 Way SPN DB Horizontal with IP 43 Protection as per IS:13032 (For UPS DBs) | 0 | Nos |  |  | 2 | Nos | 9444 | 18888 | 18888 | It is mandatory to provide 12 Way SPN DB for UPS Distribution System Hence executed | ES
33 |  | Supply and fixing of cable adopteres box with cover for DBs including, massanory work etc., complete., | 0 | Nos |  |  | 8 | Nos | 5085 | 40680 | 40680 | It is mandatory to provide cable adapters to connect RAW power with UPS power. Hence executed | ES
34 |  | Supply and fixing of FP Metal Enclosure with IP 20 Protection DB Make with 1 No 63A, 10 KA DP MCB | 0 | Nos |  |  | 2 | Nos | 4203 | 8406 | 8406 | It is mandatory required to connect Power supply to autoclave and Air shower unit | ES
35 |  | 4C x 1.5 Sqmm Copper Flexible Cable For Condensing Unit to Electrical Panel Makes : Polycab |  |  |  |  | 210 | Rmt | 130 | 27300 | 27300 | It is mandatory to provide for AHU Connection System, Hence executed | ES
36 |  | Proving and fixing Track lights at side wall décor frame with 4 fixtures and 2 tracks |  |  |  |  | 1 | Job | 9600 | 9600 | 9600 | This work was executed as per the requirement and instructions from higher officials | ES
37 |  | Supply and fixing of suitable out door feeder piller box of size made with 14 SWG CRCA sheet with double door arrangement | 0 | Nos |  |  | 1 | Nos | 30768 | 30768 | 30768 | It is mandatory to provide fedder pillar box to control separate AC units on terrace for maintenace of units | ES
[6 empty] | 2309303 |  |  | PART-A | 4975627 | 2666324
AIR CONDITIONING
346 | IVF346 | Supply, transportation and installation of split AC unit 1.5 TR inverter type 3 Star at MGMH Petlaburj | 1 | No | 48000 | 48000 | 3 | No | 48000 | 144000 | 96000 | Qty increased so as to provide AC in UPS room and Reception and proposed as AE | AC
363 | IVF363 | SITC of Magnehelic gauges across pre and fine filter at AHUs including mounting arrangement, SS nozzles, food grade PVC tubing, etc. at MGMH Petlaburj | 2 | No | 10500 | 21000 | 3 | No | 10500 | 31500 | 10500 | Qty increased as per site condition and proposed as AE | AC
365 | IVF365 | SITC of Aluminium powder coated Fresh air and Exhaust Louvers of non- vision type with nylon mosquito net etc. at MGMH Petlaburj | 1 | Sqm | 10300 | 10300 | 1.8 | Sqm | 10300 | 18540 | 8240 | Qty increased as per site condition and proposed as AE | AC
368 | IVF368 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Supply air duct running inside the building. at MGMH Petlaburj | 40 | Sqm | 785 | 31400 | 76.7 | Sqm | 785 | 60210 | 28810 | Qty increased to provide proper covering from Dampness and moisture to copper pipe of IVF units and AHU units and proposed as AE | AC
369 | IVF369 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 19mm Thick for Return air running inside the building. at MGMH Petlaburj | 40 | Sqm | 660 | 26400 | 97.49 | Sqm | 660 | 64343 | 37943 | Qty increased to provide proper covering from Dampness and moisture to copper pipe of IVF units and AHU units and proposed as AE | AC
372 | IVF372 | VRF Indoor Units: Hi wall Splits: 1.0 TR at MGMH Petlaburj | 3 | No | 30700 | 92100 | 6 | No | 30700 | 184200 | 92100
373 | IVF373 | VRF Indoor Units: Hi wall Splits: 1.5 TR at MGMH Petlaburj | 4 | No | 35000 | 140000 | 6 | No | 35000 | 210000 | 70000 | Qty increased so as to provide AC in Senior faculty room & UPS Room and proposed as AE | AC
376 | IVF376 | Supply, Installation , Testing and Commissioning of Refnet joints to be provided in refrigerant pipe line.at MGMH Petlaburj | 10 | Set | 6191 | 61910 | 15 | Set | 6191 | 92865 | 30955 | Qty increased as the no of indoor units increased and proposed as AE | AC
Air Conditioning Supplemental Works
38 |  | Supply & Installation of MS Angle for Duct Support, Cable Tray Support and Condensing Unit Stand of size 50 X 50 x 5 mm Thick. | 0 | Kg |  |  | 211.24 | Kg | 190 | 40136 | 40136 | It is mandatorly required for support duct hence this work is executed as per the instructions of TSMSIDC Higher officials. | ACS
39 |  | Supply & Installation of MS Angle for Duct Support, Cable Tray Support and Condensing Unit Stand of size 32 X 32 x 5 mm Thick. | 0 | Kg |  |  | 74.25 | Kg | 190 | 14108 | 14108 | It is mandatorly required for support duct hence this work is executed as per the instructions of TSMSIDC Higher officials. | ACS
40 |  | Supply and installation of Canvas Connections For AHUS | 0 | Nos |  |  | 2 | Nos | 6500 | 13000 | 13000 | Its mandatorly required for support duct hence this work is executed as per the instructions of TSMSIDC Higher officials. | ACS
41 |  | Condensing units - VRF/VRV System : Supply, Installation, Nitrogen testing , Vacuuming and Commissioning of air cooled variable refrigerant flow modular type condensing units, at MGMH Petlaburj 22 HP | 0 | Nos |  |  | 1 | Nos | 402500 | 402500 | 402500 | As per the site condition & floor plans approved, the increa of indoor units as the new rooms added requires higher capacity of VRV system. Hence proposed as Supplimental item | ACS
42 |  | Cassette Units : 2.0 TR – 4 way at MGMH Petlaburj | 0 |  |  |  | 2 | Nos | 40000 | 80000 | 80000 | As per the site condition & floor plans approved, the pre & post operative ward requires less capacity units. Hence proposed as Supplimental item | ACS
43 |  | Modular Double skin floor mounted EUROVENT Certified Air Handling Unit 4400CFM / 11.0 TR at MGMH Petlaburj | 0 | Nos |  |  | 1 | Nos | 718500 | 718500 | 718500 | As per the site condition & floor plans approved, the increased area requires higher capacity of AHU. Hence proposed as Supplimental item. | ACS
44 |  | SITC of air cooled condensing units with two scroll compressors, air cooled condenser, 11.0 TR capacity at MGMH Petlaburj | 0 | Nos |  |  | 2 | Nos | 240750 | 481500 | 481500 | As per the site condition & floor plans approved, the increased area requires higher capacity of condensing unit to maintain required temperature and increase in AHU capacity too. Hence proposed as Supplimental item | ACS
[6 empty] | 431110 |  |  | PART-A | 2555402 | 2124292
MGPS
384 | IVF384 | SITC of C02 Manifold for 2 Cylinders, at MGMH Petlaburj | 1 | Set | 20750 | 20750 | 2 | Set | 20750 | 41500 | 20750 | Additional Manifold is provided to supply CO2 at 2-3 bar pressure to IVF OT and proposed as AE | G
387 | IVF387 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 15mm COPPER PIPE at MGMH Petlaburj | 114 | Rmt | 824 | 93936 | 201.23 | Rmt | 824 | 165814 | 71878 | Qty. increased as per the site requirement hence proposed as AE | G
388 | IVF388 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 22mm COPPER PIPE at MGMH Petlaburj | 36 | Rmt | 1191 | 42876 | 78.65 | Rmt | 1191 | 93672 | 50796 | Qty. increased as per the site requirement hence proposed as AE | G
MGPS Supplemental Works (RATES Adopted From IVF Gandhi Hospital RE)
45 |  | Fully Automatic Control Panel for Oxygen System: Supply, installation and commissioning of Fully Automatic control panel for unintrupted Oxygen supply | 0 | Set |  |  | 1 | Set | 175180 | 175180 | 175180 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
46 |  | Trigas Emergency Manifold: SITC of Emergency Trigas Manifold maximum for 1+1 D-type Gas Cylinders complete with separate NRVs, tail pipes and brass fittings for each cylinders. | 0 | Set |  |  | 1 | Set | 9620 | 9620 | 9620 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
47 |  | Fully Automatic Control Panel for Trigas System: Supply, installation and commissioning of Fully Automatic control panel for unintrupted Nirous Oxide supply. | 0 | Set |  |  | 1 | Set | 175180 | 175180 | 175180 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
48 |  | Fully Automatic Control Panel for CO2 System: Supply, installation and commissioning of Fully Automatic control panel for unintrupted Nirous Oxide supply. | 0 | Set |  |  | 1 | Set | 175180 | 175180 | 175180 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
49 |  | SITC of Medical Air-4 Outlet with matching probe as per HTM-2022/02-01 of UK/ NFPA 99C of USA as per enclosed technical Specification. | 0 | Nos |  |  | 6 | Nos | 12470 | 74820 | 74820 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
50 |  | 12 mm Valve for 12 mm OD Pipe Note: New item added | 0 | Nos. |  |  | 3 | Nos. | 930 | 2790 | 2790 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
51 |  | Supply and installation of 46.7 liter size CO2 cylinders confirming to IS:7285 Part-2 (2017). | 0 | Nos. |  |  | 2 | Nos | 20850 | 41700 | 41700 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
52 |  | Supply and installation of 46.7 liter size O2 cylinders confirming to IS:7285 Part-2 (2017). | 0 | Nos. |  |  | 2 | Nos | 17850 | 35700 | 35700 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
53 |  | Supply and installation of 46.7 liter size Trigas cylinders confirming to IS:7285 Part-2 (2017). | 0 | Nos. |  |  | 2 | Nos | 29250 | 58500 | 58500 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
54 |  | Supply and installation of 46.7 liter size N2O cylinders confirming to IS:7285 Part-2 (2017). | 0 | Nos. |  |  | 2 | Nos | 33000 | 66000 | 66000 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
[6 empty] | 157562 |  |  | PART-A | 1115656 | 958094
[5 empty] | TOTAL PART-A | 6318969 |  |  |  | 15371366 | 9052397
[7 empty] | As Per Agreement |  | Excess | 9052397
[7 empty] | As Per RE |  | Less | 2769434
[7 empty] | Difference |  | Difference | 6282963