## New_Abstract
Name of the work: Design, fabrication, establishing & commissioning of In-Vitro Fertility Centers (IVFCs) along with allied services on Turnkey basis at MGMH Petlaburj, Hyd.
COMPARATIVE STATEMENT
S.No | Description |  | As per Agreement | As per workdone | Excess | Less | Net Difference
PART-A
1 | Equipment |  | 26020475 | 26020475 | 0 | 0 | Details on Pg No.5 of RE
2 | Civil Works |  | 5915529 | 7012631 | 1910379 | 813277 | Details on Pg No.17 of RE
3 | Plumbing works |  | 215122 | 136973 | 7086 | 85235 | Details on Pg No.21 of RE
4 | Electrical works |  | 3719411 | 5641335 | 2169638 | 247714 | Details on Pg No.33 of RE
5 | ELV works |  | 689000 | 689000 | 0 | 0 | Details on Pg No.33 of RE
6 | Fire Fighting works |  | 873880 | 873880 | 0 | 0 | Details on Pg No.34 of RE
7 | Air Conditioning works |  | 3946060 | 2725391 | 374548 | 1595217 | Details on Pg No.43 of RE
8 | MGPS works |  | 1025822 | 1141255 | 143424 | 27991 | Details on Pg No.46 of RE
9 | Sub Total (Agreement Part-A) (1 to 8) |  | 42405299 | 44240940 | 4605075 | 2769434 | 1835641
10 | PART-B
11 | Equipment supplimental |  | 0 | 221000 | 221000 | 0 | Details on Pg No.48 of RE
12 | Civil supplimental works |  | 0 | 1156237 | 1156237 | 0 | Details on Pg No.55 of RE
13 | Plumbing supplimental works |  | 0 | 8985 | 8985 | 0 | Details on Pg No.56 of RE
14 | Electrical supplimental works |  | 0 | 496686 | 496686 | 0 | Details on Pg No.59 of RE
15 | Air Conditioning supplimental works |  | 0 | 1749744 | 1749744 | 0 | Details on Pg No.62 of RE
16 | MGPS supplimental works |  | 0 | 814670 | 814670 | 0 | Details on Pg No.65 of RE
17 | Sub Total (Supplimental Part-B) (11 to 16) |  | 0 | 4447322 | 4447322 | 0
18 | Basic Total (Part-A+Part-B) (9+17) |  | 42405299 | 48688262 | 9052397 | 2769434 | 6282963
19 | Provision towards Engineering Supervision Charges @ 4% on RE Value | 4% | 1696212 | 1947530 | 251318 | 0
20 | GST @ 18% |  | 7632953.82 | 8763887.16 | 1130933 | 0
21 | Total (Part-A+Part-B) (18 to 20) |  | 51734465 | 59399679 | 10434648 | 2769434 | 7665214
22 | TGMSIDC Mandatory Charges
23 | Labour Cess @ 1% on Basic Price of Revised Estimate | 1% |  | 486882.62 | 486883 | 0
24 | NAC @ 0.1% on Basic Price of Revised estimate | 0.1% |  | 48688.262 | 48688 | 0
25 | Provision towards Seniorage Charges on Civil Component |  |  | 448 | 448 | 0
26 | Provision towards DMF Charges 30% on Seniorage Charges | 30% |  | 134.4 | 134 | 0
27 | Provision towards SMFT Charges 2% on seniorage Charges | 2% |  | 8.96 | 9 | 0
28 | Provision towards Haritha Nidhi | 0.01% |  | 4868.8262 | 4869 | 0
29 | Sub total of S.No (23 to 27) |  |  | 541031 | 541031 | 0
30 | Provision towards GST 18% on Above Charges (on 29) | 18% |  | 97385.58 | 97386 | 0
31 | Provision towards Unforseen items and rounding off (LS) - |  | 3265535 | 910280 | 0 | 2355255 | 1. Rs. 9,10,280 is inclusive of GST @18% 2. Details on Page No.1 of LS Items List
32 | Sub total of S.No (29 to 31) |  | 3265535 | 1548696.58 | 638417 | 2355255
33 | Total (32+21) |  | 55000000 | 60948375.58 | 11073065 | 5124689 | 5948376
34 | TGMSIDC Mandatory Charges For LS Amount (Rs. 9,10,280)
35 | Labour Cess @ 1% on LS Amount | 1% |  | 9103 | 9103 | 0
36 | NAC @ 0.1% on LS Amount | 0.1% |  | 910 | 910 | 0
37 | Provision towards Haritha Nidhi on LS Amount | 0.01% |  | 91 | 91 | 0
38 | Provision towards Engineering Supervision Charges @ 4% on LS Amount | 4% |  | 36411 | 36411 | 0
39 | Sub Total (35 to 38) |  |  | 46515 | 46515 | 0 | 46515
40 | Total (39+33) |  | 55000000 | 60994890.58 | 11119580 | 5124689 | 5994891
41 | PART-C
42 | Equipment |  |  | 549100 | 549100 | 0 | Details on Part-C Pg No.1
43 | Furniture |  |  | 143905 | 143905 | 0 | Details on Part-C Pg No.1
44 | Basic Sub Total (42 to 43) |  | 0 | 693005 | 693005 | 0
45 | GST @ 18% on 44 |  | 0 | 124741 | 124741 | 0
46 | Total (44 to45) |  | 0 | 817746 | 817746 | 0 | 817746
47 | TGMSIDC Mandatory Charges
48 | Labour Cess @ 1% on Part-C (S.No 44) | 1% |  | 6930 | 6930 | 0
49 | NAC @ 0.1% on Part-C (S.No 44) | 0.1% |  | 693 | 693 | 0
50 | Provision towards Haritha Nidhi Part-C (S.No 44) | 0.01% |  | 69 | 69 | 0
51 | Provision towards Engineering Supervision Charges @ 4% on Part-C (S.No 44) | 4% |  | 27720 | 27720 | 0
52 | Sub Total (48 to 51) |  | 0 | 35412 | 35412 | 0
53 | Provision towards GST 18% on Above Charges (on 52) |  | 0 | 6374 | 6374 | 0
54 | Sub Total (52 to 53) |  | 0 | 41786 | 41786 | 0
55 | Total (PART-C) (54+46) |  | 0 | 859532 | 859532 | 0 | 859532
56 | Total (PART-A+B+C) (55+40) |  | 55000000 | 61854422.58 | 11979112 | 5124689 | 6854423
57 | PART-D
58 | Additional Items As Per End User Letter |  |  | 294400 | 294400 | 0 | Details on Part-D Pg No.1
59 | GST @ 18% on 58 |  |  | 52992 | 52992 | 0
60 | Sub Total (58 to 59) |  | 0 | 347392 | 347392 | 0
61 | TGMSIDC Mandatory Charges
62 | Labour Cess @ 1% on Part-D (S.No 58) | 1% |  | 2944 | 2944 | 0
63 | NAC @ 0.1% on Part-D (S.No 58) | 0.1% |  | 294 | 294 | 0
64 | Provision towards Haritha Nidhi on Part-D (S.No 58) | 0.01% |  | 29 | 29 | 0
65 | Provision towards Engineering Supervision Charges @ 4% on Part-D (S.No 58) | 4% |  | 11776 | 11776 | 0
66 | Sub Total (62 to 65) |  | 0 | 15043 | 15043 | 0
67 | Provision towards GST 18% on Above Charges (on 66) |  | 0 | 2708 | 2708 | 0
68 | Sub Total (66 to 67) |  | 0 | 17751 | 17751 | 0
69 | Total (PART-D) (68+60) |  | 0 | 365143 | 365143 | 0 | 365143
70 | Total (PART-A+B+C+D) (69+56) |  | 55000000 | 62219565.58 | 12344255 | 5124689 | 7219566
71 | Provision towards (LS) - Inaugration Expenses |  |  | 300000 | 300000
| Grand Total (70 to 71) |  | 55000000 | 62519565.58 | 12644255 | 5124689 | 7519566
|  |  | As per Admn. Sanction | 55000000 | Excess | 12644255
|  |  | As per Work done | 62519565.58 | Less | 5124689
|  |  | Difference | 7519565.58 | Difference | 7519566

## RE
REVISED ESTIMATE
S. No | Item Code | DESCRIPTION | As Per Agreement |  |  |  | As Per Workdone Estimate |  |  |  | EXCESS | LESS | REMARKS
|  |  | QTY | UNIT | RATE (Rs.) | AMOUNT (Rs.) | QTY | UNIT | RATE (Rs.) | AMOUNT (Rs.)
MGMH Petlaburj Hospital
|  | EQUIPMENT | [13 empty] | AS PER AGREEMENT | AS PER WORKDONE | EXCESS | LESS
199 | IVF199 | Ovum Aspiration Pumps at Petlaburj Hospital | 2 | No | 240000 | 480000 | 2 | No | 240000 | 480000 | 0 | 0 | The item executed as per agreement quantity | EQP | EQP | 26020475 | 26020475 | 0 | 0
|  | Qty V.Pg No-05 of MB-10 | [11 empty] | EQP | C | 5915529 | 7012631 | 1910379 | 813277
[14 empty] | EQP | P | 215122 | 136973 | 7086 | 85235
200 | IVF200 | IVF Test tube Warmers at Petlaburj Hospital | 2 | No | 49500 | 99000 | 2 | No | 49500 | 99000 | 0 | 0 | The item executed as per agreement quantity | EQP | E | 3719411 | 5641335 | 2169638 | 247714
|  | Qty V.Pg No-03 of MB-10 | [11 empty] | EQP | ELV | 689000 | 689000 | 0 | 0
[14 empty] | EQP | FF | 873880 | 873880 | 0 | 0
201 | IVF201 | DICOM compatible fully digital, compact, portable, Ultrasound Scan Machine Colour Doppler at Petlaburj Hospital | 2 | No | 1365000 | 2730000 | 2 | No | 1365000 | 2730000 | 0 | 0 | The item executed as per agreement quantity | EQP | AC | 3946060 | 2725391 | 374548 | 1595217
|  | Qty V.Pg No-03 of MB-10 | [11 empty] | EQP | G | 1025822 | 1141255 | 143424 | 27991
[14 empty] | EQP | EQPS | 0 | 221000 | 221000 | 0
202 | IVF202 | Multipurpose Electro hydraulic with manual override mobile OT Table, with divided leg section suitable for all Gynaecological surgical procedures, complete with 5cm Mattress and corded handset at Petlaburj Hospital | 1 | No | 563750 | 563750 | 1 | No | 563750 | 563750 | 0 | 0 | The item executed as per agreement quantity | EQP | CS | 0 | 1156237 | 1156237 | 0
|  | Qty V.Pg No-03 of MB-10 | [11 empty] | EQP | PS | 0 | 8985 | 8985 | 0
[14 empty] | EQP | ES | 0 | 496686 | 496686 | 0
203 | IVF203 | LED procedure Lights Double dome at Petlaburj Hospital | 1 | No | 312500 | 312500 | 1 | No | 312500 | 312500 | 0 | 0 | The item executed as per agreement quantity | EQP | ACS | 0 | 1749744 | 1749744 | 0
|  | Qty V.Pg No-03 of MB-10 | [11 empty] | EQP | GS | 0 | 814670 | 814670 | 0
EQP
204 | IVF204 | LED procedure Lights Single dome at Petlaburj Hospital | 1 | No | 187500 | 187500 | 1 | No | 187500 | 187500 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-03 of MB-10 | [11 empty] | EQP
EQP
205 | IVF205 | IVF Workstation with LAF at Petlaburj Hospital | 1 | No | 687500 | 687500 | 1 | No | 687500 | 687500 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-05 of MB-10 | [11 empty] | EQP
EQP
206 | IVF206 | IVF Ant vibration Table for procedure at Petlaburj Hospital | 1 | No | 96250 | 96250 | 1 | No | 96250 | 96250 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-06 of MB-10 | [11 empty] | EQP
EQP
207 | IVF207 | CO2 Incubators at Petlaburj Hospital | 2 | No | 825000 | 1650000 | 2 | No | 825000 | 1650000 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-03 of MB-10 | [11 empty] | EQP
EQP
208 | IVF208 | Trigas bench Top Incubators for Human Embryo culture at Petlaburj Hospital | 1 | No | 825000 | 825000 | 1 | No | 825000 | 825000 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-06 of MB-10 | [11 empty] | EQP
EQP
209 | IVF209 | Trinocular Stereozoom Microscope at Petlaburj Hospital | 1 | No | 309000 | 309000 | 1 | No | 309000 | 309000 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-06 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
210 | IVF210 | ICSI Micro manipulator with Inverted Microscope at Petlaburj Hospital | 1 | No | 2625000 | 2625000 | 1 | No | 2625000 | 2625000 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-06 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
211 | IVF211 | IVF Laser System at Petlaburj Hospital | 1 | No | 2560000 | 2560000 | 1 | No | 2560000 | 2560000 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-06 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
212 | IVF212 | IVF Thermometer at Petlaburj Hospital | 1 | No | 61875 | 61875 | 1 | No | 61875 | 61875 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-03 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
213 | IVF213 | CO2 Cylinder and Manifold at Petlaburj Hospital | 2 | No | 50000 | 100000 | 2 | No | 50000 | 100000 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-04 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
214 | IVF214 | CO2 and O2 Analyzer at Petlaburj Hospital | 1 | No | 378000 | 378000 | 1 | No | 378000 | 378000 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-04 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
215 | IVF215 | PH Meter at Petlaburj Hospital | 1 | No | 93750 | 93750 | 1 | No | 93750 | 93750 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-04 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
216 | IVF216 | VOC Meter for ART Lab at Petlaburj Hospital | 1 | No | 731250 | 731250 | 1 | No | 731250 | 731250 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-06 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
217 | IVF217 | Sperm Counting Makler Chamber at Petlaburj Hospital | 1 | No | 75625 | 75625 | 1 | No | 75625 | 75625 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-04 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
218 | IVF218 | Binocular Microscope for Semen Analysis at Petlaburj Hospital | 1 | No | 41250 | 41250 | 1 | No | 41250 | 41250 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-06 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
219 | IVF219 | Laminar flow cabinet with Andrology Work station at Petlaburj Hospital | 1 | No | 250000 | 250000 | 1 | No | 250000 | 250000 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-06 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
220 | IVF220 | Clinical Centrifuge machine for Andrology at Petlaburj Hospital | 1 | No | 34500 | 34500 | 1 | No | 34500 | 34500 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-04 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
221 | IVF221 | Dry Incubators at Petlaburj Hospital | 1 | No | 563750 | 563750 | 1 | No | 563750 | 563750 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-04 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
222 | IVF222 | Pipetter and Denudation system at Petlaburj Hospital | 1 | No | 103125 | 103125 | 1 | No | 103125 | 103125 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-06 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
223 | IVF223 | Pharmaceutical Refrigerator at Petlaburj Hospital | 1 | No | 225000 | 225000 | 1 | No | 225000 | 225000 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-04 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
224 | IVF224 | Cryocans with wheels at Petlaburj Hospital | 2 | No | 61875 | 123750 | 2 | No | 61875 | 123750 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-04 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
225 | IVF225 | Defibrillator at Petlaburj Hospital | 1 | No | 312500 | 312500 | 1 | No | 312500 | 312500 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-04 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
226 | IVF226 | 7 Para Patient Monitor at Petlaburj Hospital | 2 | No | 280000 | 560000 | 2 | No | 280000 | 560000 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-04 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
227 | IVF227 | Suction machine at Petlaburj Hospital | 1 | No | 49500 | 49500 | 1 | No | 49500 | 49500 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-14 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
228 | IVF228 | Anaesthesia Work station at Petlaburj Hospital | 1 | No | 937500 | 937500 | 1 | No | 937500 | 937500 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-05 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
229 | IVF229 | Autoclave at Petlaburj Hospital | 1 | No | 562500 | 562500 | 1 | No | 562500 | 562500 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-06 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
230 | IVF230 | Operative Hysteroscopy and Resectoscope Set Machine at Petlaburj Hospital | 1 | No | 2125000 | 2125000 | 1 | No | 2125000 | 2125000 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-15 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
231 | IVF231 | Operative Laparoscopy Set at Petlaburj Hospital | 1 | No | 4200000 | 4200000 | 1 | No | 4200000 | 4200000 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-15 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
232 | IVF232 | Multifunctional Printer at Petlaburj Hospital | 1 | No | 43750 | 43750 | 1 | No | 43750 | 43750 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-05 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
233 | IVF233 | Ultrasound Examination Couch at Petlaburj Hospital | 1 | No | 81250 | 81250 | 1 | No | 81250 | 81250 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-05 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
234 | IVF234 | UPS 20KVA with battery backup at Petlaburj Hospital | 1 | No | 0 |  | 0 | No | 0 |  | 0 | 0 | Item Deleted | EQP
[11 empty] | 0 | 0 |  | EQP
235 | IVF235 | Laptop for Office usage at Petlaburj Hospital | 2 | No | 115000 | 230000 | 2 | No | 115000 | 230000 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-05 of MB-10 | [7 empty] | 0 | 0 | 0 |  | EQP
[10 empty] | 0 | 0 | 0 |  | EQP
236 | IVF236 | Reception Table at Petlaburj Hospital | 1 | No | 110000 | 110000 | 1 | No | 110000 | 110000 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-07 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
237 | IVF237 | Reception chair at Petlaburj Hospital | 2 | No | 34500 | 69000 | 2 | No | 34500 | 69000 | 0 | 0 | The item executed as per agreement quantity | EQP
[11 empty] | 0 | 0 |  | EQP
238 | IVF238 | Filing Cabinet at Petlaburj Hospital | 2 | No | 34500 | 69000 | 2 | No | 34500 | 69000 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-07 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
239 | IVF239 | Patient Seating 3 in 1 model at Petlaburj Hospital | 3 | No | 38500 | 115500 | 3 | No | 38500 | 115500 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-07 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
240 | IVF240 | Consultant Chair at Petlaburj Hospital | 3 | No | 20000 | 60000 | 3 | No | 20000 | 60000 | 0 | 0 | Embryologist, Anethesist and Sr. Faculty Room Requires this furniture as per the instructions of Enduser & TSMSIDC Higher officials. hence procured | EQP
|  | AE | [5 empty] | No | 20000 | 0 | 0 |  |  | EQP
[11 empty] | 0 | 0 |  | EQP
241 | IVF241 | Patient Chair at Petlaburj Hospital | 6 | No | 13750 | 82500 | 6 | No | 13750 | 82500 | 0 | 0 | Embryologist, Anethesist and Sr. Faculty Room requires this furniture as per the instructions of Enduser & TSMSIDC Higher officials. hence procured | EQP
|  | AE | [5 empty] | No | 13750 | 0 | 0 |  |  | EQP
[11 empty] | 0 | 0 |  | EQP
242 | IVF242 | Small Trolley at Petlaburj Hospital | 3 | No | 39200 | 117600 | 3 | No | 39200 | 117600 | 0 | 0 | The item executed as per agreement quantity | EQP
[11 empty] | 0 | 0 |  | EQP
243 | IVF243 | Big Trolley at Petlaburj Hospital | 3 | No | 62500 | 187500 | 3 | No | 62500 | 187500 | 0 | 0 | The item executed as per agreement quantity | EQP
[11 empty] | 0 | 0 |  | EQP
244 | IVF244 | Wall Storage Cabinets at Petlaburj Hospital | 8 | No | 17500 | 140000 | 8 | No | 17500 | 140000 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-07 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
245 | IVF245 | Office Table at Petlaburj Hospital | 3 | No | 20000 | 60000 | 3 | No | 20000 | 60000 | 0 | 0 | The item executed as per agreement quantity | EQP
|  | Qty V.Pg No-07 of MB-10 | [11 empty] | EQP
[11 empty] | 0 | 0 |  | EQP
246 | IVF246 | Consumables and Media for 100 Cycles at Petlaburj Hospital | 1 | Lot |  |  | 0 | Lot | 0 |  | 0 | 0 | Item Deleted | EQP
[11 empty] | 0 | 0 |  | EQP
[6 empty] | 26020475 |  |  | PART-A | 26020475 | 0 | 0 | 0
[5 empty] | As Per Agreement | 26020475 |  |  | Excess | 0
[5 empty] | As Per Workdone | 26020475 |  |  | Less | 0
[5 empty] | Net Difference | 0 |  |  | Net Difference | 0
Civil Works
247 | IVF247 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges, etc., complete. Brick Masonry at MGMH Petlaburj. | 80 | Cum | 398 | 31840 | 20.57 | Cum | 398 | 8187 | 0 | 23653 | The qty is utilised as per site condition and hence savings | C
|  | Qty V.Pg No-01 of MB-10, Qty V.Pg No-01 of MB-11 | [11 empty] | C
[11 empty] | 0 | 0 |  | C
248 | IVF248 | Dismantling clearing away and carefully stacking useful materials for re use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges etc complete for Flooring at MGMH Petlaburj | 400 | Sqm | 20 | 8000 | 400 | Sqm | 20 | 8000 | 0 | 0 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
|  | AE |  |  |  |  | 329.93 | Sqm | 20 | 6599 | 6599 | 0 |  | C
|  | Qty V.Pg No-01 of MB-10 | [11 empty] | C
C
249 | IVF249 | Dismantling doors, windows and clear storey windows, Ventilators etc., wood or steel shutters including Chowkhats, architraves, hold fasts and other attachments etc., and stacking them within 100m lead including labour charge etc., and complete for finished item of work. Not exceeding 3 sqm in area: Doors 1.00x2.60M at MGMH Petlaburj | 16 | No | 350 | 5600 | 16 | No | 350 | 5600 | 0 | 0 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
|  | AE |  |  |  |  | 16 | Sqm | 350 | 5600 | 5600 | 0 |  | C
|  | Qty V.Pg No-01 of MB-10 | [11 empty] | C
C
250 | IVF250 | Dismantling doors, windows and clear storey windows, Ventilators etc., wood or steel shutters including Chowkhats, architraves, hold fasts and other attachments etc., and stacking them within 100m lead including labour charge etc., and complete for finished item of work. Exceeding 3 sqm in area: Doors1.50x2.60M at MGMH Petlaburj | 5 | No | 468 | 2340 | 0 | No | 468 |  | 0 | 2340 | Not executed as per site conditions hence savings | C
[11 empty] | 0 | 0 |  | C
251 | IVF251 | Conveyance of un-useful excavated earth to a distance of 21 KM for disposal including hire charges of T and P, labour charges etc., complete for finished item of work. Dismantled Brick masonry and existing flooring. at MGMH Petlaburj | 120 | Cum | 455 | 54600 | 120 | Cum | 455 | 54600 | 0 | 0 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C | 106.24
|  | AE |  |  |  |  | 106.24 | Cum | 455 | 48339 | 48339 | 0 |  | C
252 | IVF252 | Brick masonry for panel walls in superstructure with CM 1:8 prop: Aerated Cellular Autoclaved Concrete Blocks conforming to IS:2185 Part-3 - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600 x 200 x 200 mm including cost and conveyance of all materials like cement, screened sand, bricks, water etc., to site, including sales and other taxes on all materials and such as labour charges, like mixing cement mortar, scaffolding charges, constructing masonry, lift charges, curing, etc.,complete for finished item of work. TSSS No.501 and 504. 3rd Floor at MGMH Petlaburj | 10.5 | Cum | 14558 | 152859 | 10.5 | Cum | 14558 | 152859 | 0 | 0 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
|  | AE |  |  |  |  | 9.58 | Cum | 14558 | 139466 | 139466 | 0 |  | C
|  | Qty V.Pg No-01 of MB-10, Qty V.Pg No-02 of MB-11 | [11 empty] | C
C
253 | IVF253 | Reinforced Masonry for partition walls 100 mm thick in CM 1:4 prop. Aerated Cellular Autoclaved Concrete Blocks conforming to IS:2185 Part-3- 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600 x 200 x 100 mm and placing 2Nos. of 6mm M.S plain rods in every third layer with free ends of the reinforcement pegged into mortar joints of main brick walls where applicable including cost and conveyance of all materials like cement, steel, sans, brick, water etc., to site, including sales and other taxes excluding GST on all materials, all operational, incidents charges, constructing masonry, lift charges, curing, complete for finished item of work. TSSS No. of 509. 3rd Floor at MGMH Petlaburj | 215 | Sqm | 1716 | 368940 | 215 | Sqm | 1716 | 368940 | 0 | 0 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
|  | AE |  |  |  |  | 12.17 | Sqm | 1716 | 20884 | 20884 | 0 |  | C
|  | Qty V.Pg No-01 of MB-10, Qty V.Pg No-02 of MB-11 | [11 empty] | C
C
254 | IVF254 | Providing Mild steel MS steel bars Fe 250 grade as per IS 432 of different diameters including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying including sales and other taxes on all materials etc. , complete for finished item of work. TSSS No.126 For RBM walls 6mm dia: 3rd Floor at MGMH Petlaburj | 0.9 | MT | 116500 | 104850 | 0 | MT | 116500 |  | 0 | 104850 | Not executed as per site conditions hence savings | C
[11 empty] | 0 | 0 |  | C
255 | IVF255 | Plastering 20mm thick in two coats using screened sand with base coat of 16mm thick in CM1:6 and top coat of 4mm thick in CM1:4 with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales and other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., complete for finished item of work .SS 901,903and 904 3rd Floor at MGMH Petlaburj | 45 | Sqm | 945 | 42525 | 39.56 | Sqm | 945 | 37384 | 0 | 5141 | The qty is utilised as per site condition and hence savings | C
|  | Qty V.Pg No-04 of MB-11 | [11 empty] | C
[11 empty] | 0 | 0 |  | C
256 | IVF256 | Plastering 12mm thick in two coats using screened sand with base coat of 8mm thick in CM 1:6 and top coat of 4mm thick in CM 1:4 with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales and other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and complete for finished item of work. SS 901,903 and 904. 3rd Floor at MGMH Petlaburj | 430 | Sqm | 906 | 389580 | 430 | Sqm | 906 | 389580 | 0 | 0 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
|  | AE |  |  |  |  | 475.88 | Sqm | 906 | 431147 | 431147 | 0 |  | C
|  | Qty V.Pg No-02 of MB-10, Qty V.Pg No-03 of MB-11 | [11 empty] | C
C
257 | IVF257 | Providing and laying screed plain cement concrete as per site condition for floor bedding using high quality aggregates including base preparation, compaction, levelling, all lead and lifts, rough finishing at the top surface, curing, shuttering if necessary etc., complete as directed . at MGMH Petlaburj | 20 | Sqm | 4670 | 93400 | 0 | Sqm | 4670 |  | 0 | 93400 | Not executed as per site conditions hence savings | C
[11 empty] | 0 | 0 |  | C
258 | IVF258 | Supply and fixing powder coated aluminium fully glazed swing door as per the approved drawing with fixed fan light of 500mm height at top door using aluminium sections of 101.60 mm x44.45mm , 3.18 mm thick for frame and door shutter made of styles , top and middle rail of 47.62mm x 44.45mm, 3.18 mm thick and bottom rail of 96.00mm x 44.45 mm,3.18mm thick, powder coating of aluminium sections 25mm microns thick, 5 mm thick plain glass fitted with suitable aluminium glazing clips and rubber beading in fan light portion, double shutters fitted with 5mm thick frosted glass in the top half and 12mm thick prelaminated particle board One side choice colour and other side balancing white lamination in the bottom half fitted with suitable aluminium glazing clips and rubber beading, as approved by Engineer-in-Charge including supply and fixing ISI marked powder coated aluminium fixtures of 2 Nos. tower bolts 10mm bolt IS:204 300mm long, 4 Nos. aluminium handles IS:208 150mm dia and 1 Nos. aldrops IS:2681 250mm, 1 No. door closure, Al. Butt hinges 125mm long 6Nos including labour charges for manufacturing door , fixing the door with required No. of screws etc., complete for finished item of work. The Aluminium section used shall be standard make confirming to IS 1948-1961 and as approved by the Engineer 1200mmx2100mm at MGMH Petlaburj | 5 | Sqm | 13713 | 68565 | 0 | Sqm | 13713 |  | 0 | 68565 | As per the instructions issued during site visit Dt. 01.08.2023. ABS doors were proposed hence qty not utilised | C
C
[11 empty] | 0 | 0 |  | C
259 | IVF259 | Supplying and fixing of Unplasticised Poly Vinyl Chloride UPVC 3 track sliding windows with mesh shutter – 2-glass shutters and 1-mesh shutter duly manufactured using UPVC reinforced profiles Composition of profile shall consists a minimum of 5.5 PHR of TiO2 and not more than 12 PHR of CaCo3 for every 100 parts of PVC resin of 94mm x 45 mm/80 mm x 52 mm x 2.20 mm for outer frames, 58 mm x 39 mm/54 mm x 38 mm x 2.20mm for sliding shutter frames capable of mounting single glazing system structurally reinforced with hot dip galvanized up to 50 microns of minimum thickness of 1.0/1.2 mm prefabricated and welded through fusion welding. The window sash shall be fitted with 5 mm thick clear float glass of reputed make and mesh shutter frame shall be 42 mm x 25mm/52 mm x 21.5 mm x 2.0 mm fitted with Vinyl Coated Fiber mesh- on rollers/ pulley duly fixed with Grey colour TPV Gasket for sash and Glazing bead shall be co- extruded with Grey colour soft PVC. System shall have single point locking with Touch Lock and the system is to be installed at the site using anchor fasteners, silicon rubber sealant, easy glazing/deglazing at site etc., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site includingetc., complete for finished item of work. at MGMH Petlaburj | 15 | Sqm | 9517 | 142755 | 15 | Sqm | 9517 | 142755 | 0 | 0 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
|  | AE |  |  |  |  | 24.8 | Sqm | 9517 | 236022 | 236022 | 0 |  | C
|  | Qty V.Pg No-14 of MB-10 | [11 empty] | C
C
260 | IVF260 | Providing, supplying and fixing of Fixed Louvered Ventilator made out of multi chambered uPVC sections with Glazing bead shall be co-extruded with Grey colour soft PVC. having isolated drainage and reinforced with Galvanized Iron profiles throughout the window. The outer frame having an overall size of 60 mm x 55 mm x 2.40 with reinforcement of 1 mm thickness and Mullion with overall size of 74 mm x 60 mm x 2.40 mm with reinforcement of 1 mm thickness. Composition of profile shall consists a minimum of 5.5 PHR of TiO2 and not more than 12 PHR of CaCo3 for every 100 parts of PVC resin. Ventilator shall be provided with 4.5 mm Pin Head glass, standard hardware. Wall thickness of frame and Mullion shall be 2.4 mm., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site etc., complete for finished item of work hinges IS:205 150mm long, 1 No. aldrop IS:2681 300mm long, 1 No. tower bolt IS:204 of 200 mm x 10 mm dia at top, 2 Nos. 150 mm at MGMH Petlaburj | 5 | Sqm | 8564 | 42820 | 1.96 | Sqm | 8564 | 16785 | 0 | 26035 | The qty is utilised as per site condition and hence savings | C
|  | Qty V.Pg No-14 of MB-10 | [11 empty] | C
[11 empty] | 0 | 0 |  | C
261 | IVF261 | Supply and fixing doors as per drawings with medium teak wood frame of section 100mm x 65 mm and ISI marked flush door shutters of 30 mm thick single shutter with bond wood solid block board type Core having cross bands and face veneers, hot pressed bonded with water proof phenol formaldehyde synthetic resin factory made conforming to IS 2202-1991 Part- I both sides commercial ply with internal lipping on all sides including cost and conveyance to site of teak wood frame, flush shutter including supply and fixing 6 Nos. MS Z hold fasts of size 300 mm x 40 mm x 5mm including cost of ISI marked Aluminium fixtures of 3 Nos. butt long handles IS:208, 1 No. door stopper and 1 No. rubber bush including fixing the fixtures to door with required number of screws, bolt and nuts including labour charges for fixing the frame in position, fixing the shutter to the frame etc., complete for finished item of work as per APSS 1001 and 1002 The vertical frame of door shall be embedded in flooring for a depth of not less than 10 mm 1000mm x 2100mm at MGMH Petlaburj | 35 | Sqm | 5593 | 195755 | 0 | Sqm | 5593 |  | 0 | 195755 | As per the instructions issued during site visit Dt. 01.08.2023. ABS doors were proposed hence qty not utilised | C
[11 empty] | 0 | 0 |  | C
262 | IVF262 | Supply and fixing doors as per drawings with medium teak wood frame of section 100mm x 65mm and ISI marked flush door shutter of 30mm thick single shutter with bond wood solid block board type Core having cross bands and face veneers, hot pressed bonded with water proof phenol formaldehyde synthetic resin factory made conforming to IS 2202-1991 Part- I both sides commercial ply with internal lipping on all sides including cost and conveyance to site of medium teak wood door frame, flush shutter, including suply and fixing 6 Nos. MS Z hold fasts of size 300mm x 40mm x 5mm including ISI marked Aluminium fixtures 3 Nos. butt hinges IS:205 of 150mm long, 1 No. aldrop IS:2681 250 mm long, 1 No. tower bolt IS:204 of 150 mm x 10mm dia, 2 Nos. 125mm long handles IS:208,1 No. rubber bush including supplying and fixing 1.20mm thick PVC sheet to full height of the shutter inside including labour charges for fixing the frame in position, fixing the shutter to the frame etc., complete for finished item of work as per APSS 1001 and 1002. The vertical frame of door shall be embedded in flooring for depth of not less than 10mm 750mm x 2100mm. at MGMH Petlaburj | 10 | Sqm | 6502 | 65020 | 0 | Sqm | 6502 |  | 0 | 65020 | As per the instructions issued during site visit Dt. 01.08.2023. ABS doors were proposed hence qty not utilised | C
[11 empty] | 0 | 0 |  | C
263 | IVF263 | Flooring with soluble salt porcelain vitrified tiles screen printed and polished of size 600 x 600 mm and thickness between 8 to 10mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630Parts 1 to 15 of any colour and finish in all shades and designs with borders and design as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM 1:8 prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread at the rate 3.3 kgs per Sqm. and jointed neatly with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site excluding cost of C.C. bed including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in- charge etc., and complete for finished item of work. TSSS No.701 and 707. 3rd Floor at MGMH Petlaburj | 360 | Sqm | 1593 | 573480 | 294.66 | Sqm | 1593 | 469393 | 0 | 104087 | The qty is utilised as per site condition and hence savings | C
|  | Qty V.Pg No-02 of MB-10 | [11 empty] | C
[11 empty] | 0 | 0 |  | C
264 | IVF264 | Flooring with non-skid full body ceramic floor tiles of size 300mm x 300mm and thickness between 7 - 8mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630Part 1 to 15 of any colour and finish in all shades and designs as approved by Engineer-in-charge, set over base coat of cement mortar 1:8, 12mm thick using screened sand over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread at the rate 3.3 Kgs per Sqm and jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, screened sand , water and tiles etc., complete for finished item of work. TSSS No.701 and 707 at MGMH Petlaburj | 12 | Sqm | 1395 | 16740 | 12 | Sqm | 1395 | 16740 | 0 | 0 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
|  | AE |  |  |  |  | 0.93 | Sqm | 1395 | 1297 | 1297 | 0 |  | C
|  | Qty V.Pg No-06 of MB-11 | [11 empty] | C
C
265 | IVF265 | Providing and fixing in true horizontal level 14 mm - Mineral Fiber sheet 595 x 595 Square/Tegular Fissura fine model edge tiles with a Humidity Resistance of 90 percentage RH, Average NRC 0.50, Light Reflectance greater than 80 percentage, Thermal Conductivity equal to 0.052 to 0.057 w/mk, Fire Performance Class 0/Class 1 using hot dipped Galvanized Steel section exposed surface with pre-coated capping, main Tee of size 24 x 32 mm at every 1200 mm c/c maximum and rotary stitched cross tee of size 24 x 27 mm at every 600 mm c/c and sub-cross tee of size 24 mm x 25 mm at 1200 mm c/c and wall angle of size 19 x 19 mm fixed to periphery of the wall and the above grid is suspended at every 1200 mm c/c in both directions using 2.0 mm thick pre-straightened GI Wire including cost and conveyance of all materials and labour charges such as cutting, fixing of standing of frame work exposing roof making etc., complete for finished item of work in 3rd floor. at MGMH Petlaburj | 300 | Sqm | 1636 | 490800 | 300 | Sqm | 1636 | 490800 | 0 | 0 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
|  | AE |  |  |  |  | 138.85 | Sqm | 1636 | 227159 | 227159 | 0 |  | C
|  | Qty V.Pg No-16 of MB-11 | [11 empty] | C
C
266 | IVF266 | Providing dadooing to walls with glazed full body porcelain wall tiles of size 300 x 600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. 3rd Floor at MGMH Petlaburj | 30 | Sqm | 1391 | 41730 | 30 | Sqm | 1391 | 41730 | 0 | 0 | As per the site condition and instructions of Higher officials, dadoing provided in the corridor area. Hence the qty exceeded and proposed as AE | C | 228.54
|  | AE |  |  |  |  | 228.54 | Sqm | 1391 | 317899 | 317899 | 0 |  | C
|  | Qty V.Pg No-02 of MB-10, Qty V.Pg No-05 of MB-11 | [11 empty] | C
C
267 | IVF267 | Providing and applying Wall putty of White Cement or Polymer or Cement based of average 1 to 2 mm thickness over plastered surface to prepare the surface even and smooth after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, applying emery paper, Sand the surface, clean and wipe off loose dust, applying knifing paste filler by putty knife / muslin pad, air dry for 2 - 3 hrs, sand with 180 and 320 No., emery paper for the surface preparation including cost and conveyance of all materials to work site and all operational, incidental, labour charges, over heads and etc., complete for finished item of work in 3rd floor Internal walls. at MGMH Petlaburj | 975 | Sqm | 315 | 307125 | 975 | Sqm | 315 | 307125 | 0 | 0 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
|  | AE |  |  |  |  | 473.95 | Sqm | 315 | 149294 | 149294 | 0 |  | C
|  | Qty V.Pg No-13 of MB-11 | [11 empty] | C
C
268 | IVF268 | Painting to new wood work and flush shutters with lappam finish, over a primary coat and painting two coats of synthetic enamel paint Grade-II VOC Volatile Organic Compound content less than 50 grams/litre of approved shade including cost and conveyance of all materials to site cost of primer coat and all labour charges etc. complete including applying sand paper on lappam coats for neat finish including sales and other taxes on cost of all materials etc., complete in all floors TSSS No.1200, 1207 and 1211. at MGMH Petlaburj | 80 | Sqm | 281 | 22480 | 0 | Sqm | 281 |  | 0 | 22480 | In view of Sterility, wood work was not executed. Hence savings | C
[11 empty] | 0 | 0 |  | C
269 | IVF269 | Supply and application of one coat water based cement primer of interior grade I and two coats of water based PU paint having anti bacterial applications content less than 50 grams/litre for internal walls including cost and conveyance of all materials to site, sales and other taxes, incidental, operational and all labour charges etc., and complete for finished item of work in 3rd floor. at MGMH Petlaburj | 975 | Sqm | 259 | 252525 | 975 | Sqm | 259 | 252525 | 0 | 0 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
|  | AE |  |  |  |  | 152.93 | Sqm | 259 | 39609 | 39609 | 0 |  | C
|  | Qty V.Pg No-23 of MB-11 | [11 empty] | C
C
270 | IVF270 | Painting to old walls with 2 coats of water proof cement paint of shade as approved by the Engineer-In-Charge to give an even shade after thourughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, scaffolding charges, incidental, labour charges etc., and overheads and contractors profit complete for finished item of work as per SS 912 in 3rd floor. at MGMH Petlaburj | 100 | Sqm | 229 | 22900 | 18.36 | Sqm | 229 | 4204 | 0 | 18696 | The qty is utilised as per site condition and hence savings | C | 18.36
[11 empty] | 0 | 0 |  | C
285 | IVF285 | Supply and installation of 80mm thick double skin modular wall Panels made of 0.8 mm thick powder coated GI on both the sides, with 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, flush on both sides with maximum allowable gap of 3- 4mm filled with food grade silicon sealant and placed on cold rolled galvanised bottom tracks with a recess to provide floor to wall coving flush with the wall panel. This includes all required harware for completion Panels to be covered with a protective film to avoid any damages during transportation and installation at MGMH Petlaburj | 125 | sqm | 5620 | 702500 | 121.04 | sqm | 5620 | 680245 | 0 | 22255 | The qty is utilised as per site condition and hence savings | C
|  | Qty V.Pg No-13 of MB-10 | [11 empty] | C
[11 empty] | 0 | 0 |  | C
286 | IVF286 | Supply and installation of 50mm thick double skin ceiling system made of 0.8 mm thick Powder Coated GI sheets on both sides, 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, panels flush towards room side with maximum allowable gap of 3-4mm at panel to panel joints filled with silicon sealant. Ceiling panels are suspended from the RCC slab by using concealed AL ceiling grid with tie rod and adjustable turn buckle arrangement etc. This includes all required hardware for completion. Panels to be covered with a protective film to avoid any damages during transportation and installation at MGMH Petlaburj | 60 | sqm | 5135 | 308100 | 60 | sqm | 5135 | 308100 | 0 | 0 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
|  | AE |  |  |  |  | 2.66 | sqm | 5135 | 13659 | 13659 | 0 |  | C
|  | Qty V.Pg No-14 of MB-10 | [11 empty] | C
C
287 | IVF287 | Double leaf clean room Doors : 46mm thick flush doors made of 0.8mm thick Powder coated GI sheets on both sides, 90 plus or minus 2 kg/m3 density Honeycomb with stand upto 220 Deg.C Temperature, and compressible strength upto 400 Kg/Sqm, 1.2 mm thick GPSP. door frames, double glazed vision panel with necessary adhesive tapes and silicon sealant, necessary hardware like SS304 ball bearing butt hinges, D- handles, push plates, Dorma make door closure, concealed tower bolt, drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms, Both side lock and keys etc. complete. Size 1500 X 2100 mm with 300mm X 300mm double glazed view panels at MGMH Petlaburj | 4 | No | 46000 | 184000 | 4 | No | 46000 | 184000 | 0 | 0 | As per the instructions of Higher officials Access Control Door Mandates the scientific door, the Qty. exceeded and now proposed as AE | C
|  | AE |  |  |  |  | 1 | No | 46000 | 46000 | 46000 | 0 |  | C
|  | Qty V.Pg No-13 of MB-10 | [11 empty] | C
C
288 | IVF288 | Single leaf clean room Doors : 46mm thick flush doors made of 0.8mm thick Powder coated GI sheets on both sides, 90 plus or minus 2 kg/m3 density Honeycomb with stand upto 220 Deg.C Temperature, and compressible strength upto 400 Kg/Sqm, 1.2 mm thick GPSP . door frames, double glazed vision panel with necessary adhesive tapes and silicon sealant, necessary hardware like SS304 ball bearing butt hinges, D- handles, push plates, Dorma make door closure, concealed tower bolt, drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms, Both side lock and keys etc. complete. Size 900 X 2100 mm with 300 mm x 300 mm View panelat MGMH Petlaburj | 2 | No | 28700 | 57400 | 2 | No | 28700 | 57400 | 0 | 0 | As per the instructions of Higher officials Autoclave Room, UPS Room & Electrical Room Mandates the scientific door, the Qty. exceeded and now proposed as AE | C
|  | AE |  |  |  |  | 3 | No | 28700 | 86100 | 86100 | 0 |  | C
|  | Qty V.Pg No-13 of MB-10 | [11 empty] | C
C
289 | IVF289 | Supply and installation of Extruded Aluminium Coving at MGMH Petlaburj | 100 | Rmt | 585 | 58500 | 100 | Rmt | 585 | 58500 | 0 | 0 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
|  | AE |  |  |  |  | 9.8 | Rmt | 585 | 5733 | 5733 | 0 |  | C
|  | Qty V.Pg No-14 of MB-10 | [11 empty] | C
C
290 | IVF290 | Providing, laying of scratch proof PVC/Vinyl flooring of 2mm thickness with proper welded joints air tight, along with leveling compound to match the existing flooring levels as per engineer in charge instructions. Sub floor preparation with self leveling compound. After the sub floor preparation, it should be suitable for ESD flooring. Rate inclusive of sifting of material and labour charges. at MGMH Petlaburj | 140 | Sqm | 4070 | 569800 | 140 | Sqm | 4070 | 569800 | 0 | 0 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
|  | AE |  |  |  |  | 33.31 | Sqm | 4070 | 135572 | 135572 | 0 |  | C
|  | Qty V.Pg No-24 of MB-11 | [11 empty] | C
C
291 | IVF291 | Supply, installation, testing and commissioning of 16 G GI powder coated suitable single person entry air shower as per the Technical Specifications at MGMH Petlaburj | 1 | No | 355000 | 355000 | 1 | No | 355000 | 355000 | 0 | 0 | The item executed as per agreement quantity | C
|  | Qty V.Pg No-13 of MB-10 | [11 empty] | C
[11 empty] | 0 | 0 |  | C
292 | IVF292 | Supply, installation, Testing and Commissioning of Static Pass Boxes of Size 450X450mm with 1.2mm thick SS 304 Mat finish , with interlock doors, UV light On when doors closed condition. As per clean room standard and requirement. at MGMH Petlaburj | 3 | No | 61000 | 183000 | 2 | No | 61000 | 122000 | 0 | 61000 | The qty is utilised as per site condition and hence savings | C
|  | Qty V.Pg No-14 of MB-10 | [11 empty] | C
C
[6 empty] | 5915529 |  |  | PART-A | 7012631 | 1910379 | 813277 | 1097102
[5 empty] | As Per Agreement | 5915529 |  |  | Excess | 1910379
[5 empty] | As Per Workdone | 7012631 |  |  | Less | 813277
[5 empty] | Net Difference | 1097102 |  |  | Net Difference | 1097102
PLUMBING WORKS
271 | IVF271 | Supplying and fixing 15 mm brass body CP finish bib tap of not less than 300 grams weight screw grams weight with quarter turn spindle with internal/ external threaded connection conforming to IS 8931 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, overheads and contractors profit complete for finished item of work in all floors.at MGMH Petlaburj | 2 | No | 881 | 1762 | 0 | No | 881 |  | 0 | 1762 | Not executed as per site conditions hence savings | P
[11 empty] | 0 | 0 |  | P
272 | IVF272 | Supply and fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings SDR 13.5 to meet the requirement of ASTM-D 2846 and are produced in CTS Copper Tube Sizes 1/2inches to 2inches for hot and cold water IS 15778:2007 including cost and conveyance of all materials to site, labour charges for fixing,complete for finished item of work at all floor levels. 15.90mm OD pipe at MGMH Petlaburj | 60 | Rmt | 199 | 11940 | 60 | Rmt | 199 | 11940 | 0 | 0 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | P
|  | AE |  |  |  |  | 35.61 | Rmt | 199 | 7086 | 7086 | 0 |  | P
|  | Qty V.Pg No-04 of MB-11 | [11 empty] | P
P
273 | IVF273 | Supply and fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings SDR 13.5 to meet the requirement of ASTM-D 2846 and are produced in CTS Copper Tube Sizes 1/2inches to 2inches for hot and cold water IS 15778:2007 including cost and conveyance of all materials to site, labour charges for fixing,complete for finished item of work at all floor levels. 22.20mm OD pipe at MGMH Petlaburj | 60 | Rmt | 229 | 13740 | 0 | Rmt | 229 |  | 0 | 13740 | Not executed as per site conditions hence savings | P
[11 empty] | 0 | 0 |  | P
274 | IVF274 | Supplying and fixing of SWR PVC pipes Prince/Sudhakar/Kisan/Supreme or any ISI brand 4 Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, complete for finished item of work at all floor levels. APSS No. 1302 1319 and 1326 - 75mm dia at MGMH Petlaburj | 90 | Rmt | 327 | 29430 | 0 | Rmt | 327 |  | 0 | 29430 | Not executed as per site conditions hence savings | P
[11 empty] | 0 | 0 |  | P
275 | IVF275 | Supplying and fixing of SWR PVC pipes Prince/Sudhakar/ Kisan/Supreme or any ISI brand 4 Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, complete for finished item of work at all floor levels. APSS No. 1302 1319 and 1326- 110mm dia at MGMH Petlaburj | 75 | Rmt | 444 | 33300 | 10.3 | Rmt | 444 | 4573 | 0 | 28727 | The qty is utilised as per site condition and hence savings | P
|  | Qty V.Pg No-04 of MB-11 | [8 empty] | 0 | 0 |  | P
P
276 | IVF276 | Supplying and fixing Bronze Gate/ Globe valve as per IS - 778 Class - I, Indian make heavy type including cost and conveyance of all materials , labour charges , overheads and contractors profit complete for finished item of work. 25mm Nominal bore at MGMH Petlaburj | 6 | No | 1746 | 10476 | 0 | No | 1746 |  | 0 | 10476 | Not executed as per site conditions hence savings | P
[11 empty] | 0 | 0 |  | P
277 | IVF277 | Supplying and fixing of 4inches 101.6mm multi floor trap with jali - UPVC/SWR pipe fittings as per site requirements with standard practice for all floors including cost and conveyance of all materials to site, labour charges ,etc., complete for finished item of work. at MGMH Petlaburj | 6 | No | 220 | 1320 | 1 | No | 220 | 220 | 0 | 1100 | The qty is utilised as per site condition and hence savings | P
|  | Qty V.Pg No-26 of MB-11 | [11 empty] | P
[11 empty] | 0 | 0 |  | P
278 | IVF278 | Supplying and fixing Indian make Flat Back Wash Hand Basin 1st quality conforming to IS:2556-Part-4:1972 of size 550mm x 400mm with 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963- 1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make heavy duty complete with standard CI brackets including wooden blocks ,1 No.12.70mm PVC connection with brass union nuts CP coated , angle stop cock 12.70mm dia. first quality Indian make heavy duty, 30mm dia. PVC flexible waste pipe 914.4mm length of 1st quality including cost and conveyance of all materials to site, labour charges for finished item of work at MGMH Petlaburj | 6 | No | 3800 | 22800 | 6 | No | 3800 | 22800 | 0 | 0 | The item executed as per agreement quantity | P
|  | Qty V.Pg No-26 of MB-11 | [11 empty] | P
[11 empty] | 0 | 0 |  | P
279 | IVF279 | Supply, Installation and commissioning approved make floor mounted Anglo Indian wash down EWC conforming to IS:2556 Part 8-2004 suit with P or S trap with dual flush porcelain cistern fixed on wash down EWC with all internal parts of dual flush cistern, ultra solid seat cover of approved make with rubber buffer and cap and 15 mm angle stop cock and 450 mm long PVC inter connection pipe wall flanges all of approved make etc. complete for finished item of work in all respects: TBSP-E.II-03 at MGMH Petlaburj | 6 | No | 7590 | 45540 | 6 | No | 7590 | 45540 | 0 | 0 | The item executed as per agreement quantity | P
|  | Qty V.Pg No-27 of MB-11 | [11 empty] | P
[11 empty] | 0 | 0 |  | P
280 | IVF280 | Supplying and fixing Chromium plated finish brass body quarter turn Bibcock cum Health Faucet with 1m long tube and wall hook with necessary fittings etc., complete including cost and conveyance of all materials, labour charges, complete for finished item of work in all floors. at MGMH Petlaburj | 6 | No | 4579 | 27474 | 6 | No | 4579 | 27474 | 0 | 0 | The item executed as per agreement quantity | P
|  | Qty V.Pg No-27 of MB-11 | [11 empty] | P
[11 empty] | 0 | 0 |  | P
281 | IVF281 | Supplying and fixing CP finish brass soap dish of approved make ISI quality including cost and conveyance of all materials, labour charges for fixing, for finished item of work in all floors at MGMH Petlaburj | 6 | No | 872 | 5232 | 6 | No | 872 | 5232 | 0 | 0 | The item executed as per agreement quantity | P
|  | Qty V.Pg No-28 of MB-11 | [11 empty] | P
[11 empty] | 0 | 0 |  | P
282 | IVF282 | Supplying and fixing TV shape mirror with plastic frame of size 609.6mm x 457.2mm, plywood back with NP screws 1st quality including cost and conveyance of all materials, labour charges, for finished item of work in all floors. at MGMH Petlaburj | 6 | No | 727 | 4362 | 6 | No | 727 | 4362 | 0 | 0 | The item executed as per agreement quantity | P
|  | Qty V.Pg No-28 of MB-11 | [11 empty] | P
[11 empty] | 0 | 0 |  | P
283 | IVF283 | Supplying and fixing of CP finish brass wall mounted towel ring at MGMH Petlaburj | 6 | No | 873 | 5238 | 6 | No | 873 | 5238 | 0 | 0 | The item executed as per agreement quantity | P
|  | Qty V.Pg No-28 of MB-11 | [11 empty] | P
[11 empty] | 0 | 0 |  | P
284 | IVF284 | Supplying and fixing 15 mm brass body CP finish self closing tap push type conforming to IS 1711 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, complete for finished item of work in all floors. at MGMH Petlaburj | 6 | No | 418 | 2508 | 6 | No | 418 | 2508 | 0 | 0 | The item executed as per agreement quantity | P
|  | Qty V.Pg No-29 of MB-11 | [11 empty] | P
[11 empty] | 0 | 0 |  | P
[6 empty] | 215122 |  |  | PART-A | 136973 | 7086 | 85235 | -78149
[5 empty] | As Per Agreement | 215122 |  |  | Excess | 7086
[5 empty] | As Per Workdone | 136973 |  |  | Less | 85235
[5 empty] | Net Difference | -78149 |  |  | Net Difference | -78149
ELECTRICAL WORKS
293 | IVF293 | Supply and laying of ISI 25mm outer dia medium grade with IS:9537-part 3 rigid PVC pipe concealed in wall with all required PVC / Metallic Junction Boxes including masonry work and labour charges etc., Makes: Sudhakar/ Precision /Universal/ Modi / Million Plast. at MGMH Petlaburj | 200 | Rmt | 116 | 23200 | 200 | Rmt | 116 | 23200 | 0 | 0 | Qty increased to provide point wiring in all the rooms and corridors. And also to lay and run 2.5,4,6,10 sqmm wire various places necessary and proposed as AE | E
|  | AE |  |  |  |  | 263.5 | Rmt | 116 | 30566 | 30566 | 0 |  | E
|  | Qty V.Pg No-07 of MB-10 | [11 empty] | E
E
294 | IVF294 | Supply and laying of ISI 25mm outer dia medium grade with IS:9537-part 3 rigid PVC pipe surface on wall with all required PVC / Metallic Junction Boxes including masonry work and labour charges etc., Makes: Sudhakar/ Precision /Universal/ Modi / Million Plast. at MGMH Petlaburj | 450 | Rmt | 107 | 48150 | 450 | Rmt | 107 | 48150 | 0 | 0 | Qty increased to provide point wiring in all the rooms and corridors. And also to lay and run 2.5,4,6,10 sqmm wire various places necessary and proposed as AE | E
|  | AE |  |  |  |  | 902.8 | Rmt | 107 | 96600 | 96600 | 0 |  | E
|  | Qty V.Pg No-07 of MB-10 | [11 empty] | E
E
295 | IVF295 | Wiring with 2 runs of 22/0.3mm 1.5 Sq.mm FRLS / HFFR P.V.C. insulated flexible copper cable ISI MARK in existing pipe with 6A Modular switch, Ceiling rose/BH/SBH Modular switches with cover plate and GI switch box including all labour charges etc., complete. for Non- Residential Building Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. Makes of switches: GM Four-Five / Legrand Arteor / Schneider Zen celo / Honeywell Blenge Plus/ Gold Medal curve. at MGMH Petlaburj | 100 | Pts | 945 | 94500 | 100 | Pts | 945 | 94500 | 0 | 0 | Qty increased to provide adequate lighitng in rooms and corridors including Major OT, Embriology, Andriology, Manifold room, reception area etc. hence proposed as AE | E
|  | AE |  |  |  |  | 158 | Pts | 945 | 149310 | 149310 | 0 |  | E
|  | Qty V.Pg No-08 of MB-10, Qty V.Pg No-32 of MB-11 | [11 empty] | E
E
296 | IVF296 | Supply and fixing of 6A ISI Mark 3/2 pin Modular socket with 6A 1way Modular switch, 3 Module box with cover frame and GI switch box on common switch board with connections etc., complete. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. Makes of switches:- GM Four-Five / Legrand Arteor / Schneider Zen celo/ Honeywell Blenge Plus/Gold Medal curve. at MGMH Petlaburj | 12 | No | 675 | 8100 | 12 | No | 675 | 8100 | 0 | 0 | Qty is increased as no of points increased and to provide proper power sockets in all the rooms and proposed as AE | E
|  | AE |  |  |  |  | 21 | No | 675 | 14175 | 14175 | 0 |  | E
|  | Qty V.Pg No-33 of MB-11 | [11 empty] | E
E
297 | IVF297 | Supply and fixing of 16A switches - 1Nos and 6/16A 2 in one socket - 1Nos Modular type with cover plate and GI switch box fixing on separate board including all labour charges etc., complete. Makes of switches:- GM Four-Five / Legrand Arteor / Schneider Zen celo/ Honeywell Blenge Plus/Gold Medal curve. at MGMH Petlaburj | 40 | No | 1040 | 41600 | 28 | No | 1040 | 29120 | 0 | 12480 | The item executed as per agreement quantity | E
|  | Qty V.Pg No-34 of MB-11 | [11 empty] | E
[11 empty] | 0 | 0 |  | E
298 | IVF298 | Supply and fixing of 16A/6A, 2 in one socket - 2 Nos with 16A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches:- GM Four-Five / Legrand Arteor / Schneider Zen celo/ Honeywell Blenge Plus/Gold Medal curve. at MGMH Petlaburj | 60 | No | 1755 | 105300 | 60 | No | 1755 | 105300 | 0 | 0 | Qty is increased due to extra points are used in Embrology ,Minor OT and other necessary areas and proposed as AE | E
|  | AE |  |  |  |  | 17 | No | 1755 | 29835 | 29835 | 0 |  | E
|  | Qty V.Pg No-35 of MB-11 | [11 empty] | E
E
299 | IVF299 | Supply and fixing of 16A/6A, 2 in one socket - 4 Nos with 16A switch control - 4 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches:- GM Four-Five / Legrand Arteor / Schneider Zen celo/ Honeywell Blenge Plus/Gold Medal curve. at MGMH Petlaburj | 10 | No | 3092 | 30920 | 0 | No | 3092 |  | 0 | 30920 | Not executed as per site conditions hence savings | E
[11 empty] | 0 | 0 |  | E
300 | IVF300 | Supply and run of 1 of 22 /0.3mm 1.5 Sq.mm FRLS / HFFR P.V.C. insulated flexible copper cable in existing conduit pipe for earth continuity including all labour charges etc., complete. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at MGMH Petlaburj | 350 | Rmt | 40 | 14000 | 350 | Rmt | 40 | 14000 | 0 | 0 | Qty is increased to connect all the fans to earthing, for safety of the equipments and proposed as AE | E
|  | AE |  |  |  |  | 29.6 | Rmt | 40 | 1184 | 1184 | 0 |  | E
|  | Qty V.Pg No-08 of MB-10 | [11 empty] | E
E
301 | IVF301 | Supply and run of 3 of 2.5 sq.mm 36/0.mm phase neutral and earth FRLS / HFFR PVC insulated flexible copper cable in existing conduit pipe for earth continuity including all labour charges etc., complete. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at MGMH Petlaburj | 600 | Rmt | 177 | 106200 | 600 | Rmt | 177 | 106200 | 0 | 0 | Qty is increased due to separate emergency line system is used for emergency light point for conveience of uninterupted power supply and proposed as AE | E
|  | AE |  |  |  |  | 1113.1 | Rmt | 177 | 197019 | 197019 | 0 |  | E
|  | Qty V.Pg No-08 of MB-10 | [11 empty] | E
E
302 | IVF302 | Supply and 3 runs of 4.0 sq mm 56/0.3 mm phase neutral and earth FRLS / HFFR PVC insulated flexible copper cable in existing conduit pipe for earth continuity including all labour charges etc., complete. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at MGMH Petlaburj | 1200 | Rmt | 255 | 306000 | 1200 | Rmt | 255 | 306000 | 0 | 0 | Qty is increased due to separate emergency line system is used for emergency light point for conveience of uninterupted power supply and proposed as AE | E
|  | AE |  |  |  |  | 1221 | Rmt | 255 | 311355 | 311355 | 0 |  | E
|  | Qty V.Pg No-08 of MB-10 | [11 empty] | E
E
303 | IVF303 | Supply and run of 5 of 6.0 Sqmm 90/0.3 mm 3 phases, neutral and earth FRLS / HFFR PVC insulated flexible copper cable in existing conduit pipe for earth continuity including all labour charges etc., complete. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at MGMH Petlaburj | 60 | Rmt | 606 | 36360 | 60 | Rmt | 606 | 36360 | 0 | 0 | Qty is increased due to distribution system are provided at different positions as per site condition and proposed as AE | E
|  | AE |  |  |  |  | 180.1 | Rmt | 606 | 109141 | 109141 | 0 |  | E
|  | Qty V.Pg No-08 of MB-10 | [11 empty] | E
E
304 | IVF304 | Supply and run of 5 of 10.0 Sqmm 140/0.3 mm 3 phases, neutral and earth FRLS / HFFR PVC insulated flexible copper cable in the existing conduit pipe for run of mains from Power panel board to TPN DBs with pin type lugs and connections etc., complete. for PDBs Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at MGMH Petlaburj | 40 | Rmt | 967 | 38680 | 40 | Rmt | 967 | 38680 | 0 | 0 | Qty is increased due to distribution boards are provided at different positions as per site condition and proposed as AE | E
|  | AE |  |  |  |  | 244 | Rmt | 967 | 235948 | 235948 | 0 |  | E
|  | Qty V.Pg No-08 of MB-10 | [11 empty] | E
E
305 | IVF305 | Supply and fixing of DP Metal Enclosure with IP 20 Protection DB Make with 1 No 20A, 10 KA DP MCB Make: Legrand / Schneider including internal connection and labour charges for Flush Mounting etc., complete. Makes: Legrand / Schneider. at MGMH Petlaburj | 5 | No | 2562 | 12810 | 0 | No | 2562 |  | 0 | 12810 | Not executed as per site conditions hence savings | E
[11 empty] | 0 | 0 |  | E
306 | IVF306 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand / Schneider and Supply and Fixing of 1 No., of 40A FP 30mA RCCB as incomer and 12 Nos 6-32 A 10kA SP MCBs Makes: Legrand-DX3 / Schneider-Acti9 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. For Lighting DBs at MGMH Petlaburj | 3 | No | 18325 | 54975 | 3 | No | 18325 | 54975 | 0 | 0 | Qty is increased due to number of curcuit lines are increased hence it was essential to provide separate distribtion system for UPS line, and Raw Power line and proposed as AE | E
|  | AE |  |  |  |  | 7 | No | 18325 | 128275 | 128275 | 0 |  | E
|  | Qty V.Pg No-09 of MB-10 | [11 empty] | E
E
307 | IVF307 | Supply and fixing of 8 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand / Schneider and Supply and Fixing of 1 No., of 63A FP 100mA RCCB as incomer and 24 Nos 6-32 A 10kA SP MCBs Makes: Legrand-DX3 / Schneider-Acti9 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. For Lighting DBs at MGMH Petlaburj | 2 | No | 28460 | 56920 | 0 | No | 28460 |  | 0 | 56920 | Not executed as per site conditions hence savings | E
[11 empty] | 0 | 0 |  | E
308 | IVF308 | Supply and fixing of 8 Way VTPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand / Schneider and Supply and Fixing of 1 No., of 100A FP 10KA MCB as incomer and 4 Nos 63 A 10kA TP MCBs, 4 Nos 40 A 10kA TP MCBs Makes: Legrand-DX3 / Schneider-Acti9 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. For UPS MDB DBs at MGMH Petlaburj | 1 | No | 64067 | 64067 | 1 | No | 64067 | 64067 | 0 | 0 | The item executed as per agreement quantity | E
|  | Qty V.Pg No-09 of MB-10 | [8 empty] | 0 | 0 |  | E
E
309 | IVF309 | Providing and fixing of 125A 25KA TPN Thermal Magnetic Release Based MCCB and Terminal Spreaders in Existing panel board with 1 No. and 1 Set of Indication Lamps, LED type, R,Y,B and breaker ON, OFF, TRIP and spring charged lamps and replace with above Mentioned with required Drilling Holes, removing and Making Busbar connections etc, as required. Makes: Legrand / Schneider/ ABB /LandT/CandS at MGMH Petlaburj | 1 | No | 28883 | 28883 | 1 | No | 28883 | 28883 | 0 | 0 | The item executed as per agreement quantity | E
|  | Qty V.Pg No-09 of MB-10 | [11 empty] | E
[11 empty] | 0 | 0 |  | E
310 | IVF310 | Providing and fixing of 100A 10KA FP MCB and Terminal Spreaders in IP 43 isolator Box Making connections etc, as required. Makes: Legrand / Schneider/ABB/LandT/ CandS at MGMH Petlaburj | 2 | No | 3260 | 6520 | 0 | No | 3260 |  | 0 | 6520 | Not executed as per site conditions hence savings | E
[11 empty] | 0 | 0 |  | E
311 | IVF311 | Supply, transportation and fixing of 24W edge lit LED Down light Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser Square with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor greater than 0.9, Surge protection: greater than 2KV, System efficacy of greater than100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI greater than80, and THD is less than 15percentage etc., with BIS Certification. Makes: Phillips / OSRAM / Wipro / Crompton / Bajaj / Havells at MGMH Petlaburj | 50 | No | 2652 | 132600 | 50 | No | 2652 | 132600 | 0 | 0 | Qty increased for better illumination, as per site requirement and proposed as AE | E
|  | AE |  |  |  |  | 41 | No | 2652 | 108732 | 108732 | 0 |  | E
|  | Qty V.Pg No-36 of MB-11 | [11 empty] | E
E
312 | IVF312 | Supply and Transportation 36W Edge lit, 2 feet x2 feet 600mm x600mm slim panel LED luminaire Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor greater than 0.9, Surge protection: greater than 2KV, System efficacy of greater than100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI greater than80, and THD is less than 15percentage etc., with BIS Certification. Makes: Phillips / OSRAM / Wipro / Crompton / Bajaj / Havells at MGMH Petlaburj | 30 | No | 4350 | 130500 | 30 | No | 4350 | 130500 | 0 | 0 | Qty increased for better illumination, as per site requirement and proposed as AE | E
|  | AE |  |  |  |  | 30 | No | 4350 | 130500 | 130500 | 0 |  | E
|  | Qty V.Pg No-37 of MB-11 | [11 empty] | E
E
313 | IVF313 | Supply and Transportation 42W Clean room Light fixture, 2 feet x2 feet 600mm x600mm LED luminaire CRCA powder coated white after phosphocreatine treatment provided as standard. with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor greater than 0.9, Surge protection: greater than 2KV, System efficacy of greater than100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI greater than80, and THD is less than 15percentage etc., with BIS Certification. Makes: Phillips / OSRAM / Wipro / Crompton / Bajaj / Havells at MGMH Petlaburj | 12 | No | 4762 | 57144 | 0 | No | 4762 |  | 0 | 57144 | The TSMSIDC higher officials has instructed to provide 56W lights to attain required illumination. Not executed this item, hence savings | E
[11 empty] | 0 | 0 |  | E
314 | IVF314 | Supply and fixing of ISI mark batten holder / slanting holder Makes : Anchor/ Gold Medal Olive / Million Zoom in lieu of ceiling rose of light point complete with all connections and all labour charges with 5.0W LED Lamp MAKE: OSRAM / Wipro / Crompton / Bajaj / Havells at MGMH Petlaburj | 5 | No | 184 | 920 | 0 | No | 184 |  | 0 | 920 | Not executed as per site conditions hence savings | E
[11 empty] | 0 | 0 |  | E
315 | IVF315 | Supply, Transportation of energy efficient fan, 1200 mm sweep, aluminium body, consuming 28 W, BEE 5 star rated, ceiling fan with Brush Less Direct Current BLDCmotor, class of insulation: B, 3 nos blades, 30 cm long down rod, 2 nos canopies, shackle kit, safety rope, copper winding, Power Factor greater than 0.90, Service Value CMMAV greater than 8.5, Air delivery minimum 235 CMM,350 RPM tolerance as per IS:374-2019, THD less than 10percentage. with remote or compatible to electronic step type regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise equal to75 degree Cmax, insulation resistance more than 2 mega ohm, suitable for 230V, 50 HZ, single phase AC supply, earthing etc., including all standard accessories etc., complete. Makes : Atomberg Efficio / Havells /Orient at MGMH Petlaburj | 12 | No | 4090 | 49080 | 0 | No | 4090 |  | 0 | 49080 | Not executed as maintaining BLDC fans in governement instutions is not viable. Replaced with High speed fans as per instrcutions of TSMSIDC Officials, hence savings | E
[11 empty] | 0 | 0 |  | E
316 | IVF316 | Supply and fixing of Modular type Stepped electronic regulator Makes : GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/ Cabtree Verna/ Million logus / Gold Medal Curve for sweep AC ceiling fans of 1200mm / 1400mm complete with connections. at MGMH Petlaburj | 12 | No | 827 | 9924 | 12 | No | 827 | 9924 | 0 | 0 | Qty increased due to extra fans that are provided in waiting area,UPS room, electrical room, Main fold , and Androgoly lab and proposed as AE | E
|  | AE |  |  |  |  | 16 | No | 827 | 13232 | 13232 | 0 |  | E
|  | Qty V.Pg No-38 of MB-11 | [11 empty] | E
E
317 | IVF317 | Supply and installation of 225mm Light duty exhaust fan with metal blades etc complete Makes: Crompton / Havells Ventilair-DB/ Orient hill air. at MGMH Petlaburj | 6 | No | 2203 | 13218 | 6 | No | 2203 | 13218 | 0 | 0 | Qty increaed since provided in auto clave room and proposed as AE | E
|  | AE |  |  |  |  | 2 | No | 2203 | 4406 | 4406 | 0 |  | E
|  | Qty V.Pg No-39 of MB-11 | [11 empty] | E
E
318 | IVF318 | SITC of Hot dip galvanized perforated cable tray of 100 mm Wide sizes for to run the cable from DBs to SBs and sockets and AC panel to Units units. All necessary supports and accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. at MGMH Petlaburj | 70 | Rmt | 429 | 30030 | 70 | Rmt | 429 | 30030 | 0 | 0 | Qty increaed due to cable lines provdied on terrace for AHU units and proposed as AE | E
|  | AE |  |  |  |  | 9 | Rmt | 429 | 3861 | 3861 | 0 |  | E
|  | Qty V.Pg No-09 of MB-10 | [11 empty] | E
E
319 | IVF319 | SITC of Hot dip galvanized perforated cable tray of 300 mm Wide sizes for to run the cable from Floor Panel to Lab Panel and electrical room to AC panel and AC panel to Units. All necessary supports and accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. at MGMH Petlaburj | 80 | Rmt | 1310 | 104800 | 80 | Rmt | 1310 | 104800 | 0 | 0 | Qty increased due to separate line system is used for UPS line and proposed as AE | E
|  | AE |  |  |  |  | 22.5 | Rmt | 1310 | 29475 | 29475 | 0 |  | E
|  | Qty V.Pg No-09 of MB-10 | [11 empty] | E
E
320 | IVF320 | Supply and installation of 20KVA 3ph in and 3ph out on line UPS system IGBT based rectifier with input power factor correction 32 bit microprocessor based with isolation transformers double conversion, SNMP controls, LCD display, Pure sine wave output, with auto static switch three phase input / Three phase output and modular structure for better thermal technology / cooling facility, with warranty up to three years.Makes: APC / Numeric / Emerson / Fuji Electric at MGMH Petlaburj | 1 | No | 305000 | 305000 | 1 | No | 305000 | 305000 | 0 | 0 | The item executed as per agreement quantity | E
|  | Qty V.Pg No-05 of MB-10 | [11 empty] | E
[11 empty] | 0 | 0 |  | E
321 | IVF321 | Supply and fixing of 12V 65 AH SMF battery including wire leads. Makes: Quanta / Racket / Exide. at MGMH Petlaburj | 20 | No | 20584 | 411680 | 20 | No | 20584 | 411680 | 0 | 0 | As the UPS with isolation transformer requires min 32 nos of batteries to increase uptime of 60 minutes from 30 minutes considering the load. hence the Qty. exceeded and proposed as AE | E
|  | AE |  |  |  |  | 12 | No | 20584 | 247008 | 247008 | 0 |  | E
E
322 | IVF322 | Supply and providing of UPS cum battery rack for 20 batteries at MGMH Petlaburj | 1 | No | 6764 | 6764 | 1 | No | 6764 | 6764 | 0 | 0 | The item executed as per agreement quantity | E
|  | Qty V.Pg No-05 of MB-10 | [11 empty] | E
[11 empty] | 0 | 0 |  | E
323 | IVF323 | Providing and Fixing maintenance free earthing which consists of G.I. Earth station, with 600X600X3.15mm GI Plate at 2500mm Depth including construction of brick pedestal, providing meshed funnel, GI cover and other civil Engineering works, spreading a homogenous mixture of salt, charcoal around the pipe etc., completely as per IS 3043, 1987 or latest revision. Earthing testing should be done as per IE Rules like Earth valve test Etc. at MGMH Petlaburj | 2 | No | 8500 | 17000 | 2 | No | 8500 | 17000 | 0 | 0 | The item executed as per agreement quantity | E
|  | Qty V.Pg No-10 of MB-10 | [11 empty] | E
[11 empty] | 0 | 0 |  | E
324 | IVF324 | Providing and Fixing maintenance free earthing which consists of copper. Earth station, with 600X600 X3.15mm Copper Plate at 2500mm Depth including construction of brick pedestal, providing meshed funnel, GI cover and other civil Engineering works, spreading a homogenous mixture of salt, charcoal around the pipe etc., completely as per IS 3043,1987 or latest revision. Earthing testing should be done as per IE Rules like Earth valve test Etc. at MGMH Petlaburj | 2 | No | 22283 | 44566 | 2 | No | 22283 | 44566 | 0 | 0 | Qty increased since suitable Resistance value was not getting to UPS systems. Hence proposed as AE | E
|  | AE |  |  |  |  | 2 | No | 22283 | 44566 | 44566 | 0 |  | E
|  | Qty V.Pg No-10 of MB-10 | [11 empty] | E
E
325 | IVF325 | Supply and installation of 50x6 GI flat for body earthing of electrical panel and AC Panel which is laid in 300mm cable tray at MGMH Petlaburj | 200 | Rmt | 329 | 65800 | 200 | Rmt | 329 | 65800 | 0 | 0 | Qty increased due to separate earthing line is laid on terrace for AHU units and proposed as AE | E
|  | AE |  |  |  |  | 17.3 | Rmt | 329 | 5692 | 5692 | 0 |  | E
|  | Qty V.Pg No-09 of MB-10 | [11 empty] | E
E
326 | IVF326 | Supply and installation of 25x3 GI flat for body earthing of DBs and Cable tray which is laid in 100mm cable tray at MGMH Petlaburj | 100 | Rmt | 163 | 16300 | 0 | Rmt | 163 |  | 0 | 16300 | Not executed as per site conditions hence savings | E
[11 empty] | 0 | 0 |  | E
327 | IVF327 | Supply and installation of 25x3 Copper flat for Neutral earthing of UPS and Equipment which is laid in 100mm cable tray at MGMH Petlaburj | 200 | Rmt | 902 | 180400 | 200 | Rmt | 902 | 180400 | 0 | 0 | Qty is increased due to distance of earthing to earthing were difference as per site condition hence proposed as AE | E
|  | AE |  |  |  |  | 7.3 | Rmt | 902 | 6585 | 6585 | 0 |  | E
|  | Qty V.Pg No-10 of MB-10 | [11 empty] | E
E
328 | IVF328 | Supply and installation of 4 sqmm Copper wire for Earthing of DBs Equipment at MGMH Petlaburj | 80 | Rmt | 83 | 6640 | 80 | Rmt | 83 | 6640 | 0 | 0 | Qty increased due to Separate earthing used for Distribution board body as it is necessary for DB's hence qty increased and proposed as AE | E
|  | AE |  |  |  |  | 370.6 | Rmt | 83 | 30760 | 30760 | 0 |  | E
|  | Qty V.Pg No-10 of MB-10 | [11 empty] | E
E
329 | IVF329 | Supply, Lying and testing of 3.5Cx95 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc. Make of Cable: Polycab/ KEI/ Universal / Glostar/Finolex. Make of gland and Lungs: HMI/Commet/Dowell’s at MGMH Petlaburj | 120 | Rmt | 1207 | 144840 | 120 | Rmt | 1207 | 144840 | 0 | 0 | Qty increased due to incomming supply is drawn from Hospital Main panel board rather than Sub distribution Panel. Which is at a longer distance from the IVF Center and proposed as AE | E
|  | AE |  |  |  |  | 60 | Rmt | 1207 | 72420 | 72420 | 0 |  | E
|  | Qty V.Pg No-10 of MB-10 | [11 empty] | E
E
330 | IVF330 | Supply, Lying and testing of 3.5CX50 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc. Make of Cable: Polycab/ KEI/ Universal / Glostar/Finolex. Make of gland and Lungs: HMI/Commet/Dowell’s at MGMH Petlaburj | 70 | Rmt | 722 | 50540 | 70 | Rmt | 722 | 50540 | 0 | 0 | Qty increased due to incomming supply is drawn from Hospital Main panel board rather than Sub distribution Panel. Which is at a longer distance from the IVF Center and proposed as AE | E
|  | AE |  |  |  |  | 110 | Rmt | 722 | 79420 | 79420 | 0 |  | E
|  | Qty V.Pg No-10 of MB-10 | [11 empty] | E
E
331 | IVF331 | Supply, Lying and testing of 4Cx16 sqmm PVC Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc. Make of Cable: Polycab/ KEI/ Universal / Glostar/Finolex. Make of gland and Lungs: HMI/Commet/Dowell’s at MGMH Petlaburj | 100 | Rmt | 1483 | 148300 | 100 | Rmt | 1483 | 148300 | 0 | 0 | Qty increased due to AC unit Control system is fixed in Electrical room for controlling the unit from the site and proposed as AE | E
|  | AE |  |  |  |  | 60.4 | Rmt | 1483 | 89573 | 89573 | 0 |  | E
|  | Qty V.Pg No-11 of MB-10, Qty V.Pg No-38 of MB-11 | [11 empty] | E
E
332 | IVF332 | Supply, Lying and testing of 4Cx6 sqmm Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc. Make of Cable: Polycab/ KEI/ Universal / Glostar/Finolex. Make of gland and Lungs: HMI/Commet/Dowell’s at MGMH Petlaburj | 120 | Rmt | 484 | 58080 | 120 | Rmt | 484 | 58080 | 0 | 0 | The item executed as per agreement quantity | E
|  | Qty V.Pg No-11 of MB-10 | [11 empty] | E
[11 empty] | 0 | 0 |  | E
333 | IVF333 | Supply, Lying and testing of 4Cx4 sqmm Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc. Make of Cable: Polycab/ KEI/ Universal / Glostar/Finolex. Make of gland and Lungs: HMI/Commet/Dowell’s at MGMH Petlaburj | 80 | Rmt | 356 | 28480 | 80 | Rmt | 356 | 28480 | 0 | 0 | The item executed as per agreement quantity | E
|  | Qty V.Pg No-11 of MB-10 | [11 empty] | E
[11 empty] | 0 | 0 |  | E
334 | IVF334 | SITC of IVF Center Main Panel Indoor IP-42 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with /without detachable extension type structure with all type of suitable switching accessories and bus-bar as per load requirement of respective IVF equipment’s. Which is including Lighting, power DBs and UPS at MGMH Petlaburj | 1 | No | 355000 | 355000 | 1 | No | 355000 | 355000 | 0 | 0 | The item executed as per agreement quantity | E
|  | Qty V.Pg No-11 of MB-10 | [11 empty] | E
[11 empty] | 0 | 0 |  | E
335 | IVF335 | SITC of IVF center AC Panel outdoor IP-54 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with / without detachable extension type structure with all type of suitable switching accessories and bus-bar as per load requirement of respective AC equipment’s. Which is including 1nos AHU’s stater with VFD by pass, Heater, ODU and VRF system at MGMH Petlaburj | 1 | No | 270000 | 270000 | 1 | No | 270000 | 270000 | 0 | 0 | The item executed as per agreement quantity | E
|  | Qty V.Pg No-11 of MB-10 | [11 empty] | E
[11 empty] | 0 | 0 |  | E
336 | IVF336 | Supply and installation of AHUs stater on/off push button station for Remote control for inside IVF center with control wiring from AC panel to on /off push button station with necessary items. at MGMH Petlaburj | 3 | No | 1540 | 4620 | 2 | No | 1540 |  | 0 | 4620 | The item executed as per site conditions hence savings | E
[11 empty] | 0 | 0 |  | E
[6 empty] | 3719411 |  |  | PART-A | 5641335 | 2169638 | 247714 | 1921924
[5 empty] | As Per Agreement | 3719411 |  |  | Excess | 2169638
[5 empty] | As Per Workdone | 5641335 |  |  | Less | 247714
[5 empty] | Net Difference | 1921924 |  |  | Net Difference | 1921924
ELV WORKS
337 | IVF337 | Supply, installation, testing and commissioning of 20nos LAN points with cat 6 cable and with suitable network rack and 5nos of telephone points with krone box to existing EPABEX. at MGMH Petlaburj | 1 | Job | 383000 | 383000 | 1 | Job | 383000 | 383000 | 0 | 0 | The item executed as per agreement quantity | ELV
|  | Qty V.Pg No-57 of MB-11 | [11 empty] | ELV
[11 empty] | 0 | 0 |  | ELV
338 | IVF338 | Supply, installation, testing and commissioning of 1 no of Access control system with egress switch, Power Cable, communication cable to control panel with necessary required items Etc. at MGMH Petlaburj | 1 | Job | 124000 | 124000 | 1 | Job | 124000 | 124000 | 0 | 0 | The item executed as per agreement quantity | ELV
|  | Qty V.Pg No-58 of MB-11 | [11 empty] | ELV
[11 empty] | 0 | 0 |  | ELV
340 | IVF340 | Supply, installation, testing and commissioning of 5nos IP Based CCTV cameras and Cat 6 Cable with NVR system. at MGMH Petlaburj | 1 | Job | 182000 | 182000 | 1 | Job | 182000 | 182000 | 0 | 0 | The item executed as per agreement quantity | ELV
|  | Qty V.Pg No-58 of MB-11 | [11 empty] | ELV
[11 empty] | 0 | 0 |  | ELV
[6 empty] | 689000 |  |  | PART-A | 689000 | 0 | 0 | 0
[5 empty] | As Per Agreement | 689000 |  |  | Excess | 0
[5 empty] | As Per Workdone | 689000 |  |  | Less | 0
[5 empty] | Net Difference | 0 |  |  | Net Difference | 0
FIRE FIGHTING WORKS
341 | IVF341 | Supply, installation, testing and commissioning of Audio and video recording of counseling rooms at MGMH Petlaburj | 1 | Job | 138000 | 138000 | 1 | Job | 138000 | 138000 | 0 | 0 | The item executed as per agreement quantity | FF
|  | Qty V.Pg No-58 of MB-11 | [11 empty] | FF
[11 empty] | 0 | 0 |  | FF
339 | IVF339 | Supply, installation, testing and commissioning of Automatic Fire Alarm System which is including 30 nos of smoke Detectors 1nos manual call point, 1 no of Hooter with fire alarm cable connected to the existing fire control panel with necessary Required items etc.. at MGMH Petlaburj | 1 | Job | 510000 | 510000 | 1 | Job | 510000 | 510000 | 0 | 0 | The item executed as per agreement quantity | FF
|  | Qty V.Pg No-58 of MB-11 | [11 empty] | FF
[11 empty] | 0 | 0 |  | FF
342 | IVF342 | Supply and installation of Fire Extinguishers of CO2 4.50 Kg at MGMH Petlaburj | 5 | No | 11225 | 56125 | 5 | No | 11225 | 56125 | 0 | 0 | The item executed as per agreement quantity | FF
|  | Qty V.Pg No-58 of MB-11 | [11 empty] | FF
[11 empty] | 0 | 0 |  | FF
343 | IVF343 | Supply and installation of ceiling mounted Fire Extinguishers of ABC MAP 90, 5.0 Kg stored pressure type at MGMH Petlaburj | 5 | No | 7686 | 38430 | 5 | No | 7686 | 38430 | 0 | 0 | The item executed as per agreement quantity | FF
|  | Qty V.Pg No-58 of MB-11 | [11 empty] | FF
[11 empty] | 0 | 0 |  | FF
344 | IVF344 | Supply and installation of 2.0 Kg clean agent HCFC 123 Fire Extinguishers at MGMH Petlaburj | 5 | No | 15065 | 75325 | 5 | No | 15065 | 75325 | 0 | 0 | The item executed as per agreement quantity | FF
|  | Qty V.Pg No-58 of MB-11 | [11 empty] | FF
[11 empty] | 0 | 0 |  | FF
345 | IVF345 | Supply and fixing of Fire escape signage Boards at MGMH Petlaburj | 1 | Job | 56000 | 56000 | 1 | Job | 56000 | 56000 | 0 | 0 | The item executed as per agreement quantity | FF
|  | Qty V.Pg No-25 of MB-11 | [11 empty] | FF
FF
[6 empty] | 873880 |  |  | PART-A | 873880 | 0 | 0 | 0
[5 empty] | As Per Agreement | 873880 |  |  | Excess | 0
[5 empty] | As Per Workdone | 873880 |  |  | Less | 0
[5 empty] | Net Difference | 0 |  |  | Net Difference | 0
AIR CONDITIONING
346 | IVF346 | Supply, transportation and installation of split AC unit 1.5 TR inverter type 3 Star capable of delivering 18000 BTU/hr and above with high wall mounted indoor unit and outdoor condensing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord , built-in stabilizer Voltage range 160- 264 volts and cordless remote control. Makes : Daikin / Thoshiba / O General at MGMH Petlaburj | 1 | No | 48000 | 48000 | 1 | No | 48000 | 48000 | 0 | 0 | Qty increased so as to provide AC in UPS room and Reception and proposed as AE | AC
|  | AE |  |  |  |  | 2 | No | 48000 | 96000 | 96000 | 0 |  | AC
|  | Qty V.Pg No-11 of MB-10 | [11 empty] | AC
AC
347 | IVF347 | Supply, transportation and installation of split AC unit 1.0 TR inverter type minimum 3 Star capable of delivering 12000 BTU/hr and above with high wall mounted indoor unit and outdoor condensing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord, built-in stabilizer Voltage range 160- 264 volts and cordless remote control. Makes: Daikin / Thoshiba/ O General at MGMH Petlaburj | 1 | No | 40000 | 40000 | 0 | No | 40000 |  | 0 | 40000 | In place of 1.0 ton, provided with 1.5 ton AC as room area increased. Hence savings | AC
[11 empty] | 0 | 0 |  | AC
348 | IVF348 | Modular Double skin floor mounted EUROVENT Certified Air Handling Unit 3000CFM / 8.5 TR / 150mm SP made out of 45 plus or minus 2mm thick PUF insulated panels Thermal break aluminium profile frame work with 0.8mm thick pre painted / powder coated inner and outer skins comprising of mixing box with fresh air and return air dampers, pre filters with 10 and 5 microns combination filters in single frame, Interlaced/Intertwined DX Cooling Coil suitable for connecting 2 nos of 8.5TR capacity 1W plus 1S out door condensing units, SS304 drain pan with, blower section with Nicotra / Kruger make direct drive/ Plug type fan, vibration isolators, EFF1 motor and blower section with on/off switches to operate from outside, limit switch for the fan section access door with a view port, fine filter section with 3 microns filters inspection doors for all filter and fan sections and damper at the outlet of unit. Ports for differential pressure gauges across all filters and blower to measure differential pressure. AHU Make : VTS / Systemair, Make - Blower - Nicotra / Kruger ; Motor - Crompton Greaves / Siemens ; Filter - Thermodyne / Freudenberg / Ultrafil at MGMH Petlaburj | 1 | No | 590000 | 590000 | 0 | No | 590000 |  | 0 | 590000 | As per the site condition & floor plans approved, the increased area requires higher capacity of AHU. Proposed as Supplimental item and quantity of this item not utilized. Hence savings | AC
[11 empty] | 0 | 0 |  | AC
349 | IVF349 | SITC of filter module made out of heavy duty Aluminium powder coated extrusion with minimum of 13G . and to house 610 mm X 610 mm HEPA Filter at the rate 0.3 microns , 99.9997, H-14 Grade, Filter loading from clean room side with bewel gear arrangement damper with access from clean room suitable to house the following filter sizes pressure drop and Integrity testing ports into room. Includes SS capsule perforated diffuser. This includes all required supports and accessories etc. Capacity 1000 CFM. at MGMH Petlaburj | 6 | No | 42000 | 252000 | 6 | No | 42000 | 252000 | 0 | 0 | The item executed as per agreement quantity | AC
|  | Qty V.Pg No-55 of MB-11 | [11 empty] | AC
[11 empty] | 0 | 0 |  | AC
350 | IVF350 | SITC of air cooled condensing units with two scroll compressors, air cooled condenser, power panel, vibration isolating pads, stand for ODU, thermostat, etc. of the following capacities. The nominal capacity of the condensing unit shall be as under. Air cooled condensing unit shall have horizontal discharge. All refrigerant piping accessories sight glass, drier, expansion valve, etc. shall be supplied with the condensing units and suitable to connect above AHUs. Refrigerant shall be R 407C / R 410A. Necessary thermostat, control wiring, etc. shall be included. Derating of the unit shall not be more than 15percentage under 45 deg. C ambient temperature. Condensing unit shall be capable of operating up 50 deg. C ambient temperature. 8.5 TR capacity at MGMH Petlaburj | 1 | No | 182000 | 182000 | 0 | No | 182000 |  | 0 | 182000 | As per the site condition & floor plans approved, the increased area requires higher capacity of condensing unit to maintain required temperature and increase in AHU capacity too. Proposed as Supplimental item and quantity of this item not utilized. Hence savings | AC
[11 empty] | 0 | 0 |  | AC
351 | IVF351 | SITC of Flange type, Flame proof FLP duct heaters of 5 kW capacity with Mineral Filled AISI SS304/SS321 Sheathed Tubular Heater with GI Helical fins, Tube dia 8.2mm min and Helical Finn dia 25mm min, enclosed in the frame, FLP Terminal box etc., Nickel Chromium Inner Element, Silicon Sealing to Restrict Moisture pickup, Silver brazed mounting plate etc., and heaters shall be controlled with PID thyrestor controller based on the analog output signal of 0-10 V DC of controller . And this should have saftey thermostat and cutouts and air stat etc. all safety controls. The capacities as follows and sizes of the heaters shall be as per the duct sizes and approved drawing. at MGMH Petlaburj | 1 | No | 205000 | 205000 | 1 | No | 205000 | 205000 | 0 | 0 | The item executed as per agreement quantity | AC
|  | Qty V.Pg No-56 of MB-11 | [11 empty] | AC
[11 empty] | 0 | 0 |  | AC
352 | IVF352 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Liquid Line at MGMH Petlaburjl | 20 | Rmt | 1020 | 20400 | 16 | Rmt | 1020 | 16320 | 0 | 4080 | The qty utilised as per site condition and hence savings | AC
|  | Qty V.Pg No-56 of MB-11 | [11 empty] | AC
[11 empty] | 0 | 0 |  | AC
353 | IVF353 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Suction Line at MGMH Petlaburj | 20 | Rmt | 1190 | 23800 | 16 | Rmt | 1190 | 19040 | 0 | 4760 | The qty utilised as per site condition and hence savings | AC
|  | Qty V.Pg No-57 of MB-11 | [11 empty] | AC
[11 empty] | 0 | 0 |  | AC
354 | IVF354 | SITC of CPVC drain ping with supports, clamps and 9 mm thk. Nitrile rubber tube insulation of the following sizes. Insulation shall have factory laminated glass cloth. 32mm Dia at MGMH Petlaburj | 50 | Rmt | 670 | 33500 | 0 | Rmt | 670 |  | 0 | 33500 | Not executed as not required at site. Hence savings. | AC
[11 empty] | 0 | 0 |  | AC
355 | IVF355 | SITC of CPVC drain ping with supports, clamps and 9 mm thk. Nitrile rubber tube insulation of the following sizes. Insulation shall have factory laminated glass cloth. 25mm Dia at MGMH Petlaburj | 50 | Rmt | 515 | 25750 | 9 | Rmt | 515 | 4635 | 0 | 21115 | The qty utilised as per site condition and hence savings | AC
|  | Qty V.Pg No-57 of MB-11 | [11 empty] | AC
[11 empty] | 0 | 0 |  | AC
356 | IVF356 | SITC of Factory fabricated and boxed ducting using Aluminium Sheets / coils, should be fabricated as per SMACNA, galvanised hardware and supports, silicon sealant at all longitudinal joints, Galvanized /GI Electroplated iron angle flanges for all the joints, bracing angles and minimum 5mm thick neoprene rubber gasket.- Duct pressure testing at 75mm to be carried out before insulatiting the duct. pressure testing to be done as per SMACNA. Procedure to be approved by consultant. 20G - 1.0 mm Thick at MGMH Petlaburj | 30 | Sqm | 2600 | 78000 | 24.98 | Sqm | 2600 | 64948 | 0 | 13052 | The qty utilised as per site condition and hence savings | AC
|  | Qty V.Pg No-46 of MB-11 | [11 empty] | AC
[11 empty] | 0 | 0 |  | AC
357 | IVF357 | SITC of Factory fabricated and boxed ducting using Aluminium Sheets / coils, should be fabricated as per SMACNA, galvanised hardware and supports, silicon sealant at all longitudinal joints, Galvanized /GI Electroplated iron angle flanges for all the joints, bracing angles and minimum 5mm thick neoprene rubber gasket.- Duct pressure testing at 75mm to be carried out before insulatiting the duct. pressure testing to be done as per SMACNA. Procedure to be approved by consultant. 22G - 0.8 mm Thick at MGMH Petlaburj | 250 | Sqm | 2325 | 581250 | 232.64 | Sqm | 2325 | 540888 | 0 | 40362 | The qty utilised as per site condition and hence savings | AC
|  | Qty V.Pg No-49 of MB-11 | [11 empty] | AC
[11 empty] | 0 | 0 |  | AC
358 | IVF358 | Aluminium low leakage aerofoil design volume control dampers Suitable for manual and motorised operation at MGMH Petlaburj | 2 | Sqm | 15800 | 31600 | 0.8 | Sqm | 15800 | 12640 | 0 | 18960 | The qty utilised as per site condition and hence savings | AC
[11 empty] | 0 | 0 |  | AC
359 | IVF359 | CBRI approved 16G GI Spring return actuated fire dampers rated for 90 minutes with limit switch at MGMH Petlaburj | 2 | Sqm | 25900 | 51800 | 0.8 | Sqm | 25900 | 20720 | 0 | 31080 | The qty utilised as per site condition and hence savings | AC
[11 empty] | 0 | 0 |  | AC
360 | IVF360 | SITC of SS perforated return raiser grilles with 10 microns filters with collar dampers at MGMH Petlaburj | 2 | Sqm | 26300 | 52600 | 1.59 | Sqm | 26300 | 41817 | 0 | 10783 | The qty utilised as per site condition and hence savings | AC
[11 empty] | 0 | 0 |  | AC
361 | IVF361 | Extruded Al. powder coated EXHAUST / RETURN discrete grilles at MGMH Petlaburj | 1 | Sqm | 8125 | 8125 | 1 | Sqm | 8125 | 8125 | 0 | 0 | The item executed as per agreement quantity | AC
[11 empty] | 0 | 0 |  | AC
362 | IVF362 | SITC of Collar Dampers made of Al. extrusions with black powder coating for Grilles / Diffusers at MGMH Petlaburj | 1 | Sqm | 7550 | 7550 | 0.76 | Sqm | 7550 | 5738 | 0 | 1812 | The qty utilised as per site condition and hence savings | AC
[11 empty] | 0 | 0 |  | AC
363 | IVF363 | SITC of Magnehelic gauges across pre and fine filter at AHUs including mounting arrangement, SS nozzles, food grade PVC tubing, etc. at MGMH Petlaburj | 2 | No | 10500 | 21000 | 2 | No | 10500 | 21000 | 0 | 0 | Qty increased as per site condition and proposed as AE | AC
|  | AE |  |  |  |  | 1 | No | 10500 | 10500 | 10500 | 0 |  | AC
364 | IVF364 | SITC of Magnehelic gauges to measure the room differential pressures in operation theatres with SS mounting box, SS nozzles, food grade PVC tubing, etc. at MGMH Petlaburj | 2 | No | 12900 | 25800 | 2 | No | 12900 | 25800 | 0 | 0 | The item executed as per agreement quantity | AC
[11 empty] | 0 | 0 |  | AC
365 | IVF365 | SITC of Aluminium powder coated Fresh air and Exhaust Louvers of non- vision type with nylon mosquito net etc. at MGMH Petlaburj | 1 | Sqm | 10300 | 10300 | 1 | Sqm | 10300 | 10300 | 0 | 0 | Qty increased as per site condition and proposed as AE | AC
|  | AE |  |  |  |  | 0.8 | Sqm | 10300 | 8240 | 8240 | 0 |  | AC
366 | IVF366 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 32mm Thick for Exposed Supply Air duct and finished with UV Protective Paint. at MGMH Petlaburj | 130 | Sqm | 1225 | 159250 | 45.79 | Sqm | 1225 | 56093 | 0 | 103157 | The qty utilised as per site condition and hence savings | AC
|  | Qty V.Pg No-54 of MB-11 | [11 empty] | AC
[11 empty] | 0 | 0 |  | AC
367 | IVF367 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Exposed Return Air Duct and finished with UV Protective Paint. at MGMH Petlaburj | 130 | Sqm | 1075 | 139750 | 103.32 | Sqm | 1075 | 111069 | 0 | 28681 | The qty utilised as per site condition and hence savings | AC
|  | Qty V.Pg No-53 of MB-11 | [11 empty] | AC
[11 empty] | 0 | 0 |  | AC
368 | IVF368 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Supply air duct running inside the building. at MGMH Petlaburj | 40 | Sqm | 785 | 31400 | 40 | Sqm | 785 | 31400 | 0 | 0 | Qty increased to provide proper covering from Dampness and moisture to copper pipe of IVF units and AHU units and proposed as AE | AC
|  | AE |  |  |  |  | 36.7 | Sqm | 785 | 28810 | 28810 | 0 |  | AC
|  | Qty V.Pg No-52 of MB-11 | [11 empty] | AC
AC
369 | IVF369 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 19mm Thick for Return air running inside the building. at MGMH Petlaburj | 40 | Sqm | 660 | 26400 | 40 | Sqm | 660 | 26400 | 0 | 0 | Qty increased to provide proper covering from Dampness and moisture to copper pipe of IVF units and AHU units and proposed as AE | AC
|  | AE |  |  |  |  | 57.49 | Sqm | 660 | 37943 | 37943 | 0 |  | AC
|  | Qty V.Pg No-51 of MB-11 | [11 empty] | AC
AC
370 | IVF370 | Condensing units - VRF/VRV System : Supply, Installation, Nitrogen testing, Vacuuming and Commissioning of air cooled variable refrigerant flow modular type condensing units, each comprising of multiple scroll compressors all inverter driven, full charge of refrigerant gas R-410a including additional gas filling, lubricating oil and all accessories as per the specifications. The condensing units shall be suitable to work on cooling mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1-2001 table 6.2.1B . The COP of the system shall be greater than 4 under ARI conditions for 100percentage load. The condensing units shall be suitable for operation on 415 plus or minus 10percentage volts, 50Hz, 3 phase AC power supply and, outdoor units to be mounted on MS platform with suitable Vibration Isolation pads to avoid vibrations. All the supports and angle base frame structure to be duly black painted with synthetic epoxy paint. the condensing units shall be of following capacities: The VRF ODU should be capable of working with total capacity of connected indoor units ranging between 100percentage to140percentage of ODU capacity. COP minimum 3.5. Make : Daikin / LG / O General / Toshiba at MGMH Petlaburj 16 HP | 1 | Set | 371875 | 371875 | 0 | Set | 371875 |  | 0 | 371875 | As per the site condition & floor plans approved, the increase of indoor units as the new rooms added requires higher capacity of VRV system. Proposed a Supplimental item and quantity of this item not utilized. Hence savings | AC
[11 empty] | 0 | 0 |  | AC
371 | IVF371 | VRF Indoor Units: Hi wall Splits: Supply, Instalation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1-2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 0.8 TR at MGMH Petlaburj | 2 | No | 30700 | 61400 | 2 | No | 30700 | 61400 | 0 | 0 | The item executed as per agreement quantity | AC
|  | Qty V.Pg No-12 of MB-10 | [11 empty] | AC
[11 empty] | 0 | 0 |  | AC
372 | IVF372 | VRF Indoor Units: Hi wall Splits: Supply, Instalation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1-2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.0 TR at MGMH Petlaburj | 3 | No | 30700 | 92100 | 3 | No | 30700 | 92100 | 0 | 0 | Qty increased so as to provide AC in Anesthetist room, Embryologist room, Sample collection room and proposed as AE | AC
|  | AE |  |  |  |  | 3 | No | 30700 | 92100 | 92100 | 0 |  | AC
|  | Qty V.Pg No-12 of MB-10 | [11 empty] | AC
AC
373 | IVF373 | VRF Indoor Units: Hi wall Splits: Supply, Instalation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1-2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.5 TR at MGMH Petlaburj | 4 | No | 35000 | 140000 | 4 | No | 35000 | 140000 | 0 | 0 | Qty increased so as to provide AC in Senior faculty room & UPS Room and proposed as AE | AC
|  | AE |  |  |  |  | 2 | No | 35000 | 70000 | 70000 | 0 |  | AC
|  | Qty V.Pg No-12 of MB-10 | [11 empty] | AC
AC
374 | IVF374 | Cassette Units: Supply, Instalation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1-2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 3.0 TR – 4 way at MGMH Petlaburj | 2 | No | 50000 | 100000 | 0 | No | 50000 |  | 0 | 100000 | As per the site condition & floor plans approved, the pre & post operative ward requires less capacity units. Proposed a Supplimental item and quantity of this item not utilized. Hence savings | AC
[11 empty] | 0 | 0 |  | AC
375 | IVF375 | Supply, Installation, Testing and commissioning of Hard copper REFRIGERANT PIPING of 16swg various sizes with necessary supports, fittings, interconnecting the liquid and lines between the aircooled outdoor units and the indoor units. The piping shall be carried out of Hard drawn copper pipes of type K with soldered / brazed socket fittings. Isolating valves shall be provided to isolate each compressor, strainers, sight glass and any other component requiring proper operation and maintenance. Both the suction and liquid lines shall be insulated with 19mm thick closed cell insulation for above 25mm dia , 13mm thick for pipes below 25mm dia . The insulation finished with treated woven glass fiber reinforced covering for inside Piping and including making required holes in the wall and re finishing and water tight of holes after laying holes as per the specifications and approved drawings at MGMH Petlaburj | 1 | Lot | 400000 | 400000 | 1 | Lot | 400000 | 400000 | 0 | 0 | The item executed as per agreement quantity | AC |  | Supply, Installation, Testing and commissioning of Hard copper REFRIGERANT PIPING of 16swg various sizes with necessary supports, fittings, interconnecting the liquid and lines between the aircooled outdoor units and the indoor units. The piping shall be carried out of Hard drawn copper pipes of type K with soldered / brazed socket fittings. Isolating valves shall be provided to isolate each compressor, strainers, sight glass and any other component requiring proper operation and maintenance. Both the suction and liquid lines shall be insulated with 19mm thick closed cell insulation for above 25mm dia , 13mm thick for pipes below 25mm dia . The insulation finished with treated woven glass fiber reinforced covering for inside Piping and including making required holes in the wall and re finishing and water tight of holes after laying holes as per the specifications and approved drawings at MGMH Petlaburj
|  | Qty V.Pg No-12 of MB-10 | [11 empty] | AC
[11 empty] | 0 | 0 |  | AC
376 | IVF376 | Supply, Installation , Testing and Commissioning of Refnet joints to be provided in refrigerant pipe line. Material of construction for fittings shall be similar to refrigerant piping at MGMH Petlaburj | 10 | Set | 6191 | 61910 | 10 | Set | 6191 | 61910 | 0 | 0 | Qty increased as the no of indoor units increased and proposed as AE | AC
|  | AE |  |  |  |  | 5 | Set | 6191 | 30955 | 30955 | 0 |  | AC
|  | Qty V.Pg No-13 of MB-10 | [11 empty] | AC
AC
377 | IVF377 | Supply and Installation of control cum transmission wiring of size 3C x 1.5 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing and accessories at MGMH Petlaburj | 150 | Rmt | 320 | 48000 | 150 | Rmt | 320 | 48000 | 0 | 0 | The item executed as per agreement quantity | AC
[11 empty] | 0 | 0 |  | AC
378 | IVF378 | Supply and Installation of cabling of size 2C x 1 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing and accessories as per the approved routing at MGMH Petlaburj. | 100 | Rmt | 255 | 25500 | 100 | Rmt | 255 | 25500 | 0 | 0 | The item executed as per agreement quantity | AC
AC
[6 empty] | 3946060 |  |  | PART-A | 2725391 | 374548 | 1595217 | -1220669
[5 empty] | As Per Agreement | 3946060 |  |  | Excess | 374548
[5 empty] | As Per Workdone | 2725391 |  |  | Less | 1595217
[5 empty] | Net Difference | -1220669 |  |  | Net Difference | -1220669
MGPS
379 | IVF379 | SITC of Oxygen Manifold Emergency for 1 plus 1 Cylinders, as per technical specifications. at MGMH Petlaburj | 1 | Set | 20750 | 20750 | 1 | Set | 20750 | 20750 | 0 | 0 | The item executed as per agreement quantity | G
|  | Qty V.Pg No-59 of MB-11 | [11 empty] | G
[11 empty] | 0 | 0 |  | G
380 | IVF380 | SITC of Oxygen Outlets with matching probes, as per HTM-2022/02-01 of UK/NFPA99C of USA as per enclosed technical specifications - Imported at MGMH Petlaburj | 4 | each | 2506 | 10024 | 4 | each | 2506 | 10024 | 0 | 0 | The item executed as per agreement quantity | G
|  | Qty V.Pg No-59 of MB-11 | [11 empty] | G
[11 empty] | 0 | 0 |  | G
381 | IVF381 | SITC of Oxygen Flowmeter with Humidifier, CE Certified with four digit number as per enclosed technical specifications - Imported at MGMH Petlaburj | 4 | each | 1805 | 7220 | 4 | each | 1805 | 7220 | 0 | 0 | The item executed as per agreement quantity | G
|  | Qty V.Pg No-59 of MB-11 | [11 empty] | G
[11 empty] | 0 | 0 |  | G
382 | IVF382 | SITC of Nitrous Oxide Manifold Emergency for 1 Cylinder, with high pressure Regulator, NRV, tailpipes etc. as per technical specifications at MGMH Petlaburj | 1 | Set | 13250 | 13250 | 1 | Set | 13250 | 13250 | 0 | 0 | The item executed as per agreement quantity | G
|  | Qty V.Pg No-59 of MB-11 | [11 empty] | G
[11 empty] | 0 | 0 |  | G
383 | IVF383 | SITC of N20 Outlets with matching probes, as per HTM-2022/02-01 of UK/NFPA99C of USA as per enclosed technical specifications - Imported at MGMH Petlaburj | 4 | each | 2506 | 10024 | 4 | each | 2506 | 10024 | 0 | 0 | The item executed as per agreement quantity | G
|  | Qty V.Pg No-59 of MB-11 | [11 empty] | G
[11 empty] | 0 | 0 |  | G
384 | IVF384 | SITC of C02 Manifold for 2 Cylinders, with high pressure Regulator, NRV, tailpipes etc. as per technical specifications at MGMH Petlaburj | 1 | Set | 20750 | 20750 | 1 | Set | 20750 | 20750 | 0 | 0 | Additional Manifold is provided to supply CO2 at 2-3 bar pressure to IVF OT and proposed as AE | G
|  | AE |  |  |  |  | 1 | Set | 20750 | 20750 | 20750 | 0 |  | G
|  | Qty V.Pg No-59 of MB-11 | [11 empty] | G
[11 empty] | 0 | 0 |  | G
385 | IVF385 | SITC of C02 Outlets with matching probes, as per HTM-2022102- 01ofUK/NFPA99C of USA as per enclosed technical specifications - Imported at MGMH Petlaburj | 4 | each | 2506 | 10024 | 4 | each | 2506 | 10024 | 0 | 0 | The item executed as per agreement quantity | G
|  | Qty V.Pg No-60 of MB-11 | [11 empty] | G
[11 empty] | 0 | 0 |  | G
386 | IVF386 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 12mm COPPER PIPE at MGMH Petlaburj | 24 | Rmt | 642 | 15408 | 21.7 | Rmt | 642 | 13931 | 0 | 1477 | The qty utilised as per site condition and hence savings | G
|  | Qty V.Pg No-60 of MB-11 | [11 empty] | G
[11 empty] | 0 | 0 |  | G
387 | IVF387 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 15mm COPPER PIPE at MGMH Petlaburj | 114 | Rmt | 824 | 93936 | 114 | Rmt | 824 | 93936 | 0 | 0 | Qty. increased as per the site requirement hence proposed as AE | G
|  | AE |  |  |  |  | 87.23 | Rmt | 824 | 71878 | 71878 | 0 |  | G
|  | Qty V.Pg No-60 of MB-11 | [11 empty] | G
G
388 | IVF388 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 22mm COPPER PIPE at MGMH Petlaburj | 36 | Rmt | 1191 | 42876 | 36 | Rmt | 1191 | 42876 | 0 | 0 | Qty. increased as per the site requirement hence proposed as AE | G
|  | AE |  |  |  |  | 42.65 | Rmt | 1191 | 50796 | 50796 | 0 |  | G
|  | Qty V.Pg No-60 of MB-11 | [11 empty] | G
G
389 | IVF389 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 28mm COPPER PIPE at MGMH Petlaburj | 18 | Rmt | 1473 | 26514 | 0 | Rmt | 1473 |  | 0 | 26514 | Not executed as per site conditions hence savings | G
[11 empty] | 0 | 0 |  | G
390 | IVF390 | SITC of Touch type LCD Area Alarm and Zonal Valve box- as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications imported for 3 gases at MGMH Petlaburj | 1 | each | 275000 | 275000 | 1 | each | 275000 | 275000 | 0 | 0 | The item executed as per agreement quantity | G
|  | Qty V.Pg No-61 of MB-11 | [11 empty] | G
[11 empty] | 0 | 0 |  | G
391 | IVF391 | SITC of Touch type LCD Area Alarm and Zonal Valve box-as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications imported for Master Main Alarm including all Gases at MGMH Petlaburj | 1 | each | 375000 | 375000 | 1 | each | 375000 | 375000 | 0 | 0 | The item executed as per agreement quantity | G
|  | Qty V.Pg No-61 of MB-11 | [11 empty] | G
[11 empty] | 0 | 0 |  | G
392 | IVF392 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 15mm 0D at MGMH Petlaburj | 3 | each | 1938 | 5814 | 3 | each | 1938 | 5814 | 0 | 0 | The item executed as per agreement quantity | G
|  | Qty V.Pg No-61 of MB-11 | [11 empty] | G
[11 empty] | 0 | 0 |  | G
393 | IVF393 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 22mm 0D at MGMH Petlaburj | 3 | each | 2740 | 8220 | 3 | each | 2740 | 8220 | 0 | 0 | The item executed as per agreement quantity | G
|  | Qty V.Pg No-61 of MB-11 | [11 empty] | G
[11 empty] | 0 | 0 |  | G
394 | IVF394 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 28mm 0D at MGMH Petlaburj | 4 | each | 4378 | 17512 | 4 | each | 4378 | 17512 | 0 | 0 | The item executed as per agreement quantity | G
|  | Qty V.Pg No-61 of MB-11 | [11 empty] | G
[11 empty] | 0 | 0 |  | G
395 | IVF395 | SITC of Bed Head Panel - as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications at MGMH Petlaburj | 2 | each | 36750 | 73500 | 2 | each | 36750 | 73500 | 0 | 0 | The item executed as per agreement quantity | G
|  | Qty V.Pg No-61 of MB-11 | [11 empty] | G
G
[6 empty] | 1025822 |  |  | PART-A | 1141255 | 143424 | 27991 | 115433
|  | 50038252.82 |  |  |  | 42405299 |  |  |  | 44240940 | 4605075 | 2769434 | 1835641 |  |  | 355.5
|  | Comparision For MGPS Works |  |  | As Per Agreement | 1025822 |  |  | Excess | 143424
[5 empty] | As Per Workdone | 1141255 |  |  | Less | 27991
[5 empty] | Net Difference | 115433 |  |  | Net Difference | 115433
|  | Comparision For Total Agreement Value |  |  | Total As Per Agreement | 42405299 |  |  | Total Excess | 4605075
[5 empty] | Total As Per Workdone | 44240940 |  |  | Total Less | 2769434
[5 empty] | Total Net Difference | 1835641 |  |  | Total Net Difference | 1835641
Equipment Supplemental Works (RATES Adopted From IVF Gandhi Hospital RE)
1 |  | 3-Bay Surgical Scrub Station/Sink to be provided for use in the OT complex providing for pre-procedural scrub up with minimum three bay sink combination as suitable. The Scrub Station shall be made of Stainless Steel of 304 grade sheet with minimum thickness of 1.5mm and designed as per the high aesthetics of the theatre complex. Shall have smoothened surfaces & corners. The scrub sink shall be provided with a front access panel which shall be easily removed for access to the water-controlled valve, waste connections, stoppers & strainers. The Scrub station should be equipped with two foot operated and one elbow operated mechanisms. Shall have provision for fresh water and waste water piping ready for connections. | 0 |  |  |  | 1 | Nos | 97000 | 97000 | 97000 | 0 | This item is mandatorily required for ICMR Clearance, Hence Procured | EQPS
2 |  | Supply and installation of Stainless Steel 304 grade CSSD Rectangular Working table of size 1200 x 480 x 1050 mm with inbuilt sink of size 450 x 380 x 300 mm equipped with jali at bottom to stop any large particles entering into the drain to avoid drain clog. The table to be designed with raised front section and provision of SS sheet at foot level of the table forming a flat surface for storing/placing of items. The table to be of ready to use with all necessary fittings. | 0 | Nos |  |  | 1 | Nos | 46000 | 46000 | 46000 | 0 | An autoclave needs a CSSD table. Hence Procured | EQPS
3 |  | SS-304 working table of size 685 x 685 x 762 mm with I type support inner frame SS-304 pipe of size 40 x 40 x 1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. | 0 | Nos |  |  | 2 | Nos | 16300 | 32600 | 32600 | 0 | It is necessary to place the equipments, hence procured as per the instructions of Enduser & TSMSIDC Higher officials. | EQPS
4 |  | SS-304 working table of size 457 x 457 x 762 mm with I type support inner frame SS-304 pipe of size 40 x 40 x 1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. | 0 | Nos |  |  | 1 | Nos | 14500 | 14500 | 14500 | 0 | It is necessary to place the equipments, hence procured as per the instructions of Enduser & TSMSIDC Higher officials. | EQPS
5 |  | SS-304 working table of size 61 x 610 x 762 mm with I type support inner frame SS-304 pipe of size 40 x 40 x 1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. | 0 | Nos |  |  | 1 | Nos | 15100 | 15100 | 15100 | 0 | It is necessary to place the equipments, hence procured as per the instructions of Enduser & TSMSIDC Higher officials. | EQPS
6 |  | SS-304 working table of size 660 x 610 x 762 mm with I type support inner frame SS-304 pipe of size 40 x 40 x 1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. | 0 | Nos |  |  | 1 | Nos | 15800 | 15800 | 15800 | 0 | It is necessary to place the equipments, hence procured as per the instructions of Enduser & TSMSIDC Higher officials. | EQPS
[9 empty] | PART-B | 221000 | 221000 | 0 | 221000
[5 empty] | As Per Agreement | 0 |  |  | Excess | 221000
[5 empty] | As Per Workdone | 221000 |  |  | Less | 0
[5 empty] | Net Difference | 221000 |  |  | Net Difference | 221000
Civil Supplimental Items (RATES Adopted From IVF Gandhi Hospital RE)
7 |  | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete Finished item of work Old Cement Mortar | 0 | Sqm |  |  | 289.14 | Sqm | 13 | 3759 | 3759 | 0 | The work was taken up as per approved floor plan drawings and in contingent with the main work and hence proposed as supplemental item. | CS
|  | Qty V.Pg No-02 of MB-10, Qty V.Pg No-01 of MB-11 | [11 empty] | CS
[11 empty] | 0 | 0 |  | CS
8 |  | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete Finished item of work Reinforced Cement Concrete | 0 | Cum |  |  | 0.59 | Cum | 4424 | 2610 | 2610 | 0 | The work was taken up as per approved floor plan drawings and in contingent with the main work and hence proposed as supplemental item. | CS
|  | Qty V.Pg No-02 of MB-10, Qty V.Pg No-01 of MB-11 | [11 empty] | CS
[11 empty] | 0 | 0 |  | CS
9 |  | Supply and Installation change room Cubicles at Petlaburj Hospital GENERAL SPECIFICATIONS: Thickness of compact Laminate:12mm Thick Colour OF HPL Boards,In Single Colour,Size of Cubicle As per DWG, Door Size For Normal Cubicles AS per DWG Overall Height of Cubicle,2105mm Including bottom gap of 100mm,Accessories , Manufacturers standard makes of aluminium , SS Accessories .a Aluminium H Top Rail b. SS Hinges c. SS privacy Thumb turn occupancy indicator d.SS coat hook e. SS Door knob f. Aluminium U Channel g.Aluminium Door Stopper Channel h. Runner lining i.SS Screw And PVC Wall Plugs | 0 | Sqm |  |  | 11.3 | Sqm | 9055 | 102322 | 102322 | 0 | This work was executed as per the requirement and instructions from higher officials | CS
|  | Qty V.Pg No-23 of MB-11 | [8 empty] | 0 | 0 |  | CS
[11 empty] | 0 | 0 |  | CS
10 |  | Providing, Fabricating and fixing full height V-board partitions of overall thickness of 75mm Partition frame work to be formed out of 50 X 25mm aluminium frame work placed vertically and horizontally at required centre to centre and cross braced with floor and ceiling channels. The cross bracing channels shall be provided also at above and below the partition framework and to be secured to floor at bottom and to any nearest structural member using galvanized metal screws and wooden / PVC rawl plugs. Partition framework to be cladded with 12.5mm thick tapered edge board on both sides of the partition in line and level fixed with drywall screws @ 300mm c/c with staggered joints to avoid through joints and finished with proprietary supplied jointing tape and compound. | 0 | Sqm |  |  | 13.7 | Sqm | 1625 | 22263 | 22263 | 0 | This work is mandatory in contigent to the main work. Hence, executed. | CS
|  | Qty V.Pg No-25 of MB-11 | [8 empty] | 0 | 0 |  | CS
[11 empty] | 0 | 0 |  | CS
11 |  | Emergency Fire Doors : 46mm thick flush doors made of 0.8mm thick Powder coated GI sheets on both sides, 90 plus or minus 2 kg/m3 density Honeycomb with stand upto 220 Deg.C Temperature, and compressible strength upto 400 Kg/Sqm, 1.2 mm thick GPSP . door frames, double glazed vision panel with necessary adhesive tapes and silicon sealant, necessary hardware like SS304 ball bearing butt hinges, D- handles, push plates, Dorma make door closure, concealed tower bolt, drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms, Both side lock and keys etc. complete. Size 1500 X 2100 mm with 2 hours fire rated and panic push bar and accessories etc. at MGMH Petlaburj | 0 | Nos |  |  | 1 | Nos | 55000 | 55000 | 55000 | 0 | This work was executed as per the requirement and instructions from higher officials | CS
|  | Qty V.Pg No-13 of MB-10 | [8 empty] | 0 | 0 |  | CS
[11 empty] | 0 | 0 |  | CS
12 |  | Providing of Factory made prelaminated FPVC (Foamed Polyvinyl Chloride) Door frame of the size 105x40mm with a wall thickness of 10mm made out of extruded rigid FPVC profile mitre joined with 6 Nos. of 50mm long screw. The door frame shall be fixed to the wall by using 80mm long screws through the frame with the help of PVC fasteners of 3 no's to be provided for each vertical member, GI stiffeners of ("U" channel of size 29x9x1mm, 150mm long) -3 no's at hinge point, Frame reinforcement of("U" GI channel of size 46x22x.06mm), Bottom tie rod of ("U" GI channel size of 15x15x1mm) etc. complete as per manufacturers specification for finished item of work. Maximum door frame size: 980 x 2070 including providing of 35mm thick Factory made Prelaminated ABS (Acrolynitrile Butadyne Styrene) Door shutter moulded in in different designs, consisting of all round Frame made out of water proof solid foam PVC bar of size 20x32mm, reinforced by 32x 32mm 2 nos. for vertical made out of LVL (Laminated Veneer Lumber), core material of 32 mm thick high density craft paper honey comb board, sandwiched on both sides with prelaminated ABS sheet thickness of 1.5mm. PVC edge banding of size 0.45mm on the vertical sides. Hardware made out of steel coated butterfly hinges - 3 Nos. for each shutter and ISI make S.S round lock completes for finished item of work. Maximum shutter size of : 910 x 2030 mm | 0 | Sqm |  |  | 32.08 | Sqm | 9241 | 296451 | 296451 | 0 | To maitain low VOC in Fertility center, wooden doors are replaced with ABS doors as per MOM dated: 01-08-2023. (copy Attached) | CS
CS
|  | Qty V.Pg No-44 of MB-11 | [11 empty] | CS
CS
13 |  | Providing and fixing factory made solid Wood Polymer Composite (WPC) single extruded Door Frame section of 100*65 MM with encapsulation of 6 MM rigid layer on all external surfaces. The door frame will have a rebate of 32MM/ 37 MM. The two Vertical members are to be joined together with the horizontal member using 8x75 MM long MS Star full thread screws to be used with reverse forward speed control hand drilling machine. The ready/assembled door frame is fixed to wall using Z Hand fast 300 MM long hold fast. Supplying and fixing of 28/30 mm thick Wood Plastic Composite (WPC) Door shutter, comprising of 70% virgin polymer, 15% wood powder (fiber), and the remaining 15% additives, comprising of virgin PVC polymer of K value 58-60 (Suspension grade), Calcium carbonate and natural fibers (wood powder) and non toxic additives (maximum toxicity index of 12 for 100 gms) having minimum door density of 650 kg/cum, screw withdrawal strength 1800N (Face) & 900N (Edge), Modulus of Elasticity 900N/mm2 and resistance to spread of flame of Class A category with property of being termite/borer poof, water/moisture proof and fire retardant and fixed in position with stainless steel butt hinges of required size with necessary full body threaded star headed counter sunk SS screws all as per direction of Engineer -in- Charge (SS butt hinges and SS screws shall be paid separately) | 0 | Sqm |  |  | 9.21 | Sqm | 6734 | 62020 | 62020 | 0 | To maitain low VOC in Fertility center, wooden doors are replaced with WPC doors as per MOM dated: 01-08-2023. (copy Attached) | CS
CS
[11 empty] | 0 | 0 |  | CS
14 |  | 50 LPH storage type RO of dimensions 525 x 425 x 1450 mm (WxDxH) of approx. weight 75Kg consists of 4 nos of 80 GPD 3-layer Thin Film Composite (TFC) membrane with 0.0001-micron pore size which can prevent TDS, heavy metals and equipped with 6 stage purification process which reduces pesticides in the water for reducing scale formation when water is heated. The RO should take min input pressure of 0.6 kg/cm2, 2000 ppm of TDS in Water, 500 ppm of Hardness, 6.5 to 8.5 PH of water which can give output of 20 to 25 % recovery in purified water and can run on 230V AC, 50 Hz supply with operating temp of 5oC to 45oC. | 0 | Nos |  |  | 1 | Nos | 75000 | 75000 | 75000 | 0 | Autoclave needs clean water as per ICMR guidelines, hence this item is procured | CS
15 |  | Supply of Sun Control film to the glazed windows (For Windows & Door view Windows) |  |  |  |  | 48 | Sqm | 381 | 18288 | 18288 |  | This work was taken up at Record room, P Change room, Pre/Post Operative wards, Embryologist room, Store room and Semen Collection room as per the instructions issued by the End user and TSMSIDC higher officials. | CS
16 |  | Providing and fixing Aluminium Extruded Section Body Tubular Type Hydraulic Door Closer (IS: 3564) with double speed adjustment with necessary accessories and screws etc. complete. |  |  |  |  | 15 | Nos | 2819 | 42285 | 42285 |  | This work was executed as per the requirement and instructions from higher officials | CS
17 |  | Supply and fixing of Dress Hangers of size 450mm length with 8 Nos hooks, each capped with plastic protective cap (in change rooms). |  |  |  |  | 5 | Nos | 510 | 2550 | 2550 |  | This work was executed as per the requirement and instructions from higher officials | CS
18 |  | Supplying and fixing Rectangular Mirror Frameless of size 457 .2 mm x 609.6 mm (For Change room) |  |  |  |  | 5 | Nos | 1775 | 8875 | 8875 |  | This work was executed as per the requirement and instructions from higher officials | CS
19 |  | Name Plates (Room Names) as approved by the Engineer In-charge. |  |  |  |  | 38 | Nos | 600 | 22800 | 22800 |  | This work was executed as per the requirement and instructions from higher officials | CS
21 |  | Providing and fixing PVC frames on the walls for covering the area over DB Boxes with 12 mm PVC sheets in a box section of 60mm thick including neccesary accessories |  |  |  |  | 0.74 | Sqm | 6473 | 4790 | 4790 | 0 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
20 |  | AHU shed with provision for fencing, door with lock- key arrangement shall be provided with Framework vertically made of MS Square Pipe frame: 2 Inches X 2 Inches, 16Gauge M S Fencing with wire mesh: ½ inch X ½inch. Supporting Structure M S Angle: 50 X 5mm GI pre-coated corrugated profile roof sheet: 0.5 mm thick duly supported with JHook 10 SWG with provision of door with lock and key AHU Shed with fencing should be duly enamel painted and with anti-rust coating from both sides. |  |  |  |  | 1 | Job | 300000 | 300000 | 300000 |  | This work was executed as per the requirement and instructions from higher officials | CS
|  | Civil Supplimental Items (RATES as per Quotation and SSR 2022-23) | [11 empty] | CS
22 |  | Providing Thermo Mechanically Treated ( TMT) ( Fe-500/500D/550D from primery producer TATA, SAIL, VSP, JSW Steel, Goel steel, Jindal panther, X- Vega & balaji Shakthi as per IS 1786-2008) of Different Diameters RCC Works , including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and sizes and typing and lap - spacing with binding wire of 18 SWG, Forming grills for reinforcement work as per approved design and drawings, including and conveyanace of steel bars, including all wastages such as overlaps, coupling, chairs, spacer bars including cost and conveyance of binding wire cover blocks and incidential, operational, labour charges such as cutting bending, placing in position, typing incliding sales and other taxes on all materials etc., and overheads & contractors profit completefor finished item of work | 0 | MT |  |  | 0.3 | MT | 95386 | 28616 | 28616 | 0 | This work is exectued as per site conditions. | CS
|  | Qty V.Pg No-02 of MB-10 | [11 empty] | CS
23 |  | Supplying and fixing of to windows / in open court yards using 25mm x 6mm MS flat alround and 10mm MS square bars horizontally at 125mm centre to centre and vertically at 300mm centre to centre including fixing with 4 Nos of MS Z holdfasts (2 on each side) duly making cutting brick masonry, fixing and making to original surface neatly and painting grill with one coat of red oxide primer including cost all taxes and conveyance of all materials including cutting, bending, welding including all operational charges and all labour charges etc., complete for finished item of work. | 0 | Sqm |  |  | 39.78 | Sqm | 1791 | 71246 | 71246 | 0 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
24 |  | Supply and placing of the Design Mix Concrete M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Weight Batcher / Concrete mixer with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials, centering using Casurina Ballies, Bamboos, Wooden Reapers, Runners, Wood Posts, Steel Plates etc., including all operational, incidental and labour charges such as weigh batching, machine mixing, lifting of concrete manually, laying concrete, curing, overheads & contractors profit etc., complete but excluding cost of steel and its fabrication charges for finished item of work (APSS No. 402) | 0 | Cum |  |  | 0.75 | Cum | 14683 | 11012 | 11012 | 0 | This work is exectued as per site conditions. | CS
|  | Qty V.Pg No-02 of MB-10 | [11 empty] | CS
25 |  | Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free fullbody porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707) | 0 | Rmt |  |  | 174.5 | Rmt | 151 | 26350 | 26350 | 0 | This work was executed as per the requirement and instructions from higher officials | CS
|  | Qty V.Pg No-03 of MB-10 | [11 empty] | CS
[11 empty] | 0 | 0 |  | CS
[9 empty] | PART-B | 1156237 | 1156237 | 0 | 1156237
[5 empty] | As Per Agreement | 0 |  |  | Excess | 1156237
[5 empty] | As Per Workdone | 1156237 |  |  | Less | 0
[5 empty] | Net Difference | 1156237 |  |  | Net Difference | 1156237
Plumbing Supplimental Works (RATES Adopted From IVF Gandhi Hospital RE)
26 |  | Supplying and fixing 50 mm Nominal Bore GI pipe Medium Grade properties & weight as per IS 1239 in ground or on wall with GI fittings such as elbows tees couplings, nipples, plugs including excavation for trenches and refilling the trenches ,chiselling masonry walls and making good the walls & floors to the original surface and fixing MS clamps on TW blocks on walls including cost and conveyance of all materials and labour charges , overheads & contractors profit complete for finished item of work except for GI bends union and GI connectors with checkout and socket Tata or Zenith make or equivalent. (For Autoclave) | 0 | Rmt |  |  | 15 | Rmt | 599 | 8985 | 8985 | 0 | This work is mandatory for autoclave to let out the steam outside the premises. Hence executed. | PS
[9 empty] | PART-B | 8985 | 8985 |  | 8985
[5 empty] | As Per Agreement | 0 |  |  | Excess | 8985
[5 empty] | As Per Workdone | 8985 |  |  | Less | 0
[5 empty] | Net Difference | 8985 |  |  | Net Difference | 8985
Electrical Supplimental Items (RATES Adopted From IVF Gandhi Hospital RE)
27 |  | Supply and Transportation 56W Clean room Light fixture, 2' x2' (600mm x600mm) LED luminaire CRCA powder coated white after phosphocreatine treatment provided as standard. with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% etc., complete. Make: Philips | 0 | Nos |  |  | 12 | Nos | 17241 | 206892 | 206892 | 0 | During site inspection, The TSMSIDC higher officials has instructed to provide 56W lights to attain required illumination. Hence executed. | ES
|  | Qty V.Pg No-39 of MB-11 | [11 empty] | ES
[11 empty] | 0 | 0 |  | ES
28 |  | Supply and Transportation of 48" ( 1200 mm) High Speed Fan Sweep Celing Fan with all accessories etc., complete. Make Havells S S 390 | 0 | Nos |  |  | 28 | Nos | 4317 | 120876 | 120876 | 0 | During site inspection The TSMSIDC higher officials instructed to provide regular high speed fans since maintaining BLDC fans in governement instutions is not viable. Hence executed | ES
|  | Qty V.Pg No-40 of MB-11 | [11 empty] | ES
[11 empty] | 0 | 0 |  | ES
29 |  | Labour charges for fixing of ceiling fan and regulator including transportation and giving connections with twin core wire etc., complete. | 0 | Nos |  |  | 28 | Nos | 185 | 5180 | 5180 | 0 | As per Instructions of the TSMSIDC higher officials during site inspection, regular high speed fans were provided. Hence executed | ES
|  | Qty V.Pg No-41 of MB-11 | [11 empty] | ES
[11 empty] | 0 | 0 |  | ES
30 |  | Supply & fixing of 2nos6A, 2 in one socket - 2 Nos with 6A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benz Plus | 0 | Nos |  |  | 20 | Nos | 1178 | 23560 | 23560 | 0 | 6Amp socket was required as per site conditions. Hence executed | ES
|  | Qty V.Pg No-42 of MB-11 | [11 empty] | ES
[11 empty] | 0 | 0 |  | ES
31 |  | Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete | 0 | Nos |  |  | 28 | Nos | 162 | 4536 | 4536 | 0 | As difference in false ceilling one meter down rods are used as per site conditions | ES
|  | Qty V.Pg No-43 of MB-11 | [11 empty] | ES
[11 empty] | 0 | 0 |  | ES
32 |  | Supply and fixing of 12 Way SPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand and Supply and Fixing of 1 No., of 63A FP MCB as incomer and 8 Nos 6-32 A 10kA SP MCBs Makes: Legrand-DX3 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. (For UPS DBs) | 0 | Nos |  |  | 2 | Nos | 9444 | 18888 | 18888 | 0 | It is mandatory to provide 12 Way SPN DB for UPS Distribution System Hence executed | ES
|  | Qty V.Pg No-43 of MB-11 | [11 empty] | ES
[11 empty] | 0 | 0 |  | ES
33 |  | Supply and fixing of cable adopteres box with cover for DBs including, massanory work etc., complete., | 0 | Nos |  |  | 8 | Nos | 5085 | 40680 | 40680 | 0 | It is mandatory to provide cable adapters to connect RAW power with UPS power. Hence executed | ES
|  | Qty V.Pg No-43 of MB-11 | [11 empty] | ES
[11 empty] | 0 | 0 |  | ES
34 |  | Supply and fixing of FP Metal Enclosure with IP 20 Protection DB Make with 1 No 63A, 10 KA DP MCB including internal connection and labour charges for Flush Mounting etc.,complete. Makes of Enclousure : Legrand MCB Makes : Legrand-DX3 | 0 | Nos |  |  | 2 | Nos | 4203 | 8406 | 8406 | 0 | It is mandatory required to connect Power supply to autoclave and Air shower unit | ES
|  | Qty V.Pg No-43 of MB-11 | [11 empty] | ES
ES
35 |  | 4C x 1.5 Sqmm Copper Flexible Cable For Condensing Unit to Electrical Panel Makes : Polycab |  |  |  |  | 210 | Rmt | 130 | 27300 | 27300 | 0 | It is mandatory to provide for AHU Connection System, Hence executed | ES
ES
36 |  | Proving and fixing Track lights at side wall décor frame with 4 fixtures and 2 tracks |  |  |  |  | 1 | Job | 9600 | 9600 | 9600 | 0 | This work was executed as per the requirement and instructions from higher officials | ES
[11 empty] | 0 | 0 |  | ES
|  | Electrical Supplimental Items (RATES as per SSR 2022-23) | [11 empty] | ES
37 |  | Supply and fixing of suitable out door feeder piller box of size made with 14 SWG CRCA sheet with double door arrangement, making powder coating after processing of 7 Tank process, lock and key, hinges, rubber gasket, danger board,suitable angle iron stand for mounting the feeder pillar with cement concrete, including Supply and fixing of Legrand / Schnieder make as out goings, indication lamps, din channel, 6 Sqmm 3 core copper cable for invidual light control, connectors, bus bars, shroudings, gland plates and provision for 3 phase energy meter etc., complete for finished item of work and suitable wiring provision for connecting the nature switch with following.63A, 4 Pole MCB as incomer, 9 Nos 6-32A SP MCBs | 0 | Nos |  |  | 1 | Nos | 30768 | 30768 | 30768 | 0 | It is mandatory to provide fedder pillar box to control separate AC units on terrace for maintenace of units | ES
Qty V.Pg No-44 of MB-11
[9 empty] | PART-B | 496686 | 496686 | 0 | 496686
[5 empty] | As Per Agreement | 0 |  |  | Excess | 496686
[5 empty] | As Per Workdone | 496686 |  |  | Less | 0
[5 empty] | Net Difference | 496686 |  |  | Net Difference | 496686
Air Conditioning Supplemental Works (RATES Adopted From IVF Gandhi Hospital RE)
38 |  | Supply & Installation of MS Angle for Duct Support, Cable Tray Support and Condensing Unit Stand of size 50 X 50 x 5 mm Thick. | 0 | Kg |  |  | 211.24 | Kg | 190 | 40136 | 40136 | 0 | It is mandatorly required for support duct hence this work is executed as per the instructions of TSMSIDC Higher officials. | ACS
|  | Qty V.Pg No-24 of MB-11 | [11 empty] | ACS
ACS
39 |  | Supply & Installation of MS Angle for Duct Support, Cable Tray Support and Condensing Unit Stand of size 32 X 32 x 5 mm Thick. | 0 | Kg |  |  | 74.25 | Kg | 190 | 14108 | 14108 | 0 | It is mandatorly required for support duct hence this work is executed as per the instructions of TSMSIDC Higher officials. | ACS
|  | Qty V.Pg No-25 of MB-11 | [11 empty] | ACS
ACS
40 |  | Supply and installation of Canvas Connections For AHUS | 0 | Nos |  |  | 2 | Nos | 6500 | 13000 | 13000 |  | Its mandatorly required for support duct hence this work is executed as per the instructions of TSMSIDC Higher officials. | ACS
ACS
|  | Air Conditioning Supplemental Works (RATES as per Quotation) | [11 empty] | ACS
41 |  | Condensing units - VRF/VRV System : Supply, Installation, Nitrogen testing , Vacuuming and Commissioning of air cooled variable refrigerant flow modular type condensing units, each comprising of multiple scroll compressors all inverter driven, full charge of refrigerant gas R-410a including additional gas filling , lubricating oil and all accessories as per the specifications. The condensing units shall be suitable to work on cooling mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B . The COP of the system shall be greater than 4 under ARI conditions for 100percentage load . The condensing units shall be suitable for operation on 415 plus or minus 10percentage volts, 50Hz, 3 phase AC power supply and , outdoor units to be mounted on MS platform with suitable Vibration Isolation pads to avoid vibrations. All the supports and angle base frame structure to be duly black painted with synthetic epoxy paint. the condensing units shall be of following capacities: The VRF ODU should be capable of working with total capacity of connected indoor units ranging between 100percentage to 140percentage of ODU capacity . COP minimum 3.5. Make : Daikin / LG / O General / Toshiba at MGMH Petlaburj 22 HP | 0 | Nos |  |  | 1 | Nos | 402500 | 402500 | 402500 | 0 | As per the site condition & floor plans approved, the increa of indoor units as the new rooms added requires higher capacity of VRV system. Hence proposed as Supplimental item | ACS |  | 362250
|  | Qty V.Pg No-11 of MB-10 | [11 empty] | ACS
[11 empty] | 0 | 0 |  | ACS
42 |  | Cassette Units : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling mode.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 2.0 TR – 4 way at MGMH Petlaburj | 0 |  |  |  | 2 | Nos | 40000 | 80000 | 80000 | 0 | As per the site condition & floor plans approved, the pre & post operative ward requires less capacity units. Hence proposed as Supplimental item | ACS
|  | Qty V.Pg No-12 of MB-10 | [11 empty] | ACS
[11 empty] | 0 | 0 |  | ACS
43 |  | Modular Double skin floor mounted EUROVENT Certified Air Handling Unit 4400CFM / 11.0 TR / 150mm SP made out of 45 plus or minus 2mm thick PUF insulated panels Thermal break aluminium profile frame work with 0.8mm thick pre painted / powder coated inner and outer skins comprising of mixing box with fresh air and return air dampers, pre filters with 10 and 5 microns combination filters in single frame, Interlaced/Intertwined DX Cooling Coil suitable for connecting 2 nos of 11.0TR capacity 1W plus 1S out door condensing units, SS304 drain pan with , blower section with Nicotra / Kruger make direct drive/ Plug type fan, vibration isolators, EFF1 motor and blower section with on/off switches to operate from outside, limit switch for the fan section access door with a view port, fine filter section with 3 microns filters inspection doors for all filter and fan sections and damper at the outlet of unit. Ports for differential pressure gauges across all filters and blower to measure differential pressure. AHU Make : VTS / Systemair, Make - Blower - Nicotra / Kruger ; Motor - Crompton Greaves / Siemens ; Filter - Thermodyne / Freudenberg / Ultrafil at MGMH Petlaburj | 0 | Nos |  |  | 1 | Nos | 718500 | 718500 | 718500 | 0 | As per the site condition & floor plans approved, the increased area requires higher capacity of AHU. Hence proposed as Supplimental item. | ACS | 708000
|  | Qty V.Pg No-54 of MB-11 | [11 empty] | ACS
[11 empty] | 0 | 0 |  | ACS
44 |  | SITC of air cooled condensing units with two scroll compressors, air cooled condenser, power panel, vibration isolating pads, stand for ODU, thermostat, etc. of the following capacities. The nominal capacity of the condensing unit shall be as under. Air cooled condensing unit shall have horizontal discharge. All refrigerant piping accessories sight glass, drier, expansion valve, etc. shall be supplied with the condensing units and suitable to connect above AHUs. Refrigerant shall be R 407C / R 410A. Necessary thermostat, control wiring, etc. shall be included. Derating of the unit shall not be more than 15percentage under 45 deg. C ambient temperature. Condensing unit shall be capable of operating up 50 deg. C ambient temperature. 11.0 TR capacity at MGMH Petlaburj | 0 | Nos |  |  | 2 | Nos | 240750 | 481500 | 481500 | 0 | As per the site condition & floor plans approved, the increased area requires higher capacity of condensing unit to maintain required temperature and increase in AHU capacity too. Hence proposed as Supplimental item | ACS | 218400
|  | Qty V.Pg No-55 of MB-11 | [11 empty] | ACS
[9 empty] | PART-B | 1749744 | 1749744 | 0 | 1749744
[5 empty] | As Per Agreement | 0 |  |  | Excess | 1749744
[5 empty] | As Per Workdone | 1749744 |  |  | Less | 0
[5 empty] | Net Difference | 1749744 |  |  | Net Difference | 1749744
MGPS Supplemental Works (RATES Adopted From IVF Gandhi Hospital RE)
45 |  | Fully Automatic Control Panel for Oxygen System: Supply, installation and commissioning of Fully Automatic control panel for unintrupted Oxygen supply | 0 | Set |  |  | 1 | Set | 175180 | 175180 | 175180 | 0 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
46 |  | Trigas Emergency Manifold: SITC of Emergency Trigas Manifold maximum for 1+1 D-type Gas Cylinders complete with separate NRVs, tail pipes and brass fittings for each cylinders. | 0 | Set |  |  | 1 | Set | 9620 | 9620 | 9620 | 0 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
47 |  | Fully Automatic Control Panel for Trigas System: Supply, installation and commissioning of Fully Automatic control panel for unintrupted Nirous Oxide supply. | 0 | Set |  |  | 1 | Set | 175180 | 175180 | 175180 | 0 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
48 |  | Fully Automatic Control Panel for CO2 System: Supply, installation and commissioning of Fully Automatic control panel for unintrupted Nirous Oxide supply. | 0 | Set |  |  | 1 | Set | 175180 | 175180 | 175180 | 0 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
49 |  | SITC of Medical Air-4 Outlet with matching probe as per HTM-2022/02-01 of UK/ NFPA 99C of USA as per enclosed technical Specification. | 0 | Nos |  |  | 6 | Nos | 12470 | 74820 | 74820 | 0 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
50 |  | 12 mm Valve for 12 mm OD Pipe Note: New item added | 0 | Nos. |  |  | 3 | Nos. | 930 | 2790 | 2790 | 0 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
51 |  | Supply and installation of 46.7 liter size CO2 cylinders confirming to IS:7285 Part-2 (2017). The cylinder shall have an outer diameter of 232mm, a nominal length of 1365mm, and a minimum wall thickness of 5.3mm, ensuring robustness and safety during handling and storage. The cylinders shall have a capacity of 46.7 liters and comply with the standards set forth by the Indian Standards Institute. They shall be constructed from high-quality 37 Mn (Carbon Manganese) material, guaranteeing durability and reliability. The design shall feature a concave bottom and neck threading conforming to IS 3224:2002 14 TPI Type 4 - Size 2 specifications, facilitating secure connections and ease of use. The cylinder shall be capable of withstanding a test pressure of 250 BAR and have a working pressure of 150 BAR. The nominal tare weight of each cylinder shall be 51 kg. The cylinder includes first fill. | 0 | Nos. |  |  | 2 | Nos | 20850 | 41700 | 41700 | 0 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
52 |  | Supply and installation of 46.7 liter size O2 cylinders confirming to IS:7285 Part-2 (2017). The cylinder shall have an outer diameter of 232mm, a nominal length of 1365mm, and a minimum wall thickness of 5.3mm, ensuring robustness and safety during handling and storage. The cylinders shall have a capacity of 46.7 liters and comply with the standards set forth by the Indian Standards Institute. They shall be constructed from high-quality 37 Mn (Carbon Manganese) material, guaranteeing durability and reliability. The design shall feature a concave bottom and neck threading conforming to IS 3224:2002 14 TPI Type 4 - Size 2 specifications, facilitating secure connections and ease of use. The cylinder shall be capable of withstanding a test pressure of 250 BAR and have a working pressure of 150 BAR. The nominal tare weight of each cylinder shall be 51 kg. The cylinder includes first fill. | 0 | Nos. |  |  | 2 | Nos | 17850 | 35700 | 35700 | 0 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
53 |  | Supply and installation of 46.7 liter size Trigas cylinders confirming to IS:7285 Part-2 (2017). The cylinder shall have an outer diameter of 232mm, a nominal length of 1365mm, and a minimum wall thickness of 5.3mm, ensuring robustness and safety during handling and storage. The cylinders shall have a capacity of 46.7 liters and comply with the standards set forth by the Indian Standards Institute. They shall be constructed from high-quality 37 Mn (Carbon Manganese) material, guaranteeing durability and reliability. The design shall feature a concave bottom and neck threading conforming to IS 3224:2002 14 TPI Type 4 - Size 2 specifications, facilitating secure connections and ease of use. The cylinder shall be capable of withstanding a test pressure of 250 BAR and have a working pressure of 150 BAR. The nominal tare weight of each cylinder shall be 51 kg. The cylinder includes first fill. | 0 | Nos. |  |  | 2 | Nos | 29250 | 58500 | 58500 | 0 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
54 |  | Supply and installation of 46.7 liter size N2O cylinders confirming to IS:7285 Part-2 (2017). The cylinder shall have an outer diameter of 232mm, a nominal length of 1365mm, and a minimum wall thickness of 5.3mm, ensuring robustness and safety during handling and storage. The cylinders shall have a capacity of 46.7 liters and comply with the standards set forth by the Indian Standards Institute. They shall be constructed from high-quality 37 Mn (Carbon Manganese) material, guaranteeing durability and reliability. The design shall feature a concave bottom and neck threading conforming to IS 3224:2002 14 TPI Type 4 - Size 2 specifications, facilitating secure connections and ease of use. The cylinder shall be capable of withstanding a test pressure of 250 BAR and have a working pressure of 150 BAR. The nominal tare weight of each cylinder shall be 51 kg. The cylinder includes first fill. | 0 | Nos. |  |  | 2 | Nos | 33000 | 66000 | 66000 | 0 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
[9 empty] | PART-B | 814670 | 814670 | 0 | 814670
|  | Comparision For MGPS Supplimental works |  |  | As Per Agreement | 0 |  |  | Excess | 814670
[5 empty] | As Per Workdone | 814670 |  |  | Less | 0
[5 empty] | Net Difference | 814670 |  |  | Net Difference | 814670
[5 empty] | TOTAL (PART-B) | 0 |  |  |  | 4447322 | 4447322 |  | 4447322
|  | Comparision For All Supplimental Works |  |  | As Per Agreement | 0 |  |  | Excess | 4447322
[5 empty] | As Per Workdone | 4447322 |  |  | Less | 0
[5 empty] | Net Difference | 4447322 |  |  | Net Difference | 4447322
|  | GRAND TOTAL |  |  |  | 42405299 |  |  |  | 48688262 | 9052397 | 2769434 | 6282963
[9 empty] | TOTAL EXCESS | 6282963
|  | Comparision For Total RE Values |  |  | As Per Agreement | 42405299 |  |  | Excess | 9052397
[5 empty] | As Per Workdone | 48688262 |  |  | Less | 2769434
[5 empty] | Net Difference | 6282963 |  |  | Net Difference | 6282963

## LumpSumItems
LS ITEMS LIST
S.No | Item Description | UOM | Qty | Rate (Rs.) | Amount (Rs.)
1 | Powder coated GI stand in IVF OT | Nos | 1 | 80000 | 80000
2 | High Quality IVF Procedural photos at Entrance and Reception | Nos | 12 | 9000 | 108000
3 | 60mm Thick Box framing as the back support for the name plate at Entrance | Sqm | 3.98 | 11012 | 43828
4 | Door Frame side Paneling at Entrance | Sqm | 7.551 | 9250 | 69847
5 | 32mm Double Flush Door (1800 x 2100 mm door) at Entrance | Nos | 1 | 56500 | 56500
6 | Name Plate With Glossy Laminate at Entrance | Sqm | 2.6 | 9580 | 24908
7 | MIRROR GOLD TITANIUM LETTERS & S.S. MIRROR LETTERS at Entrance | Job | 1 | 67500 | 67500
8 | Double side ACP sheet (Name board wth three languages fixed at IVF Entrance Corridor) | Nos | 1 | 6000 | 6000
9 | Foam Board (Name board wth three languages with direction to IVF Center fixed at 3rd floor) | Nos | 2 | 2800 | 5600
10 | Foam Board (Name board wth with direction to Rooms fixed to wall in IVF Corridor,) | Nos | 2 | 3200 | 6400
11 | Main IVF logo with LED arcylic board at Entrance | Nos | 1 | 11475 | 11475
12 | Addressable fire control panel at Entrance | Nos | 1 | 291366 | 291366
|  |  |  | TOTAL | 771424
|  |  |  | GST @ 18% | 138856.32
|  |  |  | Total Amount can be claimed including GST | 910280.32

## Add_Items_Part-C
PART-C
Additional Items As Per IVF Gandhi
S.No | Item Description | QTY | UOM | Rate (Rs.) | Amount (Rs.) | Remarks
Equipment
1 | Fowler Two Function Bed with ABS Panel in Pre and Post Operative wards and Semen Collection room | 5 | Nos | 39000 | 195000 | As Per IVF Gandhi
2 | Bed side Table with ABS Plastic body in Pre and Post Operative wards and Semen Collection room | 5 | Nos | 9000 | 45000 | As Per IVF Gandhi
3 | Corporate Deluxe Locker with SS 304 grade Top in Sample Collection and Injection Room | 1 | Nos | 8400 | 8400 | As Per IVF Gandhi
4 | Bed side stand with full SS 304 grade constructionof in Sample Collection and Injection Room | 1 | Nos | 9300 | 9300 | As Per IVF Gandhi
5 | Bed side stand with full GI Powder coated constructionof in Semen Collection room | 1 | Nos | 4200 | 4200 | As Per IVF Gandhi
6 | Supply of a Sample collection chair in Sample Collection and Injection Room | 1 | Nos | 16200 | 16200 | As Per IVF Gandhi
7 | Sample collection bed in Sample Collection and Injection Room | 1 | Nos | 29000 | 29000 | As Per IVF Gandhi
8 | Cryo Can 11 Ltr without wheels in Cryo room | 1 | Nos | 32000 | 32000 | As Per IVF Gandhi
9 | The Multipurpose Electro Hydraulic Mobile OT Table in Major OT | 1 | Nos | 210000 | 210000 | As Per IVF Gandhi
|  |  |  | Sub Total | 549100
Furniture
10 | Writing board in Counselling rooms | 1 | Nos | 2100 | 2100 | As Per IVF Gandhi
11 | MDF wooden table in Reception and Ultrasound room | 2 | Nos | 14500 | 29000 | As Per IVF Gandhi
12 | Office table in Embryologist and Anesthetist room | 2 | Nos | 16000 | 32000 | As Per IVF Gandhi
13 | Window blinds (For semen collection room & Counselling room Windows) | 15 | Sqm | 2187 | 32805 | As Per IVF Gandhi
14 | Sofa | 2 | Nos | 24000 | 48000 | As Per IVF Gandhi
|  |  |  | Sub Total | 143905
|  |  |  | Total | 693005
|  |  |  | GST | 124740.9
|  |  |  | Total | 817745.9
|  |  |  | TSMSIDC Charges, NAC & Labour Cess @ 5.11% | 41786.8155
|  |  |  | Grand Total | 859532.7155

## Add_Items_Part-D
PART-D
Extra Items As Per Doctors Letter
1 | Consultant Chair in Embryologist and Anesthetist room | 3 | Nos | 20000 | 60000 | Extra Items
2 | Patient Chair Embryologist and Anesthetist room | 6 | Nos | 13500 | 81000 | Extra Items
3 | Lab Chairs Type I (DCA Price) in Andrology Lab & Embryology Lab | 10 | Nos | 15340 | 153400 | Extra Items
|  |  |  | Sub Total | 294400
|  |  |  | GST | 52992
|  |  |  | Sub Total | 347392
|  |  |  | TSMSIDC Charges, NAC & Labour Cess @ 5.11% | 17751.7312
|  |  |  | Grand Total | 365143.7312

## ABSTRACT
Name of the work: Design, fabrication, establishing & commissioning of In-Vitro Fertility Centers (IVFCs) along with allied services on Turnkey basis at Gandhi Hospital, Secunderabad, MGM Hospital, Warangal & MGMH Petlaburj, Hyd.
COMPARATIVE STATEMENT
S.No | Description |  | As per Agreement | As per workdone | Excess | Less | Net Difference
1 | Equipment |  | 26020475 | 26020475 | 0 | 0
2 | Civil Works |  | 5915529 | 7012631 | 1910379 | 813277
3 | Plumbing works |  | 215122 | 136973 | 7086 | 85235
4 | Electrical works |  | 3719411 | 5641335 | 2169638 | 247714
5 | ELV works |  | 689000 | 689000 | 0 | 0
6 | Fire Fighting works |  | 873880 | 873880 | 0 | 0
7 | Air Conditioning works |  | 3946060 | 2725391 | 374548 | 1595217
8 | MGPS works |  | 1025822 | 1141255 | 143424 | 27991
| Sub Total (Agreement Part-A) |  | 42405299 | 44240940 | 4605075 | 2769434 | 1835641
9 | Equipment supplimental |  | 0 | 221000 | 221000 | 0
10 | Civil supplimental works |  | 0 | 1156237 | 1156237 | 0
11 | Plumbing supplimental works |  | 0 | 8985 | 8985 | 0
12 | Electrical supplimental works |  | 0 | 496686 | 496686 | 0
14 | Air Conditioning supplimental works |  | 0 | 1749744 | 1749744 | 0
15 | MGPS supplimental works |  | 0 | 814670 | 814670 | 0
| Sub Total (Supplimental Part-B) |  | 0 | 4447322 | 4447322 | 0
| Total (Part-A+Part-B) |  | 42405299 | 48688262 | 9052397 | 2769434 | 6282963
16 | Provision towards Engineering Supervision Charges @ 4% on RE Value | 4% | 1696212 | 1947530 | 251318 | 0
| GST @ 18% |  | 7632953.82 | 8763887.16 | 1130933 | 0
|  |  | 51734465 | 59399679.16 | 10434648 | 2769434 | 7665214
17 | Labour Cess @ 1% on Basic Price of Revised Estimate | 1% |  | 486882.62 | 486883 | 0
18 | NAC @ 0.1% on Basic Price of Revised estimate | 0.1% |  | 48688.262 | 48688 | 0
19 | Provision towards Seniorage Charges on Civil Component |  |  | 448 | 448 | 0
20 | Provision towards DMF Charges 30% on Seniorage Charges | 30% |  | 134.4 | 134 | 0
21 | Provision towards SMFT Charges 2% on seniorage Charges | 2% |  | 8.96 | 9 | 0
22 | Provision towards Haritha Nidhi | 0.01% |  | 4868.8262 | 4869 | 0
23 | Sub total of S.No 17 to 22 |  |  | 541031 | 541031 | 0
24 | Provision towards GST 18% on Seniorage Charges | 18% |  | 97385.58 | 97386 | 0
25 | Provision towards Unforseen items and rounding off (LS) - |  | 3265535 | 910280 | 0 | 2355255
| Sub total of S.No 23 to 25 |  |  | 1548696.58 | 638417 | 2355255
|  |  | 55000000 | 60948375.74 | 11073065 | 5124689 | 5948376
| As per Admn. Sanction |  |  | 55000000 | Excess | 11073065
| As per Work done |  |  | 60948375.74 | Less | 5124689
| Difference |  |  | 5948375.74 | Difference | 5948376

## SEIGNORAGE
S.No | Item Name | UOM | QTY | QTY |  |  | Co-efficients |  |  | Rates |  |  | Amount |  |  | Total Amount
|  |  |  | Sand (QTY) | Metal (QTY) | Brick (QTY) | Sand | Metal | Bricks | Sand Rate | Metal Rate | Brick Rate | Sand Amount | Metal Amount | Brick Amount
252 | Brick masonry for panel walls in superstructure with CM 1:8 prop: Aerated Cellular Autoclaved Concrete Blocks conforming to IS:2185 Part-3 - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600 x 200 x 200 mm including cost and conveyance of all materials like cement, screened sand, bricks, water etc., to site, including sales and other taxes on all materials and such as labour charges, like mixing cement mortar, scaffolding charges, constructing masonry, lift charges, curing, etc.,complete for finished item of work. TSSS No.501 and 504. 3rd Floor at MGMH Petlaburj | 20.08 | Cum | 3.522 |  | 1425 | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 61.9872 | 0 | 43.776 | 106
253 | Reinforced Masonry for partition walls 100 mm thick in CM 1:4 prop. Aerated Cellular Autoclaved Concrete Blocks conforming to IS:2185 Part-3- 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600 x 200 x 100 mm and placing 2Nos. of 6mm M.S plain rods in every third layer with free ends of the reinforcement pegged into mortar joints of main brick walls where applicable including cost and conveyance of all materials like cement, steel, sans, brick, water etc., to site, including sales and other taxes excluding GST on all materials, all operational, incidents charges, constructing masonry, lift charges, curing, complete for finished item of work. TSSS No. of 509. 3rd Floor at MGMH Petlaburj | 227.17 | Sqm | 3.586 |  | 1612 | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 63.1136 | 0 | 49.5206 | 113
254 | Providing Mild steel MS steel bars Fe 250 grade as per IS 432 of different diameters including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying including sales and other taxes on all materials etc. , complete for finished item of work. TSSS No.126 For RBM walls 6mm dia: 3rd Floor at MGMH Petlaburj | 0 | MT |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
255 | Plastering 20mm thick in two coats using screened sand with base coat of 16mm thick in CM1:6 and top coat of 4mm thick in CM1:4 with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales and other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., complete for finished item of work .SS 901,903and 904 3rd Floor at MGMH Petlaburj | 39.56 | Sqm | 0.889 |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 15.6464 | 0 | 0 | 16
256 | Plastering 12mm thick in two coats using screened sand with base coat of 8mm thick in CM 1:6 and top coat of 4mm thick in CM 1:4 with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales and other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and complete for finished item of work. SS 901,903 and 904. 3rd Floor at MGMH Petlaburj | 905.88 | Sqm | 12.117 |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 213.2592 | 0 | 0 | 213
257 | Providing and laying screed plain cement concrete as per site condition for floor bedding using high quality aggregates including base preparation, compaction, levelling, all lead and lifts, rough finishing at the top surface, curing, shuttering if necessary etc., complete as directed . at MGMH Petlaburj | 0 | Sqm |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
[15 empty] | Total | 448
[5 empty] | Brick Masonary |  | Partition walls |  | Plastering 20 mm |  | Plastering 12 mm
[5 empty] | Proportion | 1:08 |  | 227.17 | QTY | 39.56 | Qty | 905.88
[5 empty] | QTY | 20.08 | QTY | 22.717 |  | 0.63296 |  | 7.247
[5 empty] | V of 1 brick | 0.014091 | Ratio | 1:04 | dry v | 0.84184 | dry v | 9.6386
[5 empty] | no of bricks | 1425.0231 | V of 1 brick | 0.014091 | Ratio | 1:06 | Ratio | 1:06
[5 empty] | v of 1 brick | 0.012 | no of bricks | 1612.1638 | cement | 0.12026 | cement | 1.3769
[5 empty] | qty | 17.1003 | v of 1 brick | 0.012 | sand | 0.72157 | sand | 8.2616
[5 empty] | mortor qty | 2.9797 | qty | 19.346 | Ratio | 1:04 | Ratio | 1:04
[5 empty] | dry v | 3.963 | mortor qty | 3.371 |  | 0.15824 |  | 3.6235
[5 empty] | Cement | 0.44034 | dry v | 4.4835 | dry v | 0.21046 | dry v | 4.8193
[5 empty] | Sand | 3.5227 | Cement | 0.8967 | cement | 0.042092 | cement | 0.96386
[7 empty] | Sand | 3.5868 | sand | 0.16837 | sand | 3.8554
[9 empty] | T sand qty | 0.88994 | T sand qty | 12.1171

## Civil Data
CIVIL DATAS (2022-23 SSR)
42 | Providing Thermo Mechanically Treated (TMT) (Fe -500/500D/550D from Primary producer TATA, SAIL, VSP, JSW &Shyam Steel, Goel Steel, Jindal Panther, X-Vega & Balaji Shakthi as per IS 1786-2008) of different diameters for RCC works , including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying including sales and other taxes on all materials etc. ,and overheads & contractors profit complete for finished item of work.( APSS No.126)
(BLD-CSTN-4.2)& Amendment in SoR 2011-12 page No. 392
Unit - 1 MT
Material
| TMT bars including 5% for overlaps and wastage | 1.05 | MT | 60000 | 1 | MT | 63000
| Binding wire | 6 | Kgs | 71 | 1 | Kgs | 426
Labour for cutting , bending , shifting to site , tying and placing in position
| 1st class Blacksmith / Barbender | 3 | Nos. | 685 | 1 | Each | 2055
| 2nd class Blacksmith / Barbender | 7 | Nos. | 575 | 1 | Each | 4025
| Mazdoor(Unskilled) | 10 | Nos. | 520 | 1 | Each | 5200
| Add for MA @ 40% | 0.4 |  | 11280 |  |  | 4512
79218
| Rate for other Floors | FF (G.F) | SF | TF | 4 F | 5 F | 6 F
| Rate as worked out above | 79218 | 79218 | 79218 | 79218 | 79218 | 79218
| Lift charges ( Page 131 of Std. Data ) | 0 | 1128 | 2256 | 3384 | 4512 | 5640
| Add for MA @ 40% | 0 | 451.2 | 902.4 | 1353.6 | 1804.8 | 2256
| Rate per 1 MT | 79218 | 80797.2 | 82376.4 | 83955.6 | 85534.8 | 87114
| Overheads & Contractors Profit @ 13.615% | 10785.53 | 11000.54 | 11215.55 | 11430.55 | 11645.56 | 11860.57
| Rate per 1 MT | 90003.53 | 91797.74 | 93591.95 | 95386.15 | 97180.36 | 98974.57
| Or Say | 90004 | 91798 | 93592 | 95386 | 97180 | 98975
44 | Supplying and fixing of to windows / in open court yards using 25mm x 6mm MS flat alround and 10mm MS square bars horizontally at 125mm centre to centre and vertically at 300mm centre to centre including fixing with 4 Nos of MS Z holdfasts (2 on each side) duly making cutting brick masonry, fixing and making to original surface neatly and painting grill with one coat of red oxide primer including cost all taxes and conveyance of all materials including cutting, bending, welding including all operational charges and all labour charges etc., complete for finished item of work.
| For1.80mx1.80m size | 3.24 | Sqm
Quantity Anailysis
| Cost of 25mm x 6mm MS flat alround | 2 ( 1.80+ 1.80 ) |  |  |  | 7.2 | RM
|  | 7.20 RM @ 1.80 Kgs/RM |  |  |  | 12.96 | Kgs
Cost of 10mm M.S square bars @0.785 kg /RM
| Vertical bars | 6 x 1.80 |  | 10.8
| Horizontal bars | 16 x 1.80 |  | 28.8
|  |  |  | 39.6 | RM | 31.086 | Kgs
[6 empty] | 44.046 | Kgs
Cost Analysis
| Cost of 10mm MS squre bars (RMR) | 31.086 | Kgs | 61000 | 1000 | Kgs | 1896.246
| Cost of 25X 6mm MS Flat (RMR) | 12.96 | Kgs | 62000 | 1000 | Kgs | 803.52
| Cost of MS Z hold fasts | 4 | Nos. | 37 |  | Each | 148
| Labour charges for fabrication of steel TBSC-T.I-16 | 44.046 | Kgs | 37 | 1 | Kg | 1629.702
| Labour charges for fixing TBSC-T.I-17 | 44.046 |  | 6 |  |  | 264.276
| Add for MA @ 40% | 0.4 |  | 916.1568 |  |  | 366.4627
| Rate per 3.24 Sqm | [5 empty] | 5108.2067
1576.607
| Overheads & Contractors Profit @ 13.615% | 0.13615 |  | 1576.607 |  |  | 214.655
1791.2621
| Rate per 1 Sqm |  |  |  | Or Say |  | 1791
45 | Supply and placing of the Design Mix Concrete M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Weight Batcher / Concrete mixer with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials, centering using Casurina Ballies, Bamboos, Wooden Reapers, Runners, Wood Posts, Steel Plates etc., including all operational, incidental and labour charges such as weigh batching, machine mixing, lifting of concrete manually, laying concrete, curing , overheads & contractors profit etc., complete but excluding cost of steel and its fabrication charges for finished item of work (APSS No. 402)
(BLD-CSTN-3-15)
COLUMNS, LINTELS, WATER TANKS, RCC WALL IN BUILDINGS:
A.MATERIALS :
| Cement | 380 | Kgs | 5200 | 1000 | Kgs | 1976
| 20mm HBG graded metal | 0.8 | Cum | 1447.96 | 1 | Cum | 1158.368
| Sand | 0.4 | Cum | 2253.91 | 1 | Cum | 901.564
B.LABOUR :
| 1st class Mason | 0.167 | Nos | 580 | 1 | Each | 96.86
| 2nd class Mason | 0.167 | Nos | 550 | 1 | Each | 91.85
| Mazdoor (both men&women) | 5.6 | Nos | 520 | 1 | Each | 2912
| Add for MA @ 40% | 0.4 |  | 3100.71 |  |  | 1240.284
C.MACHINERY :
| Concrete Mixer 10 / 7 cft (0.2 / 0.8 cum)capacity | 1.333 | hours | 192.9 | 1 | hour | 257.1357
| Crew charges | 1.333 | hours | 302.9 | 1 | hour | 403.7657
| Needle vibrator 40mm ( petrol ) | 1.333 | hours | 36.5 | 1 | hour | 48.6545
| Crew charges | 1.333 | hours | 218 | 1 | hour | 290.594
| Add MA on crew charges | 0.4 |  | 694.3597 |  |  | 277.7439
| Water(including for curing) | 1.2 | kl | 108 | 1 | kl | 129.6
| Rate per 1 cum | [5 empty] | 9784.4198
| LINTELS : | FF (G.F) | SF | TF | 4F | 5F | 6F
Lifting by Manual means
Rate for other Floors
| Rate as above | 9784.4198 | 9784.4198 | 9784.4198 | 9784.4198 | 9784.4198 | 9784.4198
| Hire charges of centering and scaffolding | 886 | 886 | 886 | 886 | 886 | 886
| Labour charges | 1489 | 1638 | 1787 | 1936 | 2085 | 2234
| Add for MA @ 40% | 595.6 | 655.2 | 714.8 | 774.4 | 834 | 893.6
| Lift charges of materials (Manual) | 0 | 310.071 | 620.142 | 930.213 | 1240.284 | 1550.355
| Add for MA @ 40% | 0 | 124.03 | 248.06 | 372.09 | 496.11 | 620.14
| Rate per 1 cum | 12755.0198 | 13397.7208 | 14040.4218 | 14683.1228 | 15325.8138 | 15968.5148
| Overheads & Contractors Profit @ 13.615% | 0 | 0 | 0 | 0 | 0 | 0
| Rate per 1 cum | 12755.0198 | 13397.7208 | 14040.4218 | 14683.1228 | 15325.8138 | 15968.5148
| Or Say | 12755 | 13398 | 14040 | 14683 | 15326 | 15969
46 | Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707)
(BLD-CSTN-9-20)
Unit = 10 sqm
| Cost of vitrified tiles 8-10mm thick | 10.5 | sqm | 578 | 1 | sqm | 6069
| Sand for CM(1:5) base coat | 0.12 | cum | 2453.91 | 1 | cum | 294.4692
| Cement for CM(1:5) base coat | 34.56 | Kgs | 5200 | 1000 | Kgs | 179.712
| Cement for slurry | 33 | Kgs | 5200 | 1000 | Kgs | 171.6
| White cement for jointing & pointing | 2 | Kgs | 34 | 1 | Kg | 68
B.LABOUR
| Mason 1st class | 0.96 | Nos. | 580 | 1 | Each | 556.8
| Mason 2nd class | 2.24 | Nos. | 550 | 1 | Each | 1232
| Mazdoor(unskilled) | 3.3 | Nos. | 520 | 1 | Each | 1716
| Add for MA @ 40% | 0.4 |  | 3504.8 |  |  | 1401.92
| Add water charges 1% | 0.01 |  | 11689.5012 |  |  | 116.895
| Rate for 10 sqm | [5 empty] | 11806.3962
| Rate for other Floors | FF (G.F) | SF | TF | 4 F | 5 F | 6 F
| Rate as worked out above | 11806.3962 | 11806.3962 | 11806.3962 | 11806.3962 | 11806.3962 | 11806.3962
| Lift charges ( Page 131 of Std. Data ) | 0 | 350.48 | 700.96 | 1051.44 | 1401.92 | 1752.4
| Add for MA @ 40% | 0 | 140.192 | 280.384 | 420.576 | 560.768 | 700.96
|  | 11806.3962 | 12297.0682 | 12787.7402 | 13278.4122 | 13769.0842 | 14259.7562
| Overheads & Contractors Profit @ 13.615% | 1607.44 | 1674.25 | 1741.05 | 1807.86 | 1874.66 | 1941.47
| Rate per 10 Sqm | 13413.8362 | 13971.3182 | 14528.7902 | 15086.2722 | 15643.7442 | 16201.2262
| Rate per 1 RM | 134.1384 | 139.7132 | 145.2879 | 150.8627 | 156.4374 | 162.0123
| Or Say | 134 | 140 | 145 | 151 | 156 | 162
ELECTRICAL DATAS (2022-23 SSR)
61 | Supply and fixing of suitable out door feeder piller box of size made with 14 SWG CRCA sheet with double door arrangement, making powder coating after processing of 7 Tank process, lock and key, hinges, rubber gasket, danger board,suitable angle iron stand for mounting the feeder pillar with cement concrete, including Supply and fixing of Legrand / Schnieder make as out goings, indication lamps, din channel, 6 Sqmm 3 core copper cable for invidual light control, connectors,bus bars, shroudings, gland plates and provision for 3 phase energy meter etc., complete for finished item of work and suitable wirin provision for connecting the nature switch with following.63A, 4 Pole MCB as incomer, 9 Nos 6-32A SP MCBs
| Supply and fixing of suitable out door feeder piller box of size made with 14 SWG CRCA (ELEC-7.6.2) | 1 | No | 1 | No | 27081 | 27081
| Add Contractors Profit | 13.61% |  |  |  |  | 3687.0781
30768.0782
| Rate per 1 No. |  |  |  |  | Or Say | 30768

## Sheet1
Addresable Alarm Panel | 135280 | 291336
Track Light | 0 | 9600
Canvas Connections | 13000 | 13000
Titanium Letters | 48000 | 67500
Foam Boards & Vinyl Sticker | 6200 | 12000
2 Feet Deep Of Ceiling Top | 23040 | 28740
Double Flush Door | 44000 | 56500
Side panelling | 59840 | 75573
60mm Box Framing | 36000 | 51206
PVC Frames on DBs | 4800 | 4816
Name Plates | 4320 | 22800
Mirrors | 8700 | 8875
Dress Hangers | 2000 | 2550
Procedural Photos | 46500 | 117000
Sun Control film | 13300 | 18288
ivf logo | 0 | 11475
VRV & AC |  | 10000
56000
80000
43750
-54244
| 444980 | 926765
1787030
32805
919525 |  | 60000
82500
195000
45000
8400
9300
4200
16200
32000
29000
2100
29000
80000
210000
32000
867505

## GA
Name of the work: Design, fabrication, establishing & commissioning of In-Vitro Fertility Centers (IVFCs) along with allied services on Turnkey basis at MGMH Petlaburj, Hyd.
GENERAL ABSTRACT
S.No | Description | As per workdone
1 | Equipment | 26020475
2 | Civil Works | 7012631
3 | Plumbing works | 136973
4 | Electrical works | 5641335
5 | ELV works | 689000
6 | Fire Fighting works | 873880
7 | Air Conditioning works | 2725391
8 | MGPS works | 1141255
| Sub Total (Agreement Part-A) | 44240940
9 | Equipment supplimental | 221000
10 | Civil supplimental works | 1156237
11 | Plumbing supplimental works | 8985
12 | Electrical supplimental works | 496686
14 | Air Conditioning supplimental works | 1749744
15 | MGPS supplimental works | 814670
| Sub Total (Supplimental Part-B) | 4447322
| Total (Part-A+Part-B) | 48688262
16 | Provision towards Engineering Supervision Charges @ 4% on RE Value | 1947530
| GST @ 18% | 8763887.16
| Total | 59399679.16
17 | Labour Cess @ 1% on Basic Price of Revised Estimate | 486882.62
18 | NAC @ 0.1% on Basic Price of Revised estimate | 48688.262
19 | Provision towards Seniorage Charges on Civil Component | 448
20 | Provision towards DMF Charges 30% on Seniorage Charges | 134.4
21 | Provision towards SMFT Charges 2% on seniorage Charges | 8.96
22 | Provision towards Haritha Nidhi | 4868.8262
23 | Sub total of S.No 17 to 22 | 541031
24 | Provision towards GST 18% on Seniorage Charges | 97385.58
25 | Provision towards Unforseen items and rounding off (LS) - | 910280
| Sub total of S.No 23 to 25 | 1548697
| Grand Total | 60948376

## EQP_List
S.No | Item Code | Description | Qty | UOM
199 | IVF199 | Ovum Aspiration Pumps at Petlaburj Hospital | 2 | No
200 | IVF200 | IVF Test tube Warmers at Petlaburj Hospital | 2 | No
201 | IVF201 | DICOM compatible fully digital, compact, portable, Ultrasound Scan Machine Colour Doppler at Petlaburj Hospital | 2 | No
202 | IVF202 | Multipurpose Electro hydraulic with manual override mobile OT Table, with divided leg section suitable for all Gynaecological surgical procedures, complete with 5cm Mattress and corded handset at Petlaburj Hospital | 1 | No
203 | IVF203 | LED procedure Lights Double dome at Petlaburj Hospital | 1 | No
204 | IVF204 | LED procedure Lights Single dome at Petlaburj Hospital | 1 | No
205 | IVF205 | IVF Workstation with LAF at Petlaburj Hospital | 1 | No
206 | IVF206 | IVF Ant vibration Table for procedure at Petlaburj Hospital | 1 | No
207 | IVF207 | CO2 Incubators at Petlaburj Hospital | 2 | No
208 | IVF208 | Trigas bench Top Incubators for Human Embryo culture at Petlaburj Hospital | 1 | No
209 | IVF209 | Trinocular Stereozoom Microscope at Petlaburj Hospital | 1 | No
210 | IVF210 | ICSI Micro manipulator with Inverted Microscope at Petlaburj Hospital | 1 | No
211 | IVF211 | IVF Laser System at Petlaburj Hospital | 1 | No
212 | IVF212 | IVF Thermometer at Petlaburj Hospital | 1 | No
213 | IVF213 | CO2 Cylinder and Manifold at Petlaburj Hospital | 2 | No
214 | IVF214 | CO2 and O2 Analyzer at Petlaburj Hospital | 1 | No
215 | IVF215 | PH Meter at Petlaburj Hospital | 1 | No
216 | IVF216 | VOC Meter for ART Lab at Petlaburj Hospital | 1 | No
217 | IVF217 | Sperm Counting Makler Chamber at Petlaburj Hospital | 1 | No
218 | IVF218 | Binocular Microscope for Semen Analysis at Petlaburj Hospital | 1 | No
219 | IVF219 | Laminar flow cabinet with Andrology Work station at Petlaburj Hospital | 1 | No
220 | IVF220 | Clinical Centrifuge machine for Andrology at Petlaburj Hospital | 1 | No
221 | IVF221 | Dry Incubators at Petlaburj Hospital | 1 | No
222 | IVF222 | Pipetter and Denudation system at Petlaburj Hospital | 1 | No
223 | IVF223 | Pharmaceutical Refrigerator at Petlaburj Hospital | 1 | No
224 | IVF224 | Cryocans with wheels at Petlaburj Hospital | 2 | No
225 | IVF225 | Defibrillator at Petlaburj Hospital | 1 | No
226 | IVF226 | 7 Para Patient Monitor at Petlaburj Hospital | 2 | No
227 | IVF227 | Suction machine at Petlaburj Hospital | 1 | No
228 | IVF228 | Anaesthesia Work station at Petlaburj Hospital | 1 | No
229 | IVF229 | Autoclave at Petlaburj Hospital | 1 | No
230 | IVF230 | Operative Hysteroscopy and Resectoscope Set Machine at Petlaburj Hospital | 1 | No
231 | IVF231 | Operative Laparoscopy Set at Petlaburj Hospital | 1 | No
232 | IVF232 | Multifunctional Printer at Petlaburj Hospital | 1 | No
233 | IVF233 | Ultrasound Examination Couch at Petlaburj Hospital | 1 | No
234 | IVF234 | UPS 20KVA with battery backup at Petlaburj Hospital | 0 | No
235 | IVF235 | Laptop for Office usage at Petlaburj Hospital | 2 | No
236 | IVF236 | Reception Table at Petlaburj Hospital | 1 | No
237 | IVF237 | Reception chair at Petlaburj Hospital | 2 | No
238 | IVF238 | Filing Cabinet at Petlaburj Hospital | 2 | No
239 | IVF239 | Patient Seating 3 in 1 model at Petlaburj Hospital | 3 | No
240 | IVF240 | Consultant Chair at Petlaburj Hospital | 3 | No
241 | IVF241 | Patient Chair at Petlaburj Hospital | 6 | No
242 | IVF242 | Small Trolley at Petlaburj Hospital | 3 | No
243 | IVF243 | Big Trolley at Petlaburj Hospital | 3 | No
244 | IVF244 | Wall Storage Cabinets at Petlaburj Hospital | 8 | No
245 | IVF245 | Office Table at Petlaburj Hospital | 3 | No
1 |  | 3-Bay Surgical Scrub Station/Sink to be provided for use in the OT complex providing for pre-procedural scrub up with minimum three bay sink combination as suitable. The Scrub Station shall be made of Stainless Steel of 304 grade sheet with minimum thickness of 1.5mm and designed as per the high aesthetics of the theatre complex. Shall have smoothened surfaces & corners. The scrub sink shall be provided with a front access panel which shall be easily removed for access to the water-controlled valve, waste connections, stoppers & strainers. The Scrub station should be equipped with two foot operated and one elbow operated mechanisms. Shall have provision for fresh water and waste water piping ready for connections. | 1 | Nos
2 |  | Supply and installation of Stainless Steel 304 grade CSSD Rectangular Working table of size 1200 x 480 x 1050 mm with inbuilt sink of size 450 x 380 x 300 mm equipped with jali at bottom to stop any large particles entering into the drain to avoid drain clog. The table to be designed with raised front section and provision of SS sheet at foot level of the table forming a flat surface for storing/placing of items. The table to be of ready to use with all necessary fittings. | 1 | Nos
3 |  | SS-304 working table of size 685 x 685 x 762 mm with I type support inner frame SS-304 pipe of size 40 x 40 x 1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. | 2 | Nos
4 |  | SS-304 working table of size 457 x 457 x 762 mm with I type support inner frame SS-304 pipe of size 40 x 40 x 1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. | 1 | Nos
5 |  | SS-304 working table of size 61 x 610 x 762 mm with I type support inner frame SS-304 pipe of size 40 x 40 x 1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. | 1 | Nos
6 |  | SS-304 working table of size 660 x 610 x 762 mm with I type support inner frame SS-304 pipe of size 40 x 40 x 1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. | 1 | Nos