## New_Abstract
Name of the work: Design, fabrication, establishing & commissioning of In-Vitro Fertility Centers (IVFCs) along with allied services on Turnkey basis at MGM Hospital, Warangal.
COMPARATIVE STATEMENT
S.No | Description |  | As per Agreement | As per workdone | Excess | Less | Net Difference
PART-A
1 | Equipment |  | 26020476 | 26020476 | 0 | 0 | Details on Pg No.3 of RE
2 | Civil Works |  | 7320696 | 9771662 | 3717655 | 1266689 | Details on Pg No.14 of RE
3 | Plumbing works |  | 160285 | 156101 | 0 | 4184 | Details on Pg No.17 of RE
4 | Electrical works |  | 3832437 | 5402274 | 1817101 | 247264 | Details on Pg No.26 of RE
5 | ELV works |  | 1337000 | 1337000 | 0 | 0 | Details on Pg No.27 of RE
6 | Fire Fighting works |  | 225880 | 225880 | 0 | 0 | Details on Pg No.28 of RE
7 | Air Conditioning works |  | 3888485 | 4247076 | 428591 | 70000 | Details on Pg No.35 of RE
8 | MGPS works |  | 1025822 | 1046572 | 20750 | 0 | Details on Pg No.37 of RE
9 | Sub Total (Agreement Part-A) (1 to 8) |  | 43811081 | 48207041 | 5984097 | 1588137 | 4395960
10 | PART-B
11 | Equipment supplimental |  | 0 | 317600 | 317600 | 0 | Details on Pg No.39 of RE
12 | Civil supplimental works |  | 0 | 920706 | 920706 | 0 | Details on Pg No.43 of RE
13 | Plumbing supplimental works |  | 0 | 8985 | 8985 | 0 | Details on Pg No.44 of RE
14 | Electrical supplimental works |  | 0 | 486635 | 486635 | 0 | Details on Pg No.46 of RE
15 | Fire Fighting Supplimental works |  | 0 | 291366 | 291366 | 0 | Details on Pg No.47 of RE
16 | Air Conditioning supplimental works |  | 0 | 65250 | 65250 | 0 | Details on Pg No.47 of RE
17 | MGPS supplimental works |  | 0 | 814670 | 814670 | 0 | Details on Pg No.50 of RE
18 | Water Proofing Works |  | 0 | 1500000 | 1500000 | 0 | Details on Pg No.50 of RE
19 | Sub Total (Supplimental Part-B) (11 to 18) |  | 0 | 4405212 | 4405212 | 0
20 | Basic Total (Part-A+Part-B) (19+9) |  | 43811081 | 52612253 | 10389309 | 1588137 | 8801172
21 | Provision towards Engineering Supervision Charges @ 4% on RE Value (on 20) | 4% | 1752443 | 2104490 | 352047 | 0
22 | GST @ 18% (on 20) |  | 7885994.58 | 9470205.54 | 1584211 | 0
23 | Total (Part-A+Part-B) (18 to 20) |  | 53449519 | 64186949 | 12325567 | 1588137 | 10737430
24 | TGMSIDC Mandatory Charges
25 | Labour Cess @ 1% on Basic Price of Revised Estimate (on 20) | 1% |  | 526123 | 526123 | 0
26 | NAC @ 0.1% on Basic Price of Revised estimate (on 20) | 0.1% |  | 52612 | 52612 | 0
27 | Provision towards Seniorage Charges on Civil Component |  |  | 1001 | 1001 | 0
28 | Provision towards DMF Charges 30% on Seniorage Charges (on 27) | 30% |  | 300 | 300 | 0
29 | Provision towards SMFT Charges 2% on seniorage Charges (On 27) | 2% |  | 20 | 20 | 0
30 | Provision towards Haritha Nidhi (on 20) | 0.01% |  | 5261 | 5261 | 0
31 | Sub total of S.No (25 to 30) |  | 0 | 585317 | 585317 | 0
32 | Provision towards GST 18% on Above Charges (on 31) | 18% |  | 105357.06 | 105357 | 0
33 | Provision towards Unforseen items and rounding off (LS) - |  | 1550481 | 0 | 0 | 1550481
34 | Sub total of S.No (31 to 33) |  | 1550481 | 690674.06 | 690674 | 1550481
35 | Total (34+23) |  | 55000000 | 64877623.06 | 13016241 | 3138618 | 9877623
36 | PART-C
37 | Interior Works As Per IVF Petlaburj |  | 0 | 406531 | 406531 | 0 | Details on Part-C Pg No.1
38 | GST @ 18% on 37 |  | 0 | 73176 | 73176 | 0
39 | Total (37 to 38) |  | 0 | 479707 | 479707 | 0
40 | TGMSIDC Mandatory Charges
41 | Labour Cess @ 1% on Part-C (S.No 37) | 1% |  | 4065 | 4065 | 0
42 | NAC @ 0.1% on Part-C (S.No 37) | 0.1% |  | 407 | 407 | 0
43 | Provision towards Haritha Nidhi on Part-C (S.No 37) | 0.01% |  | 41 | 41 | 0
44 | Provision towards Engineering Supervision Charges @ 4% on Part-C (S.No 37) | 4% |  | 16261 | 16261 | 0
45 | Sub Total (41 to 44) |  | 0 | 20774 | 20774 | 0
46 | Provision towards GST 18% on Above Charges (on 45) |  | 0 | 3739 | 3739 | 0
47 | Sub Total (45 to 46) |  | 0 | 24513 | 24513 | 0
48 | Total (PART-C) (47+39) |  | 0 | 504220 | 504220 | 0
49 | Total (Part-A+B+C) (48+35) |  | 55000000 | 65381843.06 | 13520461 | 3138618 | 10381843
50 | PART-D
51 | Equipment |  |  | 549100 | 549100 | 0 | Details on Part-D Pg No.1
52 | Furniture |  |  | 121385 | 121385 | 0 | Details on Part-D Pg No.1
53 | Basic Sub Total (51 to 52) |  | 0 | 670485 | 670485 | 0
54 | GST @ 18% on 53 |  | 0 | 120687 | 120687 | 0
55 | Total (53 to 54) |  | 0 | 791172 | 791172 | 0 | 791172
56 | TGMSIDC Mandatory Charges
57 | Labour Cess @ 1% on Part-D (S.No 53) | 1% |  | 6705 | 6705 | 0
58 | NAC @ 0.1% on Part-D (S.No 53) | 0.1% |  | 670 | 670 | 0
59 | Provision towards Haritha Nidhi Part-D (S.No 53) | 0.01% |  | 67 | 67 | 0
60 | Provision towards Engineering Supervision Charges @ 4% on Part-D (S.No 53) | 4% |  | 26819 | 26819 | 0
61 | Sub Total (57 to 60) |  | 0 | 34261 | 34261 | 0
62 | Provision towards GST 18% on Above Charges (on 61) |  | 0 | 6167 | 6167 | 0
63 | Sub Total (61 to 62) |  | 0 | 40428 | 40428 | 0
64 | Total (PART-D) (63+55) |  | 0 | 831600 | 831600 | 0 | 831600
65 | Total (PART-A+B+C+D) (64+49) |  | 55000000 | 66213443.06 | 14352061 | 3138618 | 11213443
66 | PART-E
67 | Additional Items As Per End User Letter |  |  | 525900 | 525900 | 0 | Details on Part-E Pg No.1
68 | GST @ 18% on 67 |  |  | 94662 | 94662 | 0
69 | Sub Total (67 to 68) |  | 0 | 620562 | 620562 | 0
70 | TGMSIDC Mandatory Charges
71 | Labour Cess @ 1% on Part-E (S.No 67) | 1% |  | 5259 | 5259 | 0
72 | NAC @ 0.1% on Part-E (S.No 67) | 0.1% |  | 526 | 526 | 0
73 | Provision towards Haritha Nidhi on Part-E (S.No 67) | 0.01% |  | 53 | 53 | 0
74 | Provision towards Engineering Supervision Charges @ 4% on Part-E (S.No 67) | 4% |  | 21036 | 21036 | 0
75 | Sub Total (71 to 74) |  | 0 | 26874 | 26874 | 0
76 | Provision towards GST 18% on Above Charges (on 75) |  | 0 | 4837 | 4837 | 0
77 | Sub Total (75 to 76) |  | 0 | 31711 | 31711 | 0
78 | Total (PART-E) (77+69) |  | 0 | 652273 | 652273 | 0 | 652273
79 | Total (PART-A+B+C+D+E) (78+65) |  | 55000000 | 66865716.06 | 15004334 | 3138618 | 11865716
80 | Provision towards (LS) - Inaugration Expenses |  |  | 300000 | 300000
| Grand Total (79 to 80) |  | 55000000 | 67165716.06 | 15304334 | 3138618 | 12165716
|  |  | As per Admn. Sanction | 55000000 | Excess | 15304334
|  |  | As per Work done | 67165716.06 | Less | 3138618
|  |  | Difference | 12165716.06 | Difference | 12165716

## RE
REVISED ESTIMATE - MGM Hospital Warangal
S.No | Description | As Per Sanctioned Estimate |  |  |  | As Per Working Estimate |  |  |  | Excess | Less | Remarks
|  | QTY | UOM | RATE (Rs.) | AMOUNT (Rs.) | QTY | UOM | RATE (Rs.) | AMOUNT (Rs.)
MGM Hospital, Warangal
| EQUIPMENT | [14 empty] | As per agreement | As per workdone | excess | less
396 | Ovum Aspiration Pumps at MGM Hospital | 2 | No | 240000 | 480000 | 2 | No | 240000 | 480000 | 0 | 0 |  | EQP |  | EQP | 26020476 | 26020476 | 0 | 0
[13 empty] | EQP |  | C | 7320696 | 9771662 | 3717655 | 1266689
397 | IVF Test tube Warmers at MGM Hospital | 2 | No | 49500 | 99000 | 2 | No | 49500 | 99000 | 0 | 0 |  | EQP |  | P | 160285 | 156101 | 0 | 4184
[13 empty] | EQP |  | E | 3832437 | 5402274 | 1817101 | 247264
398 | DICOM compatible fully digital, compact, portable, Ultrasound Scan Machine Colour Doppler at MGM Hospital | 2 | No | 1365000 | 2730000 | 2 | No | 1365000 | 2730000 | 0 | 0 |  | EQP |  | ELV | 1337000 | 1337000 | 0 | 0
[13 empty] | EQP |  | FF | 225880 | 225880 | 0 | 0
399 | Multipurpose Electro hydraulic with manual override mobile OT Table, with divided leg section suitable for all Gynaecological surgical procedures, complete with 5cm Mattress and corded handset at MGM Hospital | 1 | No | 563750 | 563750 | 1 | No | 563750 | 563750 | 0 | 0 |  | EQP |  | AC | 3888485 | 4247076 | 428591 | 70000
[13 empty] | EQP |  | G | 1025822 | 1046572 | 20750 | 0
400 | LED procedure Lights Double dome at MGM Hospital | 1 | No | 312500 | 312500 | 1 | No | 312500 | 312500 | 0 | 0 |  | EQP |  | EQPS | 0 | 317600 | 317600 | 0
[13 empty] | EQP |  | CS | 0 | 920706 | 920706 | 0
401 | LED procedure Lights Single dome at MGM Hospital | 1 | No | 187500 | 187500 | 1 | No | 187500 | 187500 | 0 | 0 |  | EQP |  | PS | 0 | 8985 | 8985 | 0
[13 empty] | EQP |  | ES | 0 | 486635 | 486635 | 0
402 | IVF Workstation with LAF at MGM Hospital | 1 | No | 687500 | 687500 | 1 | No | 687500 | 687500 | 0 | 0 |  | EQP |  | FFS | 0 | 291366 | 291366 | 0
[13 empty] | EQP |  | ACS | 0 | 65250 | 65250 | 0
403 | IVF Ant vibration Table for procedure at MGM Hospital | 1 | No | 96250 | 96250 | 1 | No | 96250 | 96250 | 0 | 0 |  | EQP |  | GS | 0 | 814670 | 814670 | 0
[13 empty] | EQP |  | WP | 0 | 1500000 | 1500000 | 0
404 | CO2 Incubators at MGM Hospital | 2 | No | 825000 | 1650000 | 2 | No | 825000 | 1650000 | 0 | 0 |  | EQP |  |  | 43811081 | 52612253 | 10389309 | 1588137
EQP
405 | Trigas bench Top Incubators for Human Embryo culture at MGM Hospital | 1 | No | 825000 | 825000 | 1 | No | 825000 | 825000 | 0 | 0 |  | EQP |  |  |  | 8801172 | TRUE | 8801172
EQP
406 | Trinocular Stereozoom Microscope at MGM Hospital | 1 | No | 309000 | 309000 | 1 | No | 309000 | 309000 | 0 | 0 |  | EQP
EQP
407 | ICSI Micro manipulator with Inverted Microscope at MGM Hospital | 1 | No | 2625000 | 2625000 | 1 | No | 2625000 | 2625000 | 0 | 0 |  | EQP
EQP
408 | IVF Laser System at MGM Hospital | 1 | No | 2560000 | 2560000 | 1 | No | 2560000 | 2560000 | 0 | 0 |  | EQP
EQP
409 | IVF Thermometer at MGM Hospital | 1 | No | 61875 | 61875 | 1 | No | 61875 | 61875 | 0 | 0 |  | EQP
EQP
410 | CO2 Cylinder and Manifold at MGM Hospital | 2 | No | 50000 | 100000 | 2 | No | 50000 | 100000 | 0 | 0 |  | EQP
EQP
411 | CO2 and O2 Analyzer at MGM Hospital | 1 | No | 378000 | 378000 | 1 | No | 378000 | 378000 | 0 | 0 |  | EQP
EQP
412 | PH Meter at MGM Hospital | 1 | No | 93750 | 93750 | 1 | No | 93750 | 93750 | 0 | 0 |  | EQP
EQP
413 | VOC Meter for ART Lab at MGM Hospital | 1 | No | 731250 | 731250 | 1 | No | 731250 | 731250 | 0 | 0 |  | EQP
EQP
414 | Sperm Counting Makler Chamber at MGM Hospital | 1 | No | 75625 | 75625 | 1 | No | 75625 | 75625 | 0 | 0 |  | EQP
EQP
415 | Binocular Microscope for Semen Analysis at MGM Hospital | 1 | No | 41250 | 41250 | 1 | No | 41250 | 41250 | 0 | 0 |  | EQP
EQP
416 | Laminar flow cabinet with Andrology Work station at MGM Hospital | 1 | No | 250000 | 250000 | 1 | No | 250000 | 250000 | 0 | 0 |  | EQP
EQP
417 | Clinical Centrifuge machine for Andrology at MGM Hospital | 1 | No | 34500 | 34500 | 1 | No | 34500 | 34500 | 0 | 0 |  | EQP
EQP
418 | Dry Incubators at MGM Hospital | 1 | No | 563750 | 563750 | 1 | No | 563750 | 563750 | 0 | 0 |  | EQP
EQP
419 | Pipetter and Denudation system at MGM Hospital | 1 | No | 103125 | 103125 | 1 | No | 103125 | 103125 | 0 | 0 |  | EQP
EQP
420 | Pharmaceutical Refrigerator at MGM Hospital | 1 | No | 225000 | 225000 | 1 | No | 225000 | 225000 | 0 | 0 |  | EQP
EQP
421 | Cryocans with wheels at MGM Hospital | 2 | No | 61875 | 123750 | 2 | No | 61875 | 123750 | 0 | 0 |  | EQP
EQP
422 | Defibrillator at MGM Hospital | 1 | No | 312500 | 312500 | 1 | No | 312500 | 312500 | 0 | 0 |  | EQP
EQP
423 | 7 Para Patient Monitor at MGM Hospital | 2 | No | 280000 | 560000 | 2 | No | 280000 | 560000 | 0 | 0 |  | EQP
EQP
424 | Suction machine at MGM Hospital | 1 | No | 49500 | 49500 | 1 | No | 49500 | 49500 | 0 | 0 |  | EQP
EQP
425 | Anaesthesia Work station at MGM Hospital | 1 | No | 937500 | 937500 | 1 | No | 937500 | 937500 | 0 | 0 |  | EQP
EQP
426 | Autoclave at MGM Hospital | 1 | No | 562500 | 562500 | 1 | No | 562500 | 562500 | 0 | 0 |  | EQP
EQP
427 | Operative Hysteroscopy and Resectoscope Set Machine at MGM Hospital | 1 | No | 2125000 | 2125000 | 1 | No | 2125000 | 2125000 | 0 | 0 |  | EQP
EQP
428 | Operative Laparoscopy Set at MGM Hospital | 1 | No | 4200000 | 4200000 | 1 | No | 4200000 | 4200000 | 0 | 0 |  | EQP
EQP
429 | Multifunctional Printer at MGM Hospital | 1 | No | 43750 | 43750 | 1 | No | 43750 | 43750 | 0 | 0 |  | EQP
EQP
430 | Ultrasound Examination Couch at MGM Hospital | 1 | No | 81250 | 81250 | 1 | No | 81250 | 81250 | 0 | 0 |  | EQP
EQP
431 | UPS 20KVA with battery backup at MGM Hospital | 1 | No | 1 | 1 | 1 | No | 1 | 1 | 0 | 0 |  | EQP
EQP
432 | Laptop for Office usage at MGM Hospital | 2 | No | 115000 | 230000 | 2 | No | 115000 | 230000 | 0 | 0 |  | EQP
EQP
433 | Reception Table at MGM Hospital | 1 | No | 110000 | 110000 | 1 | No | 110000 | 110000 | 0 | 0 |  | EQP
EQP
434 | Reception chair at MGM Hospital | 2 | No | 34500 | 69000 | 2 | No | 34500 | 69000 | 0 | 0 |  | EQP
EQP
435 | Filing Cabinet at MGM Hospital | 2 | No | 34500 | 69000 | 2 | No | 34500 | 69000 | 0 | 0 |  | EQP
EQP
436 | Patient Seating 3 in 1 model at MGM Hospital | 3 | No | 38500 | 115500 | 3 | No | 38500 | 115500 | 0 | 0 |  | EQP
EQP
437 | Consultant Chair at MGM Hospital | 3 | No | 20000 | 60000 | 3 | No | 20000 | 60000 | 0 | 0 |  | EQP
EQP
438 | Patient Chair at MGM Hospital | 6 | No | 13750 | 82500 | 6 | No | 13750 | 82500 | 0 | 0 |  | EQP
EQP
439 | Small Trolley at MGM Hospital | 3 | No | 39200 | 117600 | 3 | No | 39200 | 117600 | 0 | 0 |  | EQP
EQP
440 | Big Trolley at MGM Hospital | 3 | No | 62500 | 187500 | 3 | No | 62500 | 187500 | 0 | 0 |  | EQP
EQP
441 | Wall Storage Cabinets at MGM Hospital | 8 | No | 17500 | 140000 | 8 | No | 17500 | 140000 | 0 | 0 |  | EQP
EQP
442 | Office Table at MGM Hospital | 3 | No | 20000 | 60000 | 3 | No | 20000 | 60000 | 0 | 0 |  | EQP
EQP
443 | Consumables and Media for 100 Cycles at MGM Hospital | 1 | Lot |  | 0 | 1 | Lot | 0 | 0 | 0 | 0 |  | EQP
EQP
[5 empty] | 26020476 |  |  | PART-A | 26020476 | 0 | 0 | 0
|  |  |  | As Per Agreement | 26020476 |  |  | Excess | 0
|  |  |  | As Per Workdone | 26020476 |  |  | Less | 0
|  |  |  | Net Difference | 0 |  |  | Net Difference | 0
CIVIL WORKS
444 | Dismantling, clearing away and carefully stacking useful materials for re- use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges, etc., complete. Brick Masonry and Existing flooring at MGM Warangal | 80 | Cum | 398 | 31840 | 25.58 | Cum | 398 | 10181 | 0 | 21659 |  | C
C
445 | Dismantling clearing away and carefully stacking useful materials for re use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges etc complete for Flooring at MGM Warangal | 400 | Sqm | 20 | 8000 | 400 | Sqm | 20 | 8000 | 0 | 0 |  | C
| AE |  |  |  |  | 87.68 | Sqm | 20 | 1754 | 1754 | 0 |  | C
C
446 | Dismantling doors, windows and clear storey windows, Ventilators etc., wood or steel shutters including Chowkhats, architraves, hold fasts and other attachments etc., and stacking them within 100m lead including labour charge etc., and complete for finished item of work. Not exceeding 3 sqm in area: Doors 1.00x2.60M at MGM Warangal | 11 | No | 350 | 3850 | 0 | No | 350 | 0 | 0 | 3850 |  | C
C
447 | Dismantling doors, windows and clear storey windows, Ventilators etc., wood or steel shutters including Chowkhats, architraves, hold fasts and other attachments etc., and stacking them within 100m lead including labour charge etc., and complete for finished item of work. Exceeding 3 sqm in area : Doors1.50x2.60M at MGM Warangal | 2 | No | 468 | 936 | 2 | No | 468 | 936 | 0 | 0 |  | C
| AE |  |  |  |  | 35 | No | 468 | 16380 | 16380 | 0 |  | C
C
448 | Conveyance of un-useful excavated earth to a distance of 15 KM for disposal including hire charges of T and P, labour charges etc., complete for finished item of work. Dismantled Brick masonry and Existing flooring at MGM Warangal | 120 | Cum | 455 | 54600 | 120 | Cum | 455 | 54600 | 0 | 0 |  | C
| AE |  |  |  |  | 85 | Cum | 455 | 38675 | 38675 | 0 |  | C
C
449 | Brick masonry for panel walls in superstructure with CM 1:8 prop: Aerated Cellular Autoclaved Concrete Blocks conforming to IS:2185 Part-3 - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600 x 200 x 200 mm including cost and conveyance of all materials like cement, screened sand, bricks, water etc., to site, including sales and other taxes on all materials and such as labour charges, like mixing cement mortar, scaffolding charges, constructing masonry, lift charges, curing, etc.,complete for finished item of work. TSSS No.501 and 504. 2nd Floor at MGM Warangal | 15 | Cum | 16055 | 240825 | 15 | Cum | 16055 | 240825 | 0 | 0 |  | C
| AE |  |  |  |  | 62.69 | Cum | 16055 | 1006488 | 1006488 | 0 |  | C
C
450 | Reinforced Masonry for partition walls 100 mm thick in CM 1:4 prop. Aerated Cellular Autoclaved Concrete Blocks conforming to IS:2185 Part-3 - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600 x 200 x 100 mm and placing 2Nos. of 6mm M.S plain rods in every third layer with free ends of the reinforcement pegged into mortar joints of main brick walls where applicable including cost and conveyance of all materials like cement, steel, sans, brick, water etc., to site, including sales and other taxes excluding GST on all materials, all operational, incidents charges, constructing masonry, lift charges, curing, complete for finished item of work. TSSS No. of 509. 2nd Floor at MGM Warangal | 500 | Sqm | 1952 | 976000 | 324.93 | Sqm | 1952 | 634263 | 0 | 341737 |  | C
C
451 | Providing Mild steel MS steel bars Fe 250 grade as per IS 432 of different diameters including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying including sales and other taxes on all materials etc. , complete for finished item of work. TSSS No.126 For RBM walls 6mm dia: 2nd Floor at MGM Warangal | 2.25 | MT | 116500 | 262125 | 0 | MT | 116500 | 0 | 0 | 262125 |  | C
C
452 | Plastering 20mm thick in two coats using screened sand with base coat of 16mm thick in CM1:6 and top coat of 4mm thick in CM1:4 with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales and other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., complete for finished item of work SS 901,903and 904 2ND Floor at MGM Warangal | 45 | Sqm | 1077 | 48465 | 45 | Sqm | 1077 | 48465 | 0 | 0 |  | C
| AE |  |  |  |  | 137.18 | Sqm | 1077 | 147743 | 147743 | 0 |  | C
C
453 | Plastering 12mm thick in two coats using screened sand with base coat of 8mm thick in CM 1:6 and top coat of 4mm thick in CM 1:4 with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales and other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and complete for finished item of work. SS 901,903 and 904. 2ND Floor at MGM Warangal | 930 | Sqm | 1041 | 968130 | 930 | Sqm | 1041 | 968130 | 0 | 0 |  | C
| AE |  |  |  |  | 485.32 | Sqm | 1041 | 505218 | 505218 | 0 |  | C
C
454 | Supply and Installing change room Cubicles, at MGM Warangal GENERAL SPECIFICATIONS: Thickness of Compact Laminate: 12 mm Thick Colour of HPL Boards : In Single Colour, Size of Cubicle : As per DWG, Door Size for Normal Cubicle : As per DWG, Overall Height Of Cubicle : 2105 mm Including bottom gap of 100mm, Accessories: Manufacturers standard makes of Aluminium, SS Accessories. a Aluminium H Top Rail b SS Hinges c SS Privacy Thumb turn c/w Occupancy Indicator d SS Coat Hook e SS Door Knob f Aluminium U channel g Aluminium Door Stopper channel h Rubber Lining i SS Screws and PVC Wall Plugs | 18 | Sqm | 9055 | 162990 | 12 | Sqm | 9055 | 108660 | 0 | 54330 |  | C
C
455 | Providing and laying screed plain cement concrete as per site condition for floor bedding using high quality aggregates including base preparation, compaction, levelling, all lead and lifts, rough finishing at the top surface, curing, shuttering if necessary etc., complete as directed . at MGM Warangal | 20 | Sqm | 4700 | 94000 | 0 | Sqm | 4700 | 0 | 0 | 94000 |  | C
C
456 | Supply and fixing powder coated aluminium fully glazed swing door as per the approved drawing with fixed fan light of 500mm height at top door using aluminium sections of 101.60 mm x44.45mm , 3.18 mm thick for frame and door shutter made of styles , top and middle rail of 47.62mm x 44.45mm, 3.18 mm thick and bottom rail of 96.00mm x 44.45 mm,3.18mm thick, powder coating of alluminium sections 25mm microns thick, 5 mm thick plain glass fitted with suitable aluminium glazing clips and rubber beading in fan light portion, double shutters fitted with 5mm thick frosted glass in the top half and 12mm thick prelaminated particle board One side choice colour and other side balancing white lamination in the bottom half fitted with suitable aluminium glazing clips and rubber beading, as approved by Engineer-in-Charge including supply and fixing ISI marked powder coated aluminium fixtures of 2 Nos. tower bolts 10mm bolt IS:204 300mm long, 4 Nos. alluminium handles IS:208 150mm dia and 1 Nos. aldrops IS:2681 250mm, 1 No. door closure, Al. Butt hinges 125mm long 6Nos including labour charges for manufacturing door , fixing the door with required No. of screws etc., complete for finished item of work. The Aluminium section used shall be standard make confirming to IS 1948-1961 and as approved by the Engineer 1200mmx2100mm at MGM Warangal | 5 | Sqm | 13713 | 68565 | 0 | Sqm | 13713 | 0 | 0 | 68565 |  | C
[13 empty] | C |  | 10.92
457 | Supplying and fixing of Unplasticised Poly Vinyl Chloride UPVC 3 track sliding windows with mesh shutter – 2-glass shutters and 1-mesh shutter duly manufactured using UPVC reinforced profiles Composition of profile shall consists a minimum of 5.5 PHR of TiO2 and not more than 12 PHR of CaCo3 for every 100 parts of PVC resin of 94mm x 45 mm/80 mm x 52 mm x 2.20 mm for outer frames, 58 mm x 39 mm/54 mm x 38 mm x 2.20mm for sliding shutter frames capable of mounting single glazing system structurally reinforced with hot dip galvanized up to 50 microns of minimum thickness of 1.0/1.2 mm prefabricated and welded through fusion welding. The window sash shall be fitted with 5 mm thick clear float glass of reputed make and mesh shutter frame shall be 42 mm x 25mm/52 mm x 21.5 mm x 2.0 mm fitted with Vinyl Coated Fiber mesh- on rollers/ pulley duly fixed with Grey colour TPV Gasket for sash and Glazing bead shall be co- extruded with Grey colour soft PVC. System shall have single point locking with Touch Lock and the system is to be installed at the site using anchor fasteners, silicon rubber sealant, easy glazing/deglazing at site etc., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site includingetc., complete for finished item of work at MGM Warangal | 15 | Sqm | 9517 | 142755 | 15 | Sqm | 9517 | 142755 | 0 | 0 |  | C |  | 25.92
| AE |  |  |  |  | 11 | Sqm | 9517 | 104687 | 104687 | 0 |  | C
[13 empty] | C | 1.44
458 | Providing, supplying and fixing of Fixed Louvered Ventilator made out of multi chambered uPVC sections with Glazing bead shall be co-extruded with Grey colour soft PVC. having isolated drainage and reinforced with Galvanized Iron profiles throughout the window. The outer frame having an overall size of 60 mm x 55 mm x 2.40 with reinforcement of 1 mm thickness and Mullion with overall size of 74 mm x 60 mm x 2.40 mm with reinforcement of 1 mm thickness. Composition of profile shall consists a minimum of 5.5 PHR of TiO2 and not more than 12 PHR of CaCo3 for every 100 parts of PVC resin. Ventilator shall be provided with 4.5 mm Pin Head glass, standard hardware. Wall thickness of frame and Mullion shall be 2.4 mm., including cost and conveyance of all materials, accessories, labour charges for transportation, erection at site etc., complete for finished item of work hinges IS:205 150mm long, 1 No. aldrop IS:2681 300mm long, 1 No. tower bolt IS:204 of 200 mm x 10 mm dia at top, 2 Nos. 150 mm at MGM Warangal | 3.25 | Sqm | 8564 | 27833 | 1.44 | Sqm | 8564 | 12332 | 0 | 15501 |  | C
C
459 | Supply and fixing doors as per drawings with medium teak wood frame of section 100mm x 65 mm and ISI marked flush door shutters of 30 mm thick single shutter with bond wood solid block board type Core having cross bands and face veneers, hot pressed bonded with water proof phenol formaldehyde synthetic resin factory made conforming to IS 2202-1991 Part- I both sides commercial ply with internal lipping on all sides including cost and conveyance to site of teak wood frame, flush shutter including supply and fixing 6 Nos. MS Z hold fasts of size 300 mm x 40 mm x 5mm including cost of ISI marked Aluminium fixtures of 3 Nos. butt long handles IS:208, 1 No. door stopper and 1 No. rubber bush including fixing the fixtures to door with required number of screws, bolt and nuts including labour charges for fixing the frame in position, fixing the shutter to the frame etc., complete for finished item of work as per APSS 1001 and 1002 The vertical frame of door shall be embedded in flooring for a depth of not less than 10 mm 1000mm x 2100mm at MGM Warangal | 29.5 | Sqm | 5593 | 164994 | 0 | Sqm | 5593 | 0 | 0 | 164994 |  | C
C
460 | Supply and fixing doors as per drawings with medium teak wood frame of section 100mm x 65mm and ISI marked flush door shutter of 30mm thick single shutter with bond wood solid block board type Core having cross bands and face veneers, hot pressed bonded with water proof phenol formaldehyde synthetic resin factory made conforming to IS 2202-1991 Part- I both sides commercial ply with internal lipping on all sides including cost and conveyance to site of medium teak wood door frame, flush shutter, including supply and fixing 6 Nos. MS Z hold fasts of size 300mm x 40mm x 5mm including ISI marked Aluminium fixtures 3 Nos. butt hinges IS:205 of 150mm long, 1 No. aldrop IS:2681 250 mm long, 1 No. tower bolt IS:204 of 150 mm x 10mm dia, 2 Nos. 125mm long handles IS:208,1 No. rubber bush including supplying and fixing 1.20mm thick PVC sheet to full height of the shutter inside including labour charges for fixing the frame in position, fixing the shutter to the frame etc., complete for finished item of work as per APSS 1001 and 1002. The vertical frame of door shall be embedded in flooring for depth of not less than 10mm 750mm x 2100mm. at MGM Warangal | 6.3 | Sqm | 6510 | 41013 | 0 | Sqm | 6510 | 0 | 0 | 41013 |  | C
C
461 | Flooring with soluble salt porcelain vitrified tiles screen printed and polished of size 600 x 600 mm and thickness between 8 to 10mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630Parts 1 to 15 of any colour and finish in all shades and designs with borders and design as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM 1:8 prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread at the rate 3.3 kgs per Sqm. and jointed neatly with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site excluding cost of C.C. bed including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in- charge etc., and complete for finished item of work. APSS No.701 and 707. 2nd Floor at MGM Warangal | 265 | Sqm | 1725 | 457125 | 265 | Sqm | 1725 | 457125 | 0 | 0 |  | C
| AE |  |  |  |  | 223.6 | Sqm | 1725 | 385710 | 385710 | 0 |  | C
C
462 | Flooring with non-skid full body ceramic floor tiles of size 300mm x 300mm and thickness between 7 - 8mm 1st quality conforming to IS: 13711, IS: 13712, IS: 13630Part 1 to 15 of any colour and finish in all shades and designs as approved by Engineer-in-charge, set over base coat of cement mortar 1:8, 12mm thick using screened sand over CC bed already laid or RCC roof slab, including neat cement slurry of honey like consistency spread at the rate 3.3 Kgs per Sqm and jointed neatly with white cement paste to full depth mixed with pigment of matching shade, including cost of all materials like cement, screened sand , water and tiles etc., complete for finished item of work. TSSS No.701 and 707 at MGM Warangal | 12 | Sqm | 1525 | 18300 | 8.59 | Sqm | 1525 | 13100 | 0 | 5200 |  | C
C
463 | Providing and fixing in true horizontal level 14 mm - Mineral Fiber sheet 595 x 595 Square / Tegular Fissura fine model edge tiles with a Humidity Resistance of 90percentage RH, Average NRC 0.50, Light Reflectance greater than80percentage, Thermal Conductivity equal to 0.052 to 0.057 w/mk, Fire Performance Class 0/Class 1 using hot dipped Galvanized Steel section exposed surface with pre-coated capping, main Tee of size 24 x 32 mm at every 1200 mm c/c maximum and rotary stitched cross tee of size 24 x 27 mm at every 600 mm c/c and sub-cross tee of size 24 mm x 25 mm at 1200 mm c/c and wall angle of size 19 x 19 mm fixed to periphery of the wall and the above grid is suspended at every 1200 mm c/c in both directions using 2.0 mm thick pre-straightened GI Wire including cost and conveyance of all materials and labour charges such as cutting , fixing of standing of frame work exposing roof making etc., complete for finished item of work in 2nd floor. at MGM Warangal | 300 | Sqm | 1636 | 490800 | 300 | Sqm | 1636 | 490800 | 0 | 0 |  | C
| AE |  |  |  |  | 175 | Sqm | 1636 | 286300 | 286300 | 0 |  | C
C
464 | Providing dadooing to walls with glazed full body porcelain wall tiles of size 300 x 600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. 2nd Floor at MGM Warangal | 70 | Sqm | 1423 | 99610 | 70 | Sqm | 1423 | 99610 | 0 | 0 |  | C
| AE |  |  |  |  | 151.37 | Sqm | 1423 | 215400 | 215400 | 0 |  | C
465 | Providing and applying Wall putty of White Cement or Polymer or Cement based of average 1 to 2 mm thickness over plastered surface to prepare the surface even and smooth after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, applying emery paper, Sand the surface, clean and wipe off loose dust, applying knifing paste filler by putty knife / muslin pad, air dry for 2 - 3 hrs, sand with 180 and 320 No., emery paper for the surface preparation including cost and conveyance of all materials to work site and all operational, incidental, labour charges, over heads and etc., complete for finished item of work in 2nd floor Internal walls. at MGM Warangal | 800 | Sqm | 315 | 252000 | 800 | Sqm | 315 | 252000 | 0 | 0 |  | C
| AE |  |  |  |  | 1200 | Sqm | 315 | 378000 | 378000 | 0 |  | C
C
466 | Painting to new wood work and flush shutters with lappam finish, over a primary coat and painting two coats of synthetic enamel paint Grade-II VOC Volatile Organic Compound content less than 50 grams/litre of approved shade including cost and conveyance of all materials to site cost of primer coat and all labour charges etc. complete including applying sand paper on lappam coats for neat finish including sales and other taxes on cost of all materials etc., complete in all floors TSSS No.1200, 1207 and 1211. at MGM Warangal | 65 | Sqm | 281 | 18265 | 0 | Sqm | 281 | 0 | 0 | 18265 |  | C
C
467 | Supply and application of one coat water based cement primer of interior grade I and two coats of water based PU paint having anti bacterial applications content less than 50 grams/litre for internal walls including cost and conveyance of all materials to site, sales and other taxes, incidental, operational and all labour charges etc., and complete for finished item of work in 2nd floor. at MGM Warangal | 600 | Sqm | 260 | 156000 | 600 | Sqm | 260 | 156000 | 0 | 0 |  | C
| AE |  |  |  |  | 850 | Sqm | 260 | 221000 | 221000 | 0 |  | C
C
468 | Painting to old walls with 2 coats of water proof cement paint of shade as approved by the Engineer-In-Charge to give an even shade after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, including cost and conveyance of all materials to work site and all operational, scaffolding charges, incidental, labour charges etc., and overheads and contractors profit complete for finished item of work as per SS 912 in 2nd floor. at MGM Warangal | 300 | Sqm | 229 | 68700 | 300 | Sqm | 229 | 68700 | 0 | 0 |  | C
C
483 | Supply and installation of 80mm thick double skin modular wall Panels made of 0.8 mm thick powder coated GI on both the sides, with 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, flush on both sides with maximum allowable gap of 3- 4mm filled with food grade silicon sealant and placed on cold rolled galvanised bottom tracks with a recess to provide floor to wall coving flush with the wall panel. This includes all required harware for completion Panels to be covered with a protective film to avoid any damages during transportation and installation at MGM Warangal | 130 | sqm | 5620 | 730600 | 110 | sqm | 5620 | 618200 | 0 | 112400 |  | C
C
484 | Supply and installation of 50mm thick double skin ceiling system made of 0.8 mm thick Powder Coated GI sheets on both sides, 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, panels flush towards room side with maximum allowable gap of 3-4mm at panel to panel joints filled with silicon sealant. Ceiling panels are suspended from the RCC slab by using concealed AL ceiling grid with tie rod and adjustable turn buckle arrangement etc. This includes all required hardware for completion. Panels to be covered with a protective film to avoid any damages during transportation and installation at MGM Warangal | 65 | sqm | 5135 | 333775 | 55 | sqm | 5135 | 282425 | 0 | 51350 |  | C
C
485 | Double leaf clean room Doors : 46mm thick flush doors made of 0.8mm thick Powder coated GI sheets on both sides, 90 plus or minus 2 kg/m3 density Honeycomb with stand upto 220 Deg.C Temperature, and compressible strength upto 400 Kg/Sqm, 1.2 mm thick GPSP . door frames, double glazed vision panel with necessary adhesive tapes and silicon sealant, necessary hardware like SS304 ball bearing butt hinges, D- handles, push plates, Dorma make door closure, concealed tower bolt, drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms, Both side lock and keys etc. complete. Size 1500 X 2100 mm with 300mm X 300mm double glazed view panels at MGM Warangal | 5 | No | 46000 | 230000 | 5 | No | 46000 | 230000 | 0 | 0 |  | C
| AE |  |  |  |  | 2 | No | 46000 | 92000 | 92000 | 0 |  | C
C
486 | Single leaf clean room Doors : 46mm thick flush doors made of 0.8mm thick Powder coated GI sheets on both sides, 90 plus or minus 2 kg/m3 density Honeycomb with stand upto 220 Deg.C Temperature, and compressible strength upto 400 Kg/Sqm, 1.2 mm thick GPSP . door frames, double glazed vision panel with necessary adhesive tapes and silicon sealant, necessary hardware like SS304 ball bearing butt hinges, D- handles, push plates, Dorma make door closure, concealed tower bolt, drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms, Both side lock and keys etc. complete. Size 900 X 2100 mm with 300 mm x 300 mm View panel at MGM Warangal | 1 | No | 28700 | 28700 | 1 | No | 28700 | 28700 | 0 | 0 |  | C
| AE |  |  |  |  | 4 | No | 28700 | 114800 | 114800 | 0 |  | C
C
487 | Emergency Fire Doors : 46mm thick flush doors made of 0.8mm thick Powder coated GI sheets on both sides, 90 plus or minus 2 kg/m3 density Honeycomb with stand upto 220 Deg.C Temperature, and compressible strength upto 400 Kg/Sqm, 1.2 mm thick GPSP . door frames, double glazed vision panel with necessary adhesive tapes and silicon sealant, necessary hardware like SS304 ball bearing butt hinges, D- handles, push plates, Dorma make door closure, concealed tower bolt, drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms, Both side lock and keys etc. complete. Size 1500 X 2100 mm with 2 hours fire rated and panic push bar and accessories etc. at MGM Warangal | 1 | No | 55000 | 55000 | 1 | No | 55000 | 55000 | 0 | 0 |  | C
C
488 | Supply and installation of Extruded Aluminium Coving at MGM Warangal | 100 | Rmt | 585 | 58500 | 80 | Rmt | 585 | 46800 | 0 | 11700 |  | C
C
489 | Providing, laying of scratch proof PVC/Vinyl flooring of 2mm thickness with proper welded joints air tight, along with leveling compound to match the existing flooring levels as per engineer in charge instructions. Sub floor preparation with self leveling compound. After the sub floor preparation, it should be suitable for ESD flooring. Rate inclusive of sifting of material and labour charges. at MGM Warangal | 120 | Sqm | 4070 | 488400 | 120 | Sqm | 4070 | 488400 | 0 | 0 |  | C
| AE |  |  |  |  | 50 | Sqm | 4070 | 203500 | 203500 | 0 |  | C
490 | Supply, installation, testing and commissioning of 16 G GI powder coated suitable single person entry air shower as per the technical Specifications at MGM Warangal | 1 | No | 355000 | 355000 | 1 | No | 355000 | 355000 | 0 | 0 |  | C
C
491 | Supply, installation, Testing and Commissioning of Static Pass Boxes of Size 450X450mm with 1.2mm thick SS 304 Mat finish , with interlock doors, UV light On when doors closed condition. As per clean room standard and requirement. at MGM Warangal | 3 | No | 61000 | 183000 | 3 | No | 61000 | 183000 | 0 | 0 |  | C
C
[5 empty] | 7320696 |  |  | PART-A | 9771662 | 3717655 | 1266689 | 2450966
|  |  |  | As Per Agreement | 7320696 |  |  | Excess | 3717655
|  |  |  | As Per Workdone | 9771662 |  |  | Less | 1266689
|  |  |  | Net Difference | 2450966 |  |  | Net Difference | 2450966
PLUMBING
469 | Supplying and fixing 15 mm brass body CP finish bib tap of not less than 300 grams weight screw type full turn with internal / external threaded connection conforming to IS 8931 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges , overheads and contractors profit complete for finished item of work in all floors. at MGM Warangal | 4 | No | 881 | 3524 | 0 | No | 881 | 0 | 0 | 3524 |  | P
P
470 | Supply and fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings SDR 13.5 to meet the requirement of ASTM-D 2846 and are produced in CTS Copper Tube Sizes 1/2inches to 2inches for hot and cold water IS 15778:2007 including cost and conveyance of all materials to site, labour charges for fixing,complete for finished item of work at all floor levels. 15.90mm OD pipe at MGM Warangal | 50 | Rmt | 199 | 9950 | 50 | Rmt | 199 | 9950 | 0 | 0 |  | P
P
471 | Supply and fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings SDR 13.5 to meet the requirement of ASTM-D 2846 and are produced in CTS Copper Tube Sizes 1/2inches to 2inches for hot and cold water IS 15778:2007 including cost and conveyance of all materials to site, labour charges for fixing,complete for finished item of work at all floor levels. 22.20mm OD pipe at MGM Warangal | 50 | Rmt | 229 | 11450 | 50 | Rmt | 229 | 11450 | 0 | 0 |  | P
P
472 | Supplying and fixing of SWR PVC pipes Prince/Sudhakar/Kisan/Supreme or any ISI brand 4 Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, complete for finished item of work at all floor levels. APSS No. 1302 1319 and 1326 - 75mm dia at MGM Warangal | 75 | Rmt | 327 | 24525 | 75 | Rmt | 327 | 24525 | 0 | 0 |  | P
P
473 | Supplying and fixing of SWR PVC pipes Prince/Sudhakar/Kisan/Supreme or any ISI brand 4 Kg/Sq.cm. and fixing all special such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps if necessary with required number of Bombay nails including cost and conveyance of all materials to site, labour charges, complete for finished item of work at all floor levels. APSS No. 1302 1319 and 1326- 110mm dia at MGM Warangal | 60 | Rmt | 444 | 26640 | 60 | Rmt | 444 | 26640 | 0 | 0 |  | P
P
474 | Supplying and fixing Bronze Gate/ Globe valve as per IS - 778 Class - I, Indian make heavy type including cost and conveyance of all materials , labour charges , overheads and contractors profit complete for finished item of work. 25mm Nominal bore at MGM Warangal | 4 | No | 1750 | 7000 | 4 | No | 1750 | 7000 | 0 | 0 |  | P
P
475 | Supplying and fixing of 4inches 101.6mm multi floor trap with jali - UPVC/SWR pipe fittings as per site requirements with standard practice for all floors including cost and conveyance of all materials to site, labour charges , etc., complete for finished item of work. at MGM Warangal | 8 | No | 220 | 1760 | 5 | No | 220 | 1100 | 0 | 660 |  | P
P
476 | Supplying and fixing Indian make Flat Back Wash Hand Basin 1st quality conforming to IS:2556-Part-4:1972 of size 550mm x 400mm with 32 mm nominal size C.P. Fitting with parallel pipe thread conforming to IS:2963- 1979 and fitted with 15 mm nominal bore Chromium Plated Pillar Tap of 1st quality Indian make heavy duty complete with standard CI brackets including wooden blocks ,1 No.12.70mm PVC connection with brass union nuts CP coated , angle stop cock 12.70mm dia. first quality Indian make heavy duty, 30mm dia. PVC flexible waste pipe 914.4mm length of 1st quality including cost and conveyance of all materials to site, labour charges , for finished item of work at MGM Warangal | 4 | No | 3800 | 15200 | 4 | No | 3800 | 15200 | 0 | 0 |  | P
P
477 | Supply, Installation and commissioning approved make floor mounted Anglo Indian wash down EWC conforming to IS:2556 Part 8-2004 suit with P or S trap with dual flush porcelain cistern fixed on wash down EWC with all internal parts of dual flush cistern, ultra solid seat cover of approved make with rubber buffer and cap and 15 mm angle stop cock and 450 mm long PVC inter connection pipe wall flanges all of approved make etc. complete for finished item of work in all respects: TBSP-E.II-03 at MGM Warangal | 4 | No | 7590 | 30360 | 4 | No | 7590 | 30360 | 0 | 0 |  | P
P
478 | Supplying and fixing Chromium plated finish brass body quarter turn Bibcock cum Health Faucet with 1m long tube and wall hook with necessary fittings etc., complete including cost and conveyance of all materials, labour charges, complete for finished item of work in all floors. at MGM Warangal | 4 | No | 4580 | 18320 | 4 | No | 4580 | 18320 | 0 | 0 |  | P
P
479 | Supplying and fixing CP finish brass soap dish of approved make ISI quality including cost and conveyance of all materials, labour charges for fixing, for finished item of work in all floors at MGM Warangal | 4 | No | 872 | 3488 | 4 | No | 872 | 3488 | 0 | 0 |  | P
P
480 | Supplying and fixing TV shape mirror with plastic frame of size 609.6mm x 457.2mm, plywood back with NP screws 1st quality including cost and conveyance of all materials, labour charges, for finished item of work in all floors. at MGM Warangal | 4 | No | 727 | 2908 | 4 | No | 727 | 2908 | 0 | 0 |  | P
P
481 | Supplying and fixing of CP finish brass wall mounted towel ring at MGM Warangal | 4 | No | 872 | 3488 | 4 | No | 872 | 3488 | 0 | 0 |  | P
P
482 | Supplying and fixing 15 mm brass body CP finish self closing tap push type conforming to IS 1711 as approved by the Engineer-In-Charge including cost and conveyance of all materials, labour charges, complete for finished item of work in all floors. at MGM Warangal | 4 | No | 418 | 1672 | 4 | No | 418 | 1672 | 0 | 0 |  | P
[5 empty] | 160285 |  |  | PART-A | 156101 | 0 | 4184 | -4184
|  |  |  | As Per Agreement | 160285 |  |  | Excess | 0
|  |  |  | As Per Workdone | 156101 |  |  | Less | 4184
|  |  |  | Net Difference | -4184 |  |  | Net Difference | -4184
ELECTRICAL
492 | Supply and laying of ISI 25mm outer dia medium grade with IS:9537-part 3 rigid PVC pipe concealed in wall with all required PVC / Metallic Junction Boxes including masonry work and labour charges etc., Makes: Sudhakar/ Precision /Universal/ Modi / Million Plast. at MGM Warangal | 220 | Rmt | 116 | 25520 | 220 | Rmt | 116 | 25520 | 0 | 0 |  | E
| AE |  |  |  |  | 136.9 | Rmt | 116 | 15880 | 15880 | 0 |  | E
E
493 | Supply and laying of ISI 25mm outer dia medium grade with IS:9537-part 3 rigid PVC pipe surface on wall with all required PVC / Metallic Junction Boxes including masonry work and labour charges etc., Makes: Sudhakar / Precision /Universal/ Modi / Million Plast. at MGM Warangal | 500 | Rmt | 107 | 53500 | 500 | Rmt | 107 | 53500 | 0 | 0 |  | E
| AE |  |  |  |  | 691.9 | Rmt | 107 | 74033 | 74033 | 0 |  | E
E
494 | Wiring with 2 runs of 22/0.3mm 1.5 Sq.mm FRLS / HFFR P.V.C. insulated flexible copper cable ISI MARK in existing pipe with 6A Modular switch, Ceiling rose/BH/SBH Modular switches with cover plate and GI switch box including all labour charges etc., complete. for Non- Residential Building Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. Makes of switches: - GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/Gold Medal curve. at MGM Warangal | 105 | Pts | 1070 | 112350 | 105 | Pts | 1070 | 112350 | 0 | 0 |  | E
| AE |  |  |  |  | 65 | Pts | 1070 | 69550 | 69550 | 0 |  | E
E
495 | Supply and fixing of 6A ISI Mark 3/2 pin Modular socket with 6A 1way Modular switch, 3 Module box with cover frame and GI switch box on common switch board with connections etc., complete. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. Makes of switches: - GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/Gold Medal curve. at MGM Warangal | 12 | No | 766 | 9192 | 12 | No | 766 | 9192 | 0 | 0 |  | E
| AE |  |  |  |  | 18 | No | 766 | 13788 | 13788 | 0 |  | E
E
496 | Supply and fixing of 16A switches - 1Nos and 6/16A 2 in one socket - 1Nos Modular type with cover plate and GI switch box fixing on separate board including all labour charges etc., complete. Makes of switches: - GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/Gold Medal curve. at MGM Warangal | 40 | No | 1040 | 41600 | 22 | No | 1040 | 22880 | 0 | 18720 |  | E
E
497 | Supply and fixing of 16A/6A, 2 in one socket - 2 Nos with 16A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: - GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/Gold Medal curve. at MGM Warangal | 60 | No | 1755 | 105300 | 60 | No | 1755 | 105300 | 0 | 0 |  | E
E
498 | Supply and fixing of 16A/6A, 2 in one socket - 4 Nos with 16A switch control - 4 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: - GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/Gold Medal curve. at MGM Warangal | 10 | No | 3092 | 30920 | 0 | No | 3092 | 0 | 0 | 30920 |  | E
E
499 | Supply and run of 1 of 22 /0.3mm 1.5 Sq.mm FRLS / HFFR P.V.C. insulated flexible copper cable in existing conduit pipe for earth continuity including all labour charges etc., complete. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at MGM Warangal | 375 | Rmt | 40 | 15000 | 106.5 | Rmt | 40 | 4260 | 0 | 10740 |  | E
E
500 | Supply and run of 3 of 2.5 sq.mm 36/0.mm phase neutral and earth FRLS / HFFR PVC insulated flexible copper cable in existing conduit pipe for individual lighting circuits including labour charges etc., complete as required for switch boards. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at MGM Warangal | 600 | Rmt | 177 | 106200 | 600 | Rmt | 177 | 106200 | 0 | 0 |  | E
| AE |  |  |  |  | 498.7 | Rmt | 177 | 88270 | 88270 | 0 |  | E
E
501 | Supply and 3 runs of 4.0 sq mm 56/0.3 mm phase neutral and earth FRLS / HFFR PVC insulated flexible copper cable in existing conduit pipe including labour charges etc., complete for 16A sockets. Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at MGM Warangal | 1200 | Rmt | 255 | 306000 | 1200 | Rmt | 255 | 306000 | 0 | 0 |  | E
| AE |  |  |  |  | 168.8 | Rmt | 255 | 43044 | 43044 | 0 |  | E
E
502 | Supply and run of 5 of 6.0 Sqmm 90/0.3 mm 3 phases, neutral and earth FRLS / HFFR PVC insulated flexible copper cable in the existing conduit pipe for run of mains from Power panel board to TPN DBs with pin type lugs and connections etc., complete. for LDBs Makes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL. at MGM Warangal | 60 | Rmt | 606 | 36360 | 60 | Rmt | 606 | 36360 | 0 | 0 |  | E
| AE |  |  |  |  | 152.8 | Rmt | 606 | 92597 | 92597 | 0 |  | E
E
503 | Supply and run of 5 of 10.0 Sqmm 140/0.3 mm 3 phases, neutral and earth FRLS / HFFR PVC insulated flexible copper cable in the existing conduit pipe for run of mains from Power panel board to TPN DBs with pin type lugs and connections etc., complete. for PDBsMakes of wires: Finolex/ RR Cable/ Havells/ Polycab/ HPL at MGM Warangal | 40 | Rmt | 967 | 38680 | 40 | Rmt | 967 | 38680 | 0 | 0 |  | E
| AE |  |  |  |  | 274.4 | Rmt | 967 | 265345 | 265345 | 0 |  | E
E
504 | Supply and fixing of DP Metal Enclosure with IP 20 Protection DB Make with 1 No 20A, 10 KA DP MCB Make: Legrand / Schneider including internal connection and labour charges for Flush Mounting etc., complete. Makes: Legrand / Schneider. at MGM Warangal | 5 | No | 2562 | 12810 | 5 | No | 2562 | 12810 | 0 | 0 |  | E
E
505 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand / Schneider and Supply and Fixing of 1 No., of 40A FP 30mA RCCB as incomer and 12 Nos 6-32 A 10kA SP MCBs Makes: Legrand-DX3 / Schneider-Acti9 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. For Lighting DBs at MGM Warangal | 3 | No | 18325 | 54975 | 3 | No | 18325 | 54975 | 0 | 0 |  | E
| AE |  |  |  |  | 7 | No | 18325 | 128275 | 128275 | 0 |  | E
E
506 | Supply and fixing of 8 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand / Schneider and Supply and Fixing of 1 No., of 63A FP 100mA RCCB as incomer and 24 Nos 6-32 A 10kA SP MCBs Makes: Legrand-DX3 / Schneider-Acti9 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. For Lighting DBs at MGM Warangal | 2 | No | 28460 | 56920 | 0 | No | 28460 | 0 | 0 | 56920 |  | E
E
507 | Supply and fixing of 8 Way VTPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand / Schneider and Supply and Fixing of 1 No., of 100A FP 10KA MCB as incomer and 4 Nos 63 A 10kA TP MCBs, 4 Nos 40 A 10kA TP MCBs Makes: Legrand-DX3 / Schneider-Acti9 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. For UPS MDB DBs at MGM Warangal | 1 | No | 64067 | 64067 | 1 | No | 64067 | 64067 | 0 | 0 |  | E
E
508 | Providing and fixing of 125A 25KA TPN Thermal Magnetic Release Based MCCB and Terminal Spreaders in Existing panel board with 1 No. and 1 Set of Indication Lamps, LED type, R,Y,B and breaker ON , OFF, TRIP and spring charged lamps. and replace with above Mentioned with required Drilling Holes, removing and Making Busbar connections etc, as required. Makes: Legrand / Schneider/ABB/ LandT/CandS at MGM Warangal | 1 | No | 28883 | 28883 | 1 | No | 28883 | 28883 | 0 | 0 |  | E
E
509 | Providing and fixing of 100A 10KA FP MCB and Terminal Spreaders in IP 43 isolator Box Making connections etc, as required. Makes: Legrand / Schneider/ ABB/LandT/CandS at MGM Warangal | 2 | No | 3260 | 6520 | 0 | No | 3260 | 0 | 0 | 6520 |  | E
E
510 | Supply, transportation and fixing of 24W edge lit LED Down light Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser Square with Protruded high efficiency diffuser, IP20, with wide operating voltage range, Power factor greater than 0.9, Surge protection: greater than 2KV, System efficacy of greater than100 lumens/watt, CCT: 3000K - 6500K as desired by the department and as per IS, CRI greater than80, and THD is less than 15percentage etc., with BIS Certification. Makes: Phillips / OSRAM / Wipro / Crompton / Bajaj / Havells at MGM Warangal | 56 | No | 2652 | 148512 | 56 | No | 2652 | 148512 | 0 | 0 |  | E
| AE |  |  |  |  | 14 | No | 2652 | 37128 | 37128 | 0 |  | E
E
511 | Supply and Transportation 36W Edge lit, 2 feet x2 feet 600mm x600mm slim panel LED luminaire Square Housing Made of Aluminum alloy with corrosion resistant powder coat, with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor greater than 0.9, Surge protection greater than 2KV, System efficacy of greater than100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI greater than80, and THD is less than 15percentage etc., complete. Makes: Phillips / OSRAM / Wipro / Crompton / Bajaj / Havells at MGM Warangal | 36 | No | 4350 | 156600 | 36 | No | 4350 | 156600 | 0 | 0 |  | E
| AE |  |  |  |  | 50 | No | 4350 | 217500 | 217500 | 0 |  | E
E
512 | Supply and Transportation 42W Clean room Light fixture, 2 feet x2 feet 600mm x600mm LED luminaire CRCA powder coated white after phosphocreatine treatment provided as standard. with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor greater than 0.9, Surge protection greater than 2KV, System efficacy of greater than100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI greater than80, and THD is less than 15percentage etc., complete. MAKE: OSRAM / Wipro / Crompton / Bajaj / Havells at MGM Warangal | 12 | No | 4762 | 57144 | 0 | No | 4762 | 0 | 0 | 57144 |  | E
E
513 | Supply and fixing of ISI mark batten holder / slanting holder Makes : Anchor / Gold Medal Olive / Million Zoom in lieu of ceiling rose of light point complete with all connections and all labour charges with 5.0W LED Lamp MAKE: OSRAM / Wipro / Crompton / Bajaj / Havells at MGM Warangal | 5 | No | 184 | 920 | 0 | No | 184 | 0 | 0 | 920 |  | E
E
514 | Supply, Transportation of energy efficient fan, 1200 mm sweep, aluminium body, consuming 28 W, BEE 5 star rated, ceiling fan with Brush Less Direct Current BLDCmotor, class of insulation: B, 3 nos blades, 30 cm long down rod, 2 nos canopies, shackle kit, safety rope, copper winding, Power Factor greater than 0.90, Service Value CMMAV greater than 8.5, Air delivery minimum 235 CMM,350 RPM tolerance as per IS:374-2019, THD less than 10percentage. with remote or compatible to electronic step type regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise equal to75 degree Cmax, insulation resistance more than 2 mega ohm, suitable for 230V, 50 HZ, single phase AC supply, earthing etc., including all standard accessories etc., complete. Makes : Atomberg Efficio / Havells /Orient at MGM Warangal | 12 | No | 4090 | 49080 | 0 | No | 4090 | 0 | 0 | 49080 |  | E
E
515 | Supply and fixing of Modular type Stepped electronic regulator Makes : GM Four-Five / Legrand Arteor / Schneider Zen celo /Honeywell Blenge Plus/ Cabtree Verna/ Million logus / Gold Medal Curve for sweep AC ceiling fans of 1200mm / 1400mm complete with connections. at MGM Warangal | 12 | No | 827 | 9924 | 12 | No | 827 | 9924 | 0 | 0 |  | E
| AE |  |  |  |  | 20 | No | 827 | 16540 | 16540 | 0 |  | E
E
516 | Supply and installation of 225mm Light duty exhaust fan with metal blades etc complete Makes: Crompton / Havells Ventilair-DB/ Orient hill air. at MGM Warangal | 5 | No | 2203 | 11015 | 5 | No | 2203 | 11015 | 0 | 0 |  | E
| AE |  |  |  |  | 2 | No | 2203 | 4406 | 4406 | 0 |  | E
E
517 | SITC of Hot dip galvanized perforated cable tray of 100 mm Wide sizes for to run the cable from DBs to SBs and sockets and AC panel to Units units. All necessary supports and accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. at MGM Warangal | 70 | Rmt | 429 | 30030 | 70 | Rmt | 429 | 30030 | 0 | 0 |  | E
E
518 | SITC of Hot dip galvanized perforated cable tray of 300 mm Wide sizes for to run the cable from Floor Panel to Lab Panel and electrical room to AC panel and AC panel to Units. All necessary supports and accessories are included. Cable tray for cables alone shall be included here Thickness shall be 1.6 mm. at MGM Warangal | 80 | Rmt | 1310 | 104800 | 80 | Rmt | 1310 | 104800 | 0 | 0 |  | E
| AE |  |  |  |  | 37.3 | Rmt | 1310 | 48863 | 48863 | 0 |  | E
519 | Supply and installation of 20KVA 3ph in and 3ph out on line UPS system IGBT based rectifier with input power factor correction 32 bit microprocessor based with isolation transformers double conversion, SNMP controls, LCD display, Pure sine wave output, with auto static switch three phase input / Three phase output and modular structure for better thermal technology / cooling facility, with warranty up to three years. Makes: APC / Numeric / Emerson / Fuji Electric at MGM Warangal | 1 | No | 305000 | 305000 | 1 | No | 305000 | 305000 | 0 | 0 |  | E
E
520 | Supply and fixing of 12V 65 AH SMF battery including wire leads. Makes: Quanta / Racket / Exide. at MGM Warangal | 20 | No | 20584 | 411680 | 20 | No | 20584 | 411680 | 0 | 0 |  | E
| AE |  |  |  |  | 12 | No | 20584 | 247008 | 247008 | 0 |  | E
E
521 | Supply and providing of UPS cum battery rack for 20 batteries at MGM Warangal | 1 | No | 6764 | 6764 | 1 | No | 6764 | 6764 | 0 | 0 |  | E
E
522 | Providing and Fixing maintenance free earthing which consists of G.I. Earth station, with 600X600X3.15mm GI Plate at 2500mm Depth including construction of brick pedestal, providing meshed funnel, GI cover and other civil Engineering works, spreading a homogenous mixture of salt, charcoal around the pipe etc., completely as per IS 3043, 1987 or latest revision. Earthing testing should be done as per IE Rules like Earth valve test Etc. at MGM Warangal | 2 | No | 8500 | 17000 | 2 | No | 8500 | 17000 | 0 | 0 |  | E
E
523 | Providing and Fixing maintenance free earthing which consists of copper. Earth station, with 600X600X3.15mm Copper Plate at 2500mm Depth including construction of brick pedestal, providing meshed funnel, GI cover and other civil Engineering works, spreading a homogenous mixture of salt, charcoal around the pipe etc., completely as per IS 3043, 1987 or latest revision. Earthing testing should be done as per IE Rules like Earth valve test Etc. at MGM Warangal | 2 | No | 22283 | 44566 | 2 | No | 22283 | 44566 | 0 | 0 |  | E
| AE |  |  |  |  | 2 | No | 22283 | 44566 | 44566 | 0 |  | E
E
524 | Supply and installation of 50x6 GI flat for body earthing of electrical panel and AC Panel which is laid in 300mm cable tray at MGM Warangal | 200 | Rmt | 329 | 65800 | 200 | Rmt | 329 | 65800 | 0 | 0 |  | E
| AE |  |  |  |  | 36.7 | Rmt | 329 | 12074 | 12074 | 0 |  | E
E
525 | Supply and installation of 25x3 GI flat for body earthing of DBs and Cable tray which is laid in 100mm cable tray at MGM Warangal | 100 | Rmt | 163 | 16300 | 0 | Rmt | 163 | 0 | 0 | 16300 |  | E
E
526 | Supply and installation of 25x3 Copper flat for Neutral earthing of UPS and Equipment which is laid in 100mm cable tray at MGM Warangal | 200 | Rmt | 902 | 180400 | 200 | Rmt | 902 | 180400 | 0 | 0 |  | E
| AE |  |  |  |  | 2.1 | Rmt | 902 | 1894 | 1894 | 0 |  | E
E
527 | Supply and installation of 4 sqmm Copper wire for Earthing of DBs Equipment at MGM Warangal | 80 | Rmt | 83 | 6640 | 80 | Rmt | 83 | 6640 | 0 | 0 |  | E
| AE |  |  |  |  | 484.8 | Rmt | 83 | 40238 | 40238 | 0 |  | E
E
528 | Supply, Lying and testing of 3.5Cx95 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc.. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex Make of gland and Lungs: HMI/Commet/Dowell’s at MGM Warangal | 120 | Rmt | 1207 | 144840 | 120 | Rmt | 1207 | 144840 | 0 | 0 |  | E
E
529 | Supply, Lying and testing of 3.5CX50 sqmm XLPE Insulated Cable 1100V grade armoured aluminium cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc.. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex Make of gland and Lungs: HMI/Commet/Dowell’s at MGM Warangal | 70 | Rmt | 722 | 50540 | 70 | Rmt | 722 | 50540 | 0 | 0 |  | E
E
530 | Supply, Lying and testing of 4Cx16 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc.. Make of Cable: Polycab/KEI/Universal/Glostar/Finolex Make of gland and Lungs: HMI/Commet/Dowell’s at MGM Warangal | 100 | Rmt | 1483 | 148300 | 100 | Rmt | 1483 | 148300 | 0 | 0 |  | E
| AE |  |  |  |  | 194.3 | Rmt | 1483 | 288147 | 288147 | 0 |  | E
E
531 | Supply, Lying and testing of 4Cx6 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex, Make of gland and Lungs: HMI/Commet/Dowell’s at MGM Warangal | 120 | Rmt | 484 | 58080 | 120 | Rmt | 484 | 58080 | 0 | 0 |  | E
| AE |  |  |  |  | 64.2 | Rmt | 484 | 31073 | 31073 | 0 |  | E
E
532 | Supply, Lying and testing of 4Cx4 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark as per specification confirming to IS:7098 Part - I with heavy duty type double compression weather proof type brass cable glands duly nickel plated as per BS 6121 and IP66 complete with brass checknut, outer sheath sealing gasket heavy duty long barrel aluminium lugs confirming to I.S specifications with complete nut, bolt and washer etc. Make of Cable: Polycab/ KEI/Universal/Glostar/Finolex, Make of gland and Lungs: HMI/Commet/Dowell’s at MGM Warangal | 80 | Rmt | 356 | 28480 | 80 | Rmt | 356 | 28480 | 0 | 0 |  | E
| AE |  |  |  |  | 103.6 | Rmt | 356 | 36882 | 36882 | 0 |  | E
E
533 | SITC of IVF Center Main Panel Indoor IP-42 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with /without detachable extension type structure with all type of suitable switching accessories and bus-bar as per load requirement of respective IVF equipment’s. Which is including Lighting, power DBs and UPS at MGM Warangal | 1 | No | 382355 | 382355 | 1 | No | 382355 | 382355 | 0 | 0 |  | E
E
534 | SITC of IVF center AC Panel outdoor IP-54 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with / without detachable extension type structure with all type of suitable switching accessories and bus-bar as per load requirement of respective AC equipment’s. Which is including 1nos AHU’s stater with VFD by pass, Heater, ODU and VRF system at MGM Warangal | 1 | No | 288250 | 288250 | 1 | No | 288250 | 288250 | 0 | 0 |  | E
E
535 | Supply and installation of AHUs stater on/off push button station for Remote control for inside IVF center with control wiring from AC panel to on /off push button station with necessary items. at MGM Warangal | 3 | No | 1540 | 4620 | 3 | No | 1540 | 4620 | 0 | 0 |  | E
[5 empty] | 3832437 |  |  | PART-A | 5402274 | 1817101 | 247264 | 1569837
|  |  |  | As Per Agreement | 3832437 |  |  | Excess | 1817101
|  |  |  | As Per Workdone | 5402274 |  |  | Less | 247264
|  |  |  | Net Difference | 1569837 |  |  | Net Difference | 1569837
ELV WORKS
536 | Supply, installation, testing and commissioning of 20nos LAN points with cat 6 cable and with suitable network rack and 5nos of telephone points with krone box to existing EPABEX. at MGM Warangal | 1 | Job | 383000 | 383000 | 1 | Job | 383000 | 383000 | 0 | 0 |  | ELV
ELV
537 | Supply, installation, testing and commissioning of 1 no of Access control system with egress switch, Power Cable, communication cable to control panel with necessary required items Etc. at MGM Warangal | 1 | Job | 124000 | 124000 | 1 | Job | 124000 | 124000 | 0 | 0 |  | ELV
ELV
538 | Supply, installation, testing and commissioning of Automatic Fire Alarm System which is including 30 nos of smoke Detectors 1nos manual call point, 1 no of Hooter with fire alarm cable connected to the existing fire control panel with necessary Required items etc.. at MGM Warangal | 1 | Job | 510000 | 510000 | 1 | Job | 510000 | 510000 | 0 | 0 |  | ELV
ELV
539 | Supply, installation, testing and commissioning of 5nos IP Based CCTV cameras and Cat 6 Cable with NVR system. at MGM Warangal | 1 | Job | 182000 | 182000 | 1 | Job | 182000 | 182000 | 0 | 0 |  | ELV
ELV
540 | Supply, installation, testing and commissioning of Audio and video recording of counseling rooms at MGM Warangal | 1 | Job | 138000 | 138000 | 1 | Job | 138000 | 138000 | 0 | 0 |  | ELV
[5 empty] | 1337000 |  |  | PART-A | 1337000 | 0 | 0 | 0
|  |  |  | As Per Agreement | 1337000 |  |  | Excess | 0
|  |  |  | As Per Workdone | 1337000 |  |  | Less | 0
|  |  |  | Net Difference | 0 |  |  | Net Difference | 0
FIRE FIGHTING WORKS
541 | Supply and installation of Fire Extinguishers of CO2 4.50 Kg at MGM Warangal | 5 | No | 11225 | 56125 | 5 | No | 11225 | 56125 | 0 | 0 |  | FF
FF
542 | Supply and installation of ceiling mounted Fire Extinguishers of ABC MAP 90, 5.0 Kg stored pressure type at MGM Warangal | 5 | No | 7686 | 38430 | 5 | No | 7686 | 38430 | 0 | 0 |  | FF
FF
543 | Supply and installation of 2.0 Kg clean agent HCFC 123 Fire Extinguishers at MGM Warangal | 5 | No | 15065 | 75325 | 5 | No | 15065 | 75325 | 0 | 0 |  | FF
FF
544 | Supply and fixing of Fire escape signage Boards at MGM Warangal | 1 | Job | 56000 | 56000 | 1 | Job | 56000 | 56000 | 0 | 0 |  | FF
[5 empty] | 225880 |  |  | PART-A | 225880 | 0 | 0 | 0
|  |  |  | As Per Agreement | 225880 |  |  | Excess | 0
|  |  |  | As Per Workdone | 225880 |  |  | Less | 0
|  |  |  | Net Difference | 0 |  |  | Net Difference | 0
AIR CONDITIONING WORKS
545 | Supply, transportation and installation of split AC unit 1.5 TR inverter type 3 Star capable of delivering 18000 BTU/hr and above with high wall mounted indoor unit and outdoor condensing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord , built-in stabilizer Voltage range 160- 264 volts and cordless remote control. Makes : Daikin / Thoshiba / O General at MGM Warangal | 1 | No | 48000 | 48000 | 1 | No | 48000 | 48000 | 0 | 0 |  | AC
| AE |  |  |  |  | 3 | No | 48000 | 144000 | 144000 | 0 |  | AC
546 | Supply, transportation and installation of split AC unit 1.0 TR inverter type minimum 3 Star capable of delivering 12000 BTU/hr and above with high wall mounted indoor unit and outdoor condensing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord , built-in stabilizer Voltage range 160- 264 volts and cordless remote control. Makes: Daikin / Thoshiba / O General at MGM Warangal | 1 | No | 40000 | 40000 | 1 | No | 40000 | 40000 | 0 | 0 |  | AC
AC
547 | Modular Double skin floor mounted EUROVENT Certified Air Handling Unit 3000CFM / 8.5 TR / 150mm SP made out of 45 plus or minus 2mm thick PUF insulated panels Thermal break aluminium profile frame work with 0.8mm thick pre painted / powder coated inner and outer skins comprising of mixing box with fresh air and return air dampers, pre filters with 10 and 5 microns combination filters in single frame, Interlaced/Intertwined DX Cooling Coil suitable for connecting 2 nos of 8.5TR capacity 1W plus 1S out door condensing units, SS304 drain pan with, blower section with Nicotra / Kruger make direct drive/ Plug type fan, vibration isolators, EFF1 motor and blower section with on/off switches to operate from outside, limit switch for the fan section access door with a view port, fine filter section with 3 microns filters inspection doors for all filter and fan sections and damper at the outlet of unit. Ports for differential pressure gauges across all filters and blower to measure differential pressure. AHU Make : VTS / Systemair, Make - Blower - Nicotra / Kruger ; Motor -Crompton Greaves / Siemens ; Filter - Thermodyne / Freudenberg / Ultrafil at MGM Warangal | 1 | No | 590000 | 590000 | 1 | No | 590000 | 590000 | 0 | 0 |  | AC
AC
548 | SITC of filter module made out of heavy duty Aluminium powder coated extrusion with minimum of 13G . and to house 610 mm X 610 mm HEPA Filter at the rate 0.3 microns , 99.9997, H-14 Grade, Filter loading from clean room side with bewel gear arrangement damper with access from clean room suitable to house the following filter sizes pressure drop and Integrity testing ports into room. Includes SS capsule perforated diffuser. This includes all required supports and accessories etc. Capacity 1000 CFM. at MGM Warangal | 6 | No | 42000 | 252000 | 6 | No | 42000 | 252000 | 0 | 0 |  | AC
AC
549 | SITC of air cooled condensing units with two scroll compressors, air cooled condenser, power panel, vibration isolating pads, stand for ODU, thermostat, etc. of the following capacities. The nominal capacity of the condensing unit shall be as under. Air cooled condensing unit shall have horizontal discharge. All refrigerant piping accessories sight glass, drier, expansion valve, etc. shall be supplied with the condensing units and suitable to connect above AHUs. Refrigerant shall be R 407C / R 410A. Necessary thermostat, control wiring, etc. shall be included. Derating of the unit shall not be more than 15percentage under 45 deg. C ambient temperature. Condensing unit shall be capable of operating up 50 deg. C ambient temperature. 8.5 TR capacity at MGM Warangal | 1 | No | 182000 | 182000 | 1 | No | 182000 | 182000 | 0 | 0 |  | AC
| AE |  |  |  |  | 1 | No | 182000 | 182000 | 182000 | 0 |  | AC
550 | SITC of Flange type, Flame proof FLP duct heaters of 5 kW capacity with Mineral Filled AISI SS304/SS321 Sheathed Tubular Heater with GI Helical fins, Tube dia 8.2mm min and Helical Finn dia 25mm min, enclosed in the frame, FLP Terminal box etc., Nickel Chromium Inner Element, Silicon Sealing to Restrict Moisture pickup, Silver brazed mounting plate etc., and heaters shall be controlled with PID thyrestor controller based on the analog output signal of 0-10 V DC of controller . And this should have saftey thermostat and cutouts and air stat etc. all safety controls. The capacities as follows and sizes of the heaters shall be as per the duct sizes and approved drawing. at MGM Warangal | 1 | No | 205000 | 205000 | 1 | No | 205000 | 205000 | 0 | 0 |  | AC
AC
551 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Liquid Line at MGM Warangal | 20 | Rmt | 1020 | 20400 | 20 | Rmt | 1020 | 20400 | 0 | 0 |  | AC
AC
552 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Suction Line at MGM Warangal | 20 | Rmt | 1190 | 23800 | 20 | Rmt | 1190 | 23800 | 0 | 0 |  | AC
AC
553 | SITC of CPVC drain ping with supports, clamps and 9 mm thk. Nitrile rubber tube insulation of the following sizes. Insulation shall have factory laminated glass cloth. 32mm Dia at MGM Warangal | 50 | Rmt | 670 | 33500 | 50 | Rmt | 670 | 33500 | 0 | 0 |  | AC
AC
554 | SITC of CPVC drain ping with supports, clamps and 9 mm thk. Nitrile rubber tube insulation of the following sizes. Insulation shall have factory laminated glass cloth. 25mm Dia at MGM Warangal | 50 | Rmt | 515 | 25750 | 50 | Rmt | 515 | 25750 | 0 | 0 |  | AC
AC
555 | SITC of Factory fabricated and boxed ducting using Aluminium Sheets / coils, should be fabricated as per SMACNA, galvanised hardware and supports, silicon sealant at all longitudinal joints, Galvanized /GI Electroplated iron angle flanges for all the joints, bracing angles and minimum 5mm thick neoprene rubber gasket.- Duct pressure testing at 75mm to be carried out before insulatiting the duct. pressure testing to be done as per SMACNA. Procedure to be approved by consultant. 20G - 1.0 mm Thick at MGM Warangal | 30 | Sqm | 2600 | 78000 | 30 | Sqm | 2600 | 78000 | 0 | 0 |  | AC
AC
556 | SITC of Factory fabricated and boxed ducting using Aluminium Sheets / coils, should be fabricated as per SMACNA, galvanised hardware and supports, silicon sealant at all longitudinal joints, Galvanized /GI Electroplated iron angle flanges for all the joints, bracing angles and minimum 5mm thick neoprene rubber gasket.- Duct pressure testing at 75mm to be carried out before insulatiting the duct. pressure testing to be done as per SMACNA. Procedure to be approved by consultant. 22G - 0.8 mm Thick at MGM Warangal | 250 | Sqm | 2325 | 581250 | 250 | Sqm | 2325 | 581250 | 0 | 0 |  | AC
AC
557 | Aluminium low leakage aerofoil design volume control dampers Suitable for manual and motorised operation at MGM Warangal | 2 | Sqm | 15800 | 31600 | 2 | Sqm | 15800 | 31600 | 0 | 0 |  | AC
AC
558 | CBRI approved 16G GI Spring return actuated fire dampers rated for 90 minutes with limit switch. at MGM Warangal | 2 | Sqm | 25900 | 51800 | 2 | Sqm | 25900 | 51800 | 0 | 0 |  | AC
AC
559 | SITC of SS perforated return raiser grilles with 10 microns filters with collar dampers at MGM Warangal | 2 | Sqm | 26300 | 52600 | 2 | Sqm | 26300 | 52600 | 0 | 0 |  | AC
AC
560 | Extruded Al. powder coated EXHAUST / RETURN discrete grilles at MGM Warangal | 1 | Sqm | 8125 | 8125 | 1 | Sqm | 8125 | 8125 | 0 | 0 |  | AC
AC
561 | SITC of Collar Dampers made of Al. extrusions with black powder coating for Grilles / Diffusers at MGM Warangal | 1 | Sqm | 7550 | 7550 | 1 | Sqm | 7550 | 7550 | 0 | 0 |  | AC
AC
562 | SITC of Magnehelic gauges across pre and fine filter at AHUs including mounting arrangement, SS nozzles, food grade PVC tubing, etc. at MGM Warangal | 2 | No | 10500 | 21000 | 2 | No | 10500 | 21000 | 0 | 0 |  | AC
AC
563 | SITC of Magnehelic gauges to measure the room differential pressures in operation theatres with SS mounting box, SS nozzles, food grade PVC tubing, etc. at MGM Warangal | 2 | No | 12900 | 25800 | 2 | No | 12900 | 25800 | 0 | 0 |  | AC
AC
564 | SITC of Aluminium powder coated Fresh air and Exhaust Louvers of non- vision type with nylon mosquito net etc. at MGM Warangal | 1 | Sqm | 10300 | 10300 | 1 | Sqm | 10300 | 10300 | 0 | 0 |  | AC
AC
565 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 32mm Thick for Exposed Supply Air duct and finished with UV Protective Paint. at MGM Warangal | 130 | Sqm | 1225 | 159250 | 130 | Sqm | 1225 | 159250 | 0 | 0 |  | AC
AC
566 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Exposed Return Air Duct and finished with UV Protective Paint.at MGM Warangal | 130 | Sqm | 1075 | 139750 | 130 | Sqm | 1075 | 139750 | 0 | 0 |  | AC
AC
567 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Supply air duct running inside the building. at MGM Warangal | 40 | Sqm | 785 | 31400 | 40 | Sqm | 785 | 31400 | 0 | 0 |  | AC
AC
568 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 19mm Thick for Return air running inside the building. at MGM Warangal | 40 | Sqm | 660 | 26400 | 40 | Sqm | 660 | 26400 | 0 | 0 |  | AC
AC
569 | Condensing units - VRF/VRV System : Supply, Installation, Nitrogen testing , Vacuuming and Commissioning of air cooled variable refrigerant flow modular type condensing units, each comprising of multiple scroll compressors all inverter driven, full charge of refrigerant gas R-410a including additional gas filling , lubricating oil and all accessories as per the specifications. The condensing units shall be suitable to work on cooling mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B . The COP of the system shall be greater than 4 under ARI conditions for 100percentage load . The condensing units shall be suitable for operation on 415 plus or minus 10percentage volts, 50Hz, 3 phase AC power supply and , outdoor units to be mounted on MS platform with suitable Vibration Isolation pads to avoid vibrations. All the supports and angle base frame structure to be duly black painted with synthetic epoxy paint. the condensing units shall be of following capacities: The VRF ODU should be capable of working with total capacity of connected indoor units ranging between 100percentage to 140percentage of ODU capacity . COP minimum 3.5. Make : Daikin / LG / O General / Toshiba at MGM Warangal 14 HP | 1 | Set | 325000 | 325000 | 1 | Set | 325000 | 325000 | 0 | 0 |  | AC
AC
570 | VRF Indoor Units : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 0.8 TR at MGM Warangal | 2 | No | 30700 | 61400 | 2 | No | 30700 | 61400 | 0 | 0 |  | AC
AC
571 | VRF Indoor Units : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.0 TR at MGM Warangal | 2 | No | 30700 | 61400 | 2 | No | 30700 | 61400 | 0 | 0 |  | AC
| AE |  |  |  |  | 2 | No | 30700 | 61400 | 61400 | 0 |  | AC
572 | VRF Indoor Units : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.25 TR at MGM Warangal | 2 | No | 35000 | 70000 | 0 | No | 35000 | 0 | 0 | 70000 |  | AC
AC
573 | VRF Indoor Units : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.50 TR at MGM Warangal | 4 | No | 35000 | 140000 | 4 | No | 35000 | 140000 | 0 | 0 |  | AC
| AE |  |  |  |  | 1 | No | 35000 | 35000 | 35000 | 0 |  | AC
574 | Cassette Units : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling mode.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 3.0 TR – 4 way at MGM Warangal | 1 | No | 50000 | 50000 | 1 | No | 50000 | 50000 | 0 | 0 |  | AC
AC
575 | Supply, Installation, Testing and Commissioning of Hard copper REFRIGERANT PIPING of 16swg various sizes with necessary supports, fittings, interconnecting the liquid and suction lines between the aircooled outdoor units and the indoor units. The piping shall be carried out of Hard drawn copper pipes of type K with soldered / brazed socket fittings. Isolating valves shall be provided to isolate each compressor, strainers, sight glass and any other component requiring proper operation and maintenance. Both the suction and liquid lines shall be insulated with 19mm thick closed cell insulation for above 25mm dia , 13mm thick for pipes below 25mm dia . The insulation finished with treated woven glass fiber reinforced covering for inside Piping and including making required holes in the wall and re finishing and water tight of holes after laying holes as per the specifications and approved drawings at MGM Warangal | 1 | Lot | 400000 | 400000 | 1 | Lot | 400000 | 400000 | 0 | 0 |  | AC
AC
576 | Supply, Installation , Testing and Commissioning of Refnet joints to be provided in refrigerant pipe line. Material of construction for fittings shall be similar to refrigerant piping. at MGM Warangal | 10 | Set | 6191 | 61910 | 10 | Set | 6191 | 61910 | 0 | 0 |  | AC
| AE |  |  |  |  | 1 | Set | 6191 | 6191 | 6191 | 0 |  | AC
577 | Supply and Installation of control cum transmission wiring of size 3C x 1.5 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing and accessories as at MGM Warangal | 150 | Rmt | 320 | 48000 | 150 | Rmt | 320 | 48000 | 0 | 0 |  | AC
AC
578 | Supply and Installation of cabling of size 2C x 1 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing and accessories as per the approved routing. at MGM Warangal | 100 | Rmt | 255 | 25500 | 100 | Rmt | 255 | 25500 | 0 | 0 |  | AC
[5 empty] | 3888485 |  |  | PART-A | 4247076 | 428591 | 70000 | 358591
|  |  |  | As Per Agreement | 3888485 |  |  | Excess | 428591
|  |  |  | As Per Workdone | 4247076 |  |  | Less | 70000
|  |  |  | Net Difference | 358591 |  |  | Net Difference | 358591
MGPS
579 | SITC of Oxygen Manifold Emergency for 1 plus 1 Cylinders, as per technical specifications. | 1 | Set | 20750 | 20750 | 1 | Set | 20750 | 20750 | 0 | 0 |  | G
G
580 | SITC of Oxygen Outlets with matching probes, as per HTM-2022/02-01 of UK/NFPA99C of USA as per enclosed technical specifications - Imported | 4 | each | 2506 | 10024 | 4 | each | 2506 | 10024 | 0 | 0 |  | G
G
581 | SITC of Oxygen Flowmeter with Humidifier, CE Certified with four digit number as per enclosed technical specifications - Imported | 4 | each | 1805 | 7220 | 4 | each | 1805 | 7220 | 0 | 0 |  | G
G
582 | SITC of Nitrous Oxide Manifold Emergency for 1 Cylinder, with high pressure Regulator, NRV, tailpipes etc. as per technical specifications | 1 | Set | 13250 | 13250 | 1 | Set | 13250 | 13250 | 0 | 0 |  | G
G
583 | SITC of N20 Outlets with matching probes, as per HTM-2022/02-01 of UK/NFPA99C of USA as per enclosed technical specifications - Imported | 4 | each | 2506 | 10024 | 4 | each | 2506 | 10024 | 0 | 0 |  | G
G
584 | SITC of C02 Manifold for 2 Cylinders, with high pressure Regulator, NRV, tailpipes etc. as per technical specifications | 1 | Set | 20750 | 20750 | 1 | Set | 20750 | 20750 | 0 | 0 |  | G
| AE |  |  |  |  | 1 | Set | 20750 | 20750 | 20750 | 0 |  | G
585 | SITC of C02 Outlets with matching probes, as per HTM-2022102- 01ofUK/NFPA99C of USA as per enclosed technical specifications - Imported | 4 | each | 2506 | 10024 | 4 | each | 2506 | 10024 | 0 | 0 |  | G
G
586 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 12mm COPPER PIPE at MGM Warangal | 24 | Rmt | 642 | 15408 | 24 | Rmt | 642 | 15408 | 0 | 0 |  | G
G
587 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 15mm COPPER PIPE at MGM Warangal | 114 | Rmt | 824 | 93936 | 114 | Rmt | 824 | 93936 | 0 | 0 |  | G
G
588 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 22mm COPPER PIPE at MGM Warangal | 36 | Rmt | 1191 | 42876 | 36 | Rmt | 1191 | 42876 | 0 | 0 |  | G
G
589 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 28mm COPPER PIPE at MGM Warangal | 18 | Rmt | 1473 | 26514 | 18 | Rmt | 1473 | 26514 | 0 | 0 |  | G
G
590 | SITC of Touch type LCD Area Alarm and Zonal Valve box- as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications imported for 3 gases at MGM Warangal | 1 | each | 275000 | 275000 | 1 | each | 275000 | 275000 | 0 | 0 |  | G
G
591 | SITC of Touch type LCD Area Alarm and Zonal Valve box- as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications imported for Master Main Alarm including all Gases at MGM Warangal | 1 | each | 375000 | 375000 | 1 | each | 375000 | 375000 | 0 | 0 |  | G
G
592 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 15mm 0D at MGM Warangal | 3 | each | 1938 | 5814 | 3 | each | 1938 | 5814 | 0 | 0 |  | G
G
593 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 22mm 0D at MGM Warangal | 3 | each | 2740 | 8220 | 3 | each | 2740 | 8220 | 0 | 0 |  | G
G
594 | SITC of Medical Line Valve, As per CE Certified/UL Listed, As per Technical Specifications- Indian 28mm 0D at MGM Warangal | 4 | each | 4378 | 17512 | 4 | each | 4378 | 17512 | 0 | 0 |  | G
G
595 | SITC of Bed Head Panel - as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications at MGM Warangal | 2 | each | 36750 | 73500 | 2 | each | 36750 | 73500 | 0 | 0 |  | G
[5 empty] | 1025822 |  |  | PART-A | 1046572 | 20750 | 0 | 20750
[5 empty] | 43811081 |  |  | TOTAL PART-A | 48207041 | 5984097 | 1588137 | 4395960
| For MGPS Works |  |  | As Per Agreement | 1025822 |  |  | Excess | 20750
|  |  |  | As Per Workdone | 1046572 |  |  | Less | 0
|  |  |  | Net Difference | 20750 |  |  | Net Difference | 20750
| For Total Part-A |  |  | As Per Agreement | 43811081 |  |  | Excess | 5984097
|  |  |  | As Per Workdone | 48207041 |  |  | Less | 1588137
|  |  |  | Net Difference | 4395960 |  |  | Net Difference | 4395960
EQUIPMENT SUPPLIMENTAL
1 | 3-Bay Surgical Scrub Station/Sink to be provided for use in the OT complex providing for pre-procedural scrub up with minimum three bay sink combination as suitable. The Scrub Station shall be made of Stainless Steel of 304 grade sheet with minimum thickness of 1.5mm and designed as per the high aesthetics of the theatre complex. Shall have smoothened surfaces & corners. The scrub sink shall be provided with a front access panel which shall be easily removed for access to the water-controlled valve, waste connections, stoppers & strainers. The Scrub station should be equipped with two foot operated and one elbow operated mechanisms. Shall have provision for fresh water and waste water piping ready for connections. |  |  |  |  | 1 | Nos | 97000 | 97000 | 97000 | 0 |  | EQPS
2 | Supply and installation of Stainless Steel 304 grade CSSD Rectangular Working table of size 1200 x 480 x 1050 mm with inbuilt sink of size 450 x 380 x 300 mm equipped with jali at bottom to stop any large particles entering into the drain to avoid drain clog. The table to be designed with raised front section and provision of SS sheet at foot level of the table forming a flat surface for storing/placing of items. The table to be of ready to use with all necessary fittings. |  |  |  |  | 1 | Nos | 46000 | 46000 | 46000 | 0 |  | EQPS
3 | Writing board made of Pressed wood coated with melamine surface. It has 900mm writing surface height, 200mm writing surface wide, and 11mm deep, suitable for working on dry wipe board markers. It has an aluminium frame with dark grey plastic corner caps and maker tray. It is enabled with an easy wall mounting with a concealed slot system. It can be mounted either horizontally or vertically. IT consists of a complete mounting set, marker tray, and a board marker |  |  |  |  | 1 | Nos | 2100 | 2100 | 2100 | 0 |  | EQPS
4 | Providing MDF 18 mm thick wooden table of size 900x450 mm with 1 drawer at right side of the table. The table includes keyboard tray. Bottom equipped with nylone bushes for floor protection and easy movement. |  |  |  |  | 1 | Nos | 14500 | 14500 | 14500 | 0 |  | EQPS
5 | SS-304 working table of size 685 x 685 x 762 mm with I type support inner frame SS-304 pipe of size 40 x 40 x 1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. |  |  |  |  | 2 | Nos | 16300 | 32600 | 32600 | 0 |  | EQPS
6 | SS-304 working table of size 457 x 457 x 762 mm with I type support inner frame SS-304 pipe of size 40 x 40 x 1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. |  |  |  |  | 1 | Nos | 14500 | 14500 | 14500 | 0 |  | EQPS
7 | SS-304 working table of size 61 x 610 x 762 mm with I type support inner frame SS-304 pipe of size 40 x 40 x 1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. |  |  |  |  | 1 | Nos | 15100 | 15100 | 15100 | 0 |  | EQPS
8 | SS-304 working table of size 660 x 610 x 762 mm with I type support inner frame SS-304 pipe of size 40 x 40 x 1.5 mm, and top with 1.5 mm thick SS-304 sheet. All four legs equipped with adjustable nylone bushes. |  |  |  |  | 1 | Nos | 15800 | 15800 | 15800 | 0 |  | EQPS
9 | Supply and fixing of Powder coated GI stand with 4 nos height adjustable racks of size 670x410x1570 mm connected to two big rods of rectangular hollow section type supported with 4 legs with wheels with brakes to restrict movement/easy movement. Equipped with frame for holding a cylinder. A lockable box type space to be provided at bottom rack. |  |  |  |  | 1 | Nos | 80000 | 80000 | 80000 | 0 |  | EQPS
[8 empty] | PART-B | 317600 | 317600 | 0 | 317600
|  |  |  | As Per Agreement | 0 |  |  | Excess | 317600
|  |  |  | As Per Workdone | 317600 |  |  | Less | 0
|  |  |  | Net Difference | 317600 |  |  | Net Difference | 317600
CIVIL SUPPLIMENTAL
10 | Providing, Fabricating and fixing full height V-board partitions of overall thickness of 75mm Partition frame work to be formed out of 50 X 25mm aluminium frame work placed vertically and horizontally at required centre to centre and cross braced with floor and ceiling channels. The cross bracing channels shall be provided also at above and below the partition framework and to be secured to floor at bottom and to any nearest structural member using galvanized metal screws and wooden / PVC rawl plugs. Partition framework to be cladded with 12.5mm thick tapered edge board on both sides of the partition in line and level fixed with drywall screws @ 300mm c/c with staggered joints to avoid through joints and finished with proprietary supplied jointing tape and compound. |  |  |  |  | 15 | Sqm | 1625 | 24375 | 24375 | 0 |  | CS
11 | Providing of Factory made prelaminated FPVC (Foamed Polyvinyl Chloride) Door frame of the size 105x40mm with a wall thickness of 10mm made out of extruded rigid FPVC profile mitre joined with 6 Nos. of 50mm long screw. The door frame shall be fixed to the wall by using 80mm long screws through the frame with the help of PVC fasteners of 3 no's to be provided for each vertical member, GI stiffeners of ("U" channel of size 29x9x1mm, 150mm long) -3 no's at hinge point, Frame reinforcement of("U" GI channel of size 46x22x.06mm), Bottom tie rod of ("U" GI channel size of 15x15x1mm) etc. complete as per manufacturers specification for finished item of work. Maximum door frame size: 980 x 2070 including providing of 35mm thick Factory made Prelaminated ABS (Acrolynitrile Butadyne Styrene) Door shutter moulded in in different designs, consisting of all round Frame made out of water proof solid foam PVC bar of size 20x32mm, reinforced by 32x 32mm 2 nos. for vertical made out of LVL (Laminated Veneer Lumber), core material of 32 mm thick high density craft paper honey comb board, sandwiched on both sides with prelaminated ABS sheet thickness of 1.5mm. PVC edge banding of size 0.45mm on the vertical sides. Hardware made out of steel coated butterfly hinges - 3 Nos. for each shutter and ISI make S.S round lock completes for finished item of work. Maximum shutter size of : 910 x 2030 mm |  |  |  |  | 26 | Sqm | 9241 | 240266 | 240266 | 0 |  | CS
12 | Providing and fixing factory made solid Wood Polymer Composite (WPC) single extruded Door Frame section of 100*65 MM with encapsulation of 6 MM rigid layer on all external surfaces. The door frame will have a rebate of 32MM/ 37 MM. The two Vertical members are to be joined together with the horizontal member using 8x75 MM long MS Star full thread screws to be used with reverse forward speed control hand drilling machine. The ready/assembled door frame is fixed to wall using Z Hand fast 300 MM long hold fast. Supplying and fixing of 28/30 mm thick Wood Plastic Composite (WPC) Door shutter, comprising of 70% virgin polymer, 15% wood powder (fiber), and the remaining 15% additives, comprising of virgin PVC polymer of K value 58-60 (Suspension grade), Calcium carbonate and natural fibers (wood powder) and non toxic additives (maximum toxicity index of 12 for 100 gms) having minimum door density of 650 kg/cum, screw withdrawal strength 1800N (Face) & 900N (Edge), Modulus of Elasticity 900N/mm2 and resistance to spread of flame of Class A category with property of being termite/borer poof, water/moisture proof and fire retardant and fixed in position with stainless steel butt hinges of required size with necessary full body threaded star headed counter sunk SS screws all as per direction of Engineer -in- Charge (SS butt hinges and SS screws shall be paid separately) |  |  |  |  | 6.5 | Sqm | 6734 | 43771 | 43771 | 0 |  | CS | 6.4
13 | 50 LPH storage type RO of dimensions 525 x 425 x 1450 mm (WxDxH) of approx. weight 75Kg consists of 4 nos of 80 GPD 3-layer Thin Film Composite (TFC) membrane with 0.0001-micron pore size which can prevent TDS, heavy metals and equipped with 6 stage purification process which reduces pesticides in the water for reducing scale formation when water is heated. The RO should take min input pressure of 0.6 kg/cm2, 2000 ppm of TDS in Water, 500 ppm of Hardness, 6.5 to 8.5 PH of water which can give output of 20 to 25 % recovery in purified water and can run on 230V AC, 50 Hz supply with operating temp of 5oC to 45oC. |  |  |  |  | 1 | Nos | 75000 | 75000 | 75000 | 0 |  | CS
14 | Supply of Sun Control film to the glazed windows (For Windows & Door view Windows) |  |  |  |  | 45 | Sqm | 381 | 17145 | 17145 | 0 |  | CS
15 | Supply of Venetian blinds Vertical blinds 100 mm wide with all accessories. (For semen collection room & Counselling room Windows) |  |  |  |  | 15 | Sqm | 2187 | 32805 | 32805 | 0 |  | CS
16 | Supply and fixing of Dress Hangers of size 450mm length with 8 Nos hooks, each capped with plastic protective cap (in change rooms). |  |  |  |  | 5 | Nos | 510 | 2550 | 2550 | 0 |  | CS
17 | Supplying and fixing Rectangular Mirror Frameless of size 457 .2 mm x 609.6 mm (For Change room) |  |  |  |  | 5 | Nos | 1775 | 8875 | 8875 | 0 |  | CS
18 | Name Plates (Room Names) as approved by the Engineer In-charge. |  |  |  |  | 30 | Nos | 600 | 18000 | 18000 | 0 |  | CS
19 | AHU shed with provision for fencing, door with lock- key arrangement shall be provided with Framework vertically made of MS Square Pipe frame: 2 Inches X 2 Inches, 16Gauge M S Fencing with wire mesh: ½ inch X ½inch. Supporting Structure M S Angle: 50 X 5mm GI pre-coated corrugated profile roof sheet: 0.5 mm thick duly supported with JHook 10 SWG with provision of door with lock and key AHU Shed with fencing should be duly enamel painted and with anti-rust coating from both sides. |  |  |  |  | 1 | Job | 300000 | 300000 | 300000 | 0 |  | CS
20 | Providing Thermo Mechanically Treated ( TMT) ( Fe-500/500D/550D from primery producer TATA, SAIL, VSP, JSW Steel, Goel steel, Jindal panther, X- Vega & balaji Shakthi as per IS 1786-2008) of Different Diameters RCC Works , including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and sizes and typing and lap - spacing with binding wire of 18 SWG, Forming grills for reinforcement work as per approved design and drawings, including and conveyanace of steel bars, including all wastages such as overlaps, coupling, chairs, spacer bars including cost and conveyance of binding wire cover blocks and incidential, operational, labour charges such as cutting bending, placing in position, typing incliding sales and other taxes on all materials etc., and overheads & contractors profit completefor finished item of work |  |  |  |  | 0.3 | MT | 95386 | 28616 | 28616 | 0 |  | CS
21 | Supplying and fixing of to windows / in open court yards using 25mm x 6mm MS flat alround and 10mm MS square bars horizontally at 125mm centre to centre and vertically at 300mm centre to centre including fixing with 4 Nos of MS Z holdfasts (2 on each side) duly making cutting brick masonry, fixing and making to original surface neatly and painting grill with one coat of red oxide primer including cost all taxes and conveyance of all materials including cutting, bending, welding including all operational charges and all labour charges etc., complete for finished item of work. |  |  |  |  | 26 | Sqm | 1791 | 46566 | 46566 | 0 |  | CS | 25.92
22 | Supply and placing of the Design Mix Concrete M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Weight Batcher / Concrete mixer with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials, centering using Casurina Ballies, Bamboos, Wooden Reapers, Runners, Wood Posts, Steel Plates etc., including all operational, incidental and labour charges such as weigh batching, machine mixing, lifting of concrete manually, laying concrete, curing, overheads & contractors profit etc., complete but excluding cost of steel and its fabrication charges for finished item of work (APSS No. 402) |  |  |  |  | 0.75 | Cum | 14683 | 11012 | 11012 | 0 |  | CS
23 | Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free fullbody porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707) |  |  |  |  | 475 | Rmt | 151 | 71725 | 71725 | 0 |  | CS
[8 empty] | PART-B | 920706 | 920706 | 0 | 920706
|  |  |  | As Per Agreement | 0 |  |  | Excess | 920706
|  |  |  | As Per Workdone | 920706 |  |  | Less | 0
|  |  |  | Net Difference | 920706 |  |  | Net Difference | 920706
PLUMBING SUPPLIMENTAL
24 | Supplying and fixing 50 mm Nominal Bore GI pipe Medium Grade properties & weight as per IS 1239 in ground or on wall with GI fittings such as elbows tees couplings, nipples, plugs including excavation for trenches and refilling the trenches ,chiselling masonry walls and making good the walls & floors to the original surface and fixing MS clamps on TW blocks on walls including cost and conveyance of all materials and labour charges , overheads & contractors profit complete for finished item of work except for GI bends union and GI connectors with checkout and socket Tata or Zenith make or equivalent. (For Autoclave) |  |  |  |  | 15 | Rmt | 599 | 8985 | 8985 | 0 |  | PS
[8 empty] | PART-B | 8985 | 8985 | 0 | 8985
|  |  |  | As Per Agreement | 0 |  |  | Excess | 8985
|  |  |  | As Per Workdone | 8985 |  |  | Less | 0
|  |  |  | Net Difference | 8985 |  |  | Net Difference | 8985
ELECTRICAL SUPPLIMENTAL
25 | Supply and Transportation 56W Clean room Light fixture, 2' x2' (600mm x600mm) LED luminaire CRCA powder coated white after phosphocreatine treatment provided as standard. with high efficiency acrylic wide diffuser, with wide operating voltage range, Power factor > 0.9, Surge protection >2KV, System efficacy of >100 lumens/watt, CCT: 3000K - 6500K as desired by the department, CRI >80, and THD is less than 15% etc., complete. Make: Philips |  |  |  |  | 12 | Nos | 17241 | 206892 | 206892 | 0 |  | ES
ES
26 | Supply and Transportation of 48" ( 1200 mm) High Speed Fan Sweep Celing Fan with all accessories etc., complete. Make Havells S S 390 |  |  |  |  | 32 | Nos | 4317 | 138144 | 138144 | 0 |  | ES
ES
27 | Labour charges for fixing of ceiling fan and regulator including transportation and giving connections with twin core wire etc., complete. |  |  |  |  | 32 | Nos | 185 | 5920 | 5920 | 0 |  | ES
ES
28 | Supply and fixing of Anchor fastner with fan hook / Providing MS Fan hook with grouting and cement plastering. |  |  |  |  | 32 | Nos | 122 | 3904 | 3904 | 0 |  | ES
ES
29 | Supply & fixing of 2nos6A, 2 in one socket - 2 Nos with 6A switch control - 2 Nos modular type with and GI switch box with front cover plate including all labour charges etc., complete. Makes of switches: -Hooney well Benz Plus |  |  |  |  | 23 | Nos | 1178 | 27094 | 27094 | 0 |  | ES
ES
30 | Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete |  |  |  |  | 32 | Nos | 162 | 5184 | 5184 | 0 |  | ES
ES
31 | Supply and fixing of 12 Way SPN DB Horizontal with IP 43 Protection as per IS:13032 Makes: Legrand and Supply and Fixing of 1 No., of 63A FP MCB as incomer and 8 Nos 6-32 A 10kA SP MCBs Makes: Legrand-DX3 as out goings including internal connections and labour charges for FLUSH Mounting etc., complete. (For UPS DBs) |  |  |  |  | 1 | Nos | 9444 | 9444 | 9444 | 0 |  | ES
ES
32 | Supply and fixing of cable adopteres box with cover for DBs including, massanory work etc., complete., |  |  |  |  | 10 | Nos | 5085 | 50850 | 50850 | 0 |  | ES
ES
33 | Supply and fixing of FP Metal Enclosure with IP 20 Protection DB Make with 1 No 63A, 10 KA DP MCB including internal connection and labour charges for Flush Mounting etc.,complete. Makes of Enclousure : Legrand MCB Makes : Legrand-DX3 |  |  |  |  | 1 | Nos | 4203 | 4203 | 4203 | 0 |  | ES
ES
34 | Supply and fixing of suitable out door feeder piller box of size made with 14 SWG CRCA sheet with double door arrangement, making powder coating after processing of 7 Tank process, lock and key, hinges, rubber gasket, danger board,suitable angle iron stand for mounting the feeder pillar with cement concrete, including Supply and fixing of Legrand / Schnieder make as out goings, indication lamps, din channel, 6 Sqmm 3 core copper cable for invidual light control, connectors, bus bars, shroudings, gland plates and provision for 3 phase energy meter etc., complete for finished item of work and suitable wiring provision for connecting the nature switch with following.63A, 4 Pole MCB as incomer, 9 Nos 6-32A SP MCBs |  |  |  |  | 1 | No | 35000 | 35000 | 35000 | 0 |  | ES
[8 empty] | PART-B | 486635 | 486635 | 0 | 486635
|  |  |  | As Per Agreement | 0 |  |  | Excess | 486635
|  |  |  | As Per Workdone | 486635 |  |  | Less | 0
|  |  |  | Net Difference | 486635 |  |  | Net Difference | 486635
FIRE FIGHTING SUPPLIMENTAL
35 | Supply, Installation, testing and commissioning of EN54-2 Listed and LPCB approved based analog addressable fire control panel expandable by minimum 2 additional loops with minimum 80 character LCD display 4 access levels 1000 events, historical logging, flash E-PROM, 240 volts A C Power supply, automatic battery charger, 24V SLA batteries suitable for operating the entire system including tack back units and the hooters / strobes for a minimum of 4 hours in battery condition the panel shall have suitable power amplifiers for hooter / strobes the panel shall be capable beeing integrated with the BMS system and shall include cost of supply, installation of any additional modules or interfaces required for the same. The panel shall be completed as per the specification and as required for fixing of above Micro processor based Fire Alarm control panel with zonal indictions and battery back up as per detailed specifications. Makes: Ravel |  |  |  |  | 1 | Nos | 291366 | 291366 | 291366 | 0 |  | FFS
[8 empty] | PART-B | 291366 | 291366 | 0 | 291366
|  |  |  | As Per Agreement | 0 |  |  | Excess | 291366
|  |  |  | As Per Workdone | 291366 |  |  | Less | 0
|  |  |  | Net Difference | 291366 |  |  | Net Difference | 291366
AIR CONDITIONING SUPPLIMENTAL
36 | Supply & Installation of MS Angle for Duct Support, Cable Tray Support and Condensing Unit Stand of size 50 X 50 x 5 mm Thick. |  |  |  |  | 200 | Kg | 190 | 38000 | 38000 | 0 |  | ACS
37 | Supply & Installation of MS Angle for Duct Support, Cable Tray Support and Condensing Unit Stand of size 32 X 32 x 5 mm Thick. |  |  |  |  | 75 | Kg | 190 | 14250 | 14250 | 0 |  | ACS
38 | Supply and installation of Canvas Connections For AHUS |  |  |  |  | 2 | Nos | 6500 | 13000 | 13000 | 0 |  | ACS
[8 empty] | PART-B | 65250 | 65250 | 0 | 65250
|  |  |  | As Per Agreement | 0 |  |  | Excess | 65250
|  |  |  | As Per Workdone | 65250 |  |  | Less | 0
|  |  |  | Net Difference | 65250 |  |  | Net Difference | 65250
MGPS SUPPLIMENTAL
39 | Fully Automatic Control Panel for Oxygen System: Supply, installation and commissioning of Fully Automatic control panel for unintrupted Oxygen supply |  |  |  |  | 1 | Set | 175180 | 175180 | 175180 | 0 |  | GS
40 | Trigas Emergency Manifold: SITC of Emergency Trigas Manifold maximum for 1+1 D-type Gas Cylinders complete with separate NRVs, tail pipes and brass fittings for each cylinders. |  |  |  |  | 1 | Set | 9620 | 9620 | 9620 | 0 |  | GS
41 | Fully Automatic Control Panel for Trigas System: Supply, installation and commissioning of Fully Automatic control panel for unintrupted Nirous Oxide supply. |  |  |  |  | 1 | Set | 175180 | 175180 | 175180 | 0 |  | GS
42 | Fully Automatic Control Panel for CO2 System: Supply, installation and commissioning of Fully Automatic control panel for unintrupted Nirous Oxide supply. |  |  |  |  | 1 | Set | 175180 | 175180 | 175180 | 0 |  | GS
43 | SITC of Medical Air-4 Outlet with matching probe as per HTM-2022/02-01 of UK/ NFPA 99C of USA as per enclosed technical Specification. |  |  |  |  | 6 | Nos | 12470 | 74820 | 74820 | 0 |  | GS
44 | 12 mm Valve for 12 mm OD Pipe Note: New item added |  |  |  |  | 3 | Nos. | 930 | 2790 | 2790 | 0 |  | GS
45 | Supply and installation of 46.7 liter size CO2 cylinders confirming to IS:7285 Part-2 (2017). The cylinder shall have an outer diameter of 232mm, a nominal length of 1365mm, and a minimum wall thickness of 5.3mm, ensuring robustness and safety during handling and storage. The cylinders shall have a capacity of 46.7 liters and comply with the standards set forth by the Indian Standards Institute. They shall be constructed from high-quality 37 Mn (Carbon Manganese) material, guaranteeing durability and reliability. The design shall feature a concave bottom and neck threading conforming to IS 3224:2002 14 TPI Type 4 - Size 2 specifications, facilitating secure connections and ease of use. The cylinder shall be capable of withstanding a test pressure of 250 BAR and have a working pressure of 150 BAR. The nominal tare weight of each cylinder shall be 51 kg. The cylinder includes first fill. |  |  |  |  | 2 | Nos | 20850 | 41700 | 41700 | 0 |  | GS
46 | Supply and installation of 46.7 liter size O2 cylinders confirming to IS:7285 Part-2 (2017). The cylinder shall have an outer diameter of 232mm, a nominal length of 1365mm, and a minimum wall thickness of 5.3mm, ensuring robustness and safety during handling and storage. The cylinders shall have a capacity of 46.7 liters and comply with the standards set forth by the Indian Standards Institute. They shall be constructed from high-quality 37 Mn (Carbon Manganese) material, guaranteeing durability and reliability. The design shall feature a concave bottom and neck threading conforming to IS 3224:2002 14 TPI Type 4 - Size 2 specifications, facilitating secure connections and ease of use. The cylinder shall be capable of withstanding a test pressure of 250 BAR and have a working pressure of 150 BAR. The nominal tare weight of each cylinder shall be 51 kg. The cylinder includes first fill. |  |  |  |  | 2 | Nos | 17850 | 35700 | 35700 | 0 |  | GS
47 | Supply and installation of 46.7 liter size Trigas cylinders confirming to IS:7285 Part-2 (2017). The cylinder shall have an outer diameter of 232mm, a nominal length of 1365mm, and a minimum wall thickness of 5.3mm, ensuring robustness and safety during handling and storage. The cylinders shall have a capacity of 46.7 liters and comply with the standards set forth by the Indian Standards Institute. They shall be constructed from high-quality 37 Mn (Carbon Manganese) material, guaranteeing durability and reliability. The design shall feature a concave bottom and neck threading conforming to IS 3224:2002 14 TPI Type 4 - Size 2 specifications, facilitating secure connections and ease of use. The cylinder shall be capable of withstanding a test pressure of 250 BAR and have a working pressure of 150 BAR. The nominal tare weight of each cylinder shall be 51 kg. The cylinder includes first fill. |  |  |  |  | 2 | Nos | 29250 | 58500 | 58500 | 0 |  | GS
48 | Supply and installation of 46.7 liter size N2O cylinders confirming to IS:7285 Part-2 (2017). The cylinder shall have an outer diameter of 232mm, a nominal length of 1365mm, and a minimum wall thickness of 5.3mm, ensuring robustness and safety during handling and storage. The cylinders shall have a capacity of 46.7 liters and comply with the standards set forth by the Indian Standards Institute. They shall be constructed from high-quality 37 Mn (Carbon Manganese) material, guaranteeing durability and reliability. The design shall feature a concave bottom and neck threading conforming to IS 3224:2002 14 TPI Type 4 - Size 2 specifications, facilitating secure connections and ease of use. The cylinder shall be capable of withstanding a test pressure of 250 BAR and have a working pressure of 150 BAR. The nominal tare weight of each cylinder shall be 51 kg. The cylinder includes first fill. |  |  |  |  | 2 | Nos | 33000 | 66000 | 66000 | 0 |  | GS
[8 empty] | PART-B | 814670 | 814670 | 0 | 814670
|  |  |  | As Per Agreement | 0 |  |  | Excess | 814670
|  |  |  | As Per Workdone | 814670 |  |  | Less | 0
|  |  |  | Net Difference | 814670 |  |  | Net Difference | 814670
Water Proofing Works
49 | Water Proofing on Terrace Floor |  |  |  |  | 1 | Job | 1500000 | 1500000 | 1500000 | 0 |  | WP
[8 empty] | PART-B | 1500000 | 1500000 | 0 | 1500000
[8 empty] | TOTAL PART-B | 4405212 | 4405212 | 0 | 4405212
[5 empty] | 43811081 |  |  | TOTAL | 52612253 | 10389309 | 1588137 | 8801172
[8 empty] | NETEXCESS | 8801172
| For Water Proofing Works |  |  | As Per Agreement | 0 |  |  | Excess | 1500000
|  |  |  | As Per Workdone | 1500000 |  |  | Less | 0
|  |  |  | Net Difference | 1500000 |  |  | Net Difference | 1500000
| For Total Part-B |  |  | As Per Agreement | 0 |  |  | Excess | 4405212
|  |  |  | As Per Workdone | 4405212 |  |  | Less | 0
|  |  |  | Net Difference | 4405212 |  |  | Net Difference | 4405212
| For Total Part-A+Part-B |  |  | As Per Agreement | 43811081 |  |  | Excess | 10389309
|  |  |  | As Per Workdone | 52612253 |  |  | Less | 1588137
|  |  |  | Net Difference | 8801172 |  |  | Net Difference | 8801172

## Part-C
PART-C
Interior Works As Per IVF Petlaburj
S.No | Item Description | UOM | Qty | Rate (Rs.) | Amount (Rs.) | Remarks
1 | High Quality IVF Procedural photos at Entrance and Reception | Nos | 12 | 9000 | 108000 | As Per IVF Petlaburj
2 | 60mm Thick Box framing as the back support for the name plate at Entrance | Sqm | 3.98 | 11012 | 43828 | As Per IVF Petlaburj
3 | Door Frame side Paneling at Entrance | Sqm | 7.551 | 9250 | 69847 | As Per IVF Petlaburj
4 | 32mm Double Flush Door (1800 x 2100 mm door) at Entrance | Nos | 1 | 56500 | 56500 | As Per IVF Petlaburj
5 | Name Plate With Glossy Laminate at Entrance | Sqm | 2.6 | 9580 | 24908 | As Per IVF Petlaburj
6 | MIRROR GOLD TITANIUM LETTERS & S.S. MIRROR LETTERS at Entrance | Job | 1 | 67500 | 67500 | As Per IVF Petlaburj
7 | Double side ACP sheet (Name board wth three languages fixed at IVF Entrance Corridor) | Nos | 1 | 6000 | 6000 | As Per IVF Petlaburj
8 | Foam Board (Name board wth three languages with direction to IVF Center fixed at 3rd floor) | Nos | 2 | 2800 | 5600 | As Per IVF Petlaburj
9 | Foam Board (Name board wth with direction to Rooms fixed to wall in IVF Corridor,) | Nos | 2 | 3200 | 6400 | As Per IVF Petlaburj
10 | Main IVF logo with LED arcylic board at Entrance | Nos | 1 | 11475 | 11475 | As Per IVF Petlaburj
11 | PVC frames on the walls for covering the area over DB Boxes | Sqm | 1 | 6473 | 6473 | As Per IVF Petlaburj
|  |  |  | Sub Total | 406531
|  |  |  | GST @ 18% | 73175.58
|  |  |  | Sub Total | 479706.58
|  |  |  | TGMSIDC Charges @5.11% | 24513
|  |  |  | Total | 504220

## Part-D
PART-D
Additional Items As Per IVF Gandhi
S.No | Description | QTY | UOM | Rate (Rs.) | Amount (Rs.) | Remarks
Equipment
1 | Fowler Two Function Bed with ABS Panel in Pre/Post Operative ward and Semen Collection room | 5 | Nos | 39000 | 195000 | As Per IVF Gandhi
2 | Bed side Table with ABS Plastic body construction in Pre/Post Operative ward and Semen Collection room | 5 | Nos | 9000 | 45000 | As Per IVF Gandhi
3 | Corporate Deluxe Locker with SS 304 grade Top in Sample collection and Injection room | 1 | Nos | 8400 | 8400 | As Per IVF Gandhi
4 | Bed side stand with full SS 304 grade constructionof in Sample collection and Injection room | 1 | Nos | 9300 | 9300 | As Per IVF Gandhi
5 | Bed side stand with full GI Powder coated construction in Semen collection room | 1 | Nos | 4200 | 4200 | As Per IVF Gandhi
6 | Sample collection chair in Sample collection and Injection room | 1 | Nos | 16200 | 16200 | As Per IVF Gandhi
7 | Cryo Can 11 Ltr without wheels In Cryo room | 1 | Nos | 32000 | 32000 | As Per IVF Gandhi
8 | Sample collection bed in Sample collection and Injection room | 1 | Nos | 29000 | 29000 | As Per IVF Gandhi
9 | The Multipurpose Electro Hydraulic Mobile OT Table in Major OT | 1 | Nos | 210000 | 210000 | As Per IVF Gandhi
|  |  |  | Sub Total | 549100
Furniture
10 | Hydraulic Door Closer for ABS Doors | 15 | Nos | 2819 | 42285 | As Per IVF Gandhi
11 | Writing board in Counselling rooms | 1 | Nos | 2100 | 2100 | As Per IVF Gandhi
12 | MDF wooden table in Reception and Ultrasound room | 2 | Nos | 14500 | 29000 | As Per IVF Gandhi
13 | 3 Seater Sofa | 2 | Nos | 24000 | 48000 | As Per IVF Gandhi
|  |  |  | Sub Total | 121385
|  |  |  | Total | 670485
|  |  |  | GST @ 18% | 120687
|  |  |  | Sub Total | 791172
|  |  |  | TGMSIDC Charges @5.11% | 40429
|  |  |  | Total | 831601
Interiors
14 | Supply and fixing of Wall paper as approved by the Engineer In-charge. | 3 | Nos | 5175 | 15525 | As Per IVF Gandhi
15 | 25X25 mm WPC corner L-Patties at the topper edge of the wall tile cladding | 15 | Rmt | 6473 | 97095 | As Per IVF Gandhi
16 | SS-ROSE GOLD corner & L-Patties at the SIDE edge of the wall tile cladding | 60 | Rmt | 230 | 13800 | As Per IVF Gandhi
17 | 14mm thick Indoor WPC louvers | 15 | Sqm | 1500 | 22500 | As Per IVF Gandhi
18 | Praviding and fixing WPC Louvers to the Celling | 40 | Sqm | 15500 | 620000 | As Per IVF Gandhi
19 | Providing and fixing of wooden box celling at the top of Reception table | 40 | Sqm | 17450 | 698000 | As Per IVF Gandhi
20 | Back Pannelling with laminate Finish of 1 mm thick | 6 | Sqm | 11335 | 68010 | As Per IVF Gandhi
|  |  |  | Sub Total | 1534930
|  |  |  | Total | 2205415
|  |  |  | GST @ 18% | 396975
|  |  |  | Sub Total | 2602390
|  |  |  | TGMSIDC Charges @5.11% | 132982
|  |  |  | Total | 2735372

## Part-E
PART-E
Extra Items As Per End User Letter
Sno | Description | Qty | UOM | Rate (Rs.) | Amount (Rs.) | Remarks
1 | Consultant Chair in Embryologist and Anesthetist room | 3 | Nos | 20000 | 60000 | Extra Items
2 | Patient Chair Embryologist and Anesthetist room | 6 | Nos | 13500 | 81000 | Extra Items
3 | Lab Chairs Type I (DCA Price) in Andrology Lab & Embryology Lab | 10 | Nos | 15340 | 153400 | Extra Items
4 | IUI Couch/ Table in IUI Room | 2 | Nos | 50000 | 100000 | Extra Items
5 | office table in Embryologist room | 1 | Nos | 16000 | 16000 | Extra Items
6 | Patient Seating 3 in 1 model in waiting area | 3 | Nos | 38500 | 115500 | Extra Items
|  |  |  | Sub Total | 525900
|  |  |  | GST | 94662
|  |  |  | Sub Total | 620562
|  |  |  | TSMSIDC Charges, NAC & Labour Cess @ 5.11% | 31711
|  |  |  | Grand Total | 652273

## ABSTRACT
Name of the work: Design, fabrication, establishing & commissioning of In-Vitro Fertility Centers (IVFCs) along with allied services on Turnkey basis at Gandhi Hospital, Secunderabad, MGM Hospital, Warangal & MGMH Petlaburj, Hyd.
COMPARITIVE STATEMENT FOR GENERAL ABSTRACT
S.No | Description |  | As per Agreement | As per workdone/To be done | Excess | Less | Remarks
1 | Equipment |  | 26020476 | 26020476 | 0 | 0
2 | Civil Works |  | 7320696 | 9771662 | 2450966 | 0
3 | Plumbing works |  | 160285 | 156101 | 0 | 4184
4 | Electrical works |  | 3832437 | 5402274 | 1569837 | 0
5 | ELV works |  | 1337000 | 1337000 | 0 | 0
6 | Fire Fighting works |  | 225880 | 225880 | 0 | 0
7 | Air Conditioning works |  | 3888485 | 4247076 | 358591 | 0
8 | MGPS works |  | 1025822 | 1046572 | 20750 | 0
| Sub Total (Agreement Part-A) |  | 43811081 | 48207041 | 4400144 | 4184
9 | Equipment supplimental |  | 0 | 317600 | 317600 | 0
10 | Civil supplimental works |  | 0 | 920706 | 920706 | 0
11 | Plumbing supplimental works |  | 0 | 8985 | 8985 | 0
12 | Electrical supplimental works |  | 0 | 486635 | 486635 | 0
13 | Fire Fighting supplimental works |  | 0 | 291366 | 291366 | 0
14 | Air Conditioning supplimental works |  | 0 | 65250 | 65250 | 0
15 | MGPS supplimental works |  | 0 | 814670 | 814670 | 0
| Water Proofing Works |  | 0 | 1500000 | 1500000 | 0
| Sub Total (Supplimental Part-B) |  | 0 | 4405212 | 4405212 | 0
| Total (Part-A+Part-B) |  | 43811081 | 52612253 | 8805356 | 4184
16 | Provision towards Engineering Supervision Charges @ 4% on RE Value | 4% | 1752443.24 | 2104490.12 | 352047 | 0
| GST @ 18% |  | 8201434.3632 | 9470205.54 | 1268771 | 0
|  |  | 53764958.6032 | 64186948.66 | 10426174 | 4184
17 | Labour Cess @ 1% on Basic Price of Revised Estimate | 1% |  | 526122.53 | 526123 | 0
18 | NAC @ 0.1% on Basic Price of Revised estimate | 0.1% |  | 52612.253 | 52612 | 0
19 | Provision towards Seniorage Charges on Civil Component |  |  | 1001 | 1001 | 0
20 | Provision towards DMF Charges 30% on Seniorage Charges | 30% |  | 300.3 | 300 | 0
21 | Provision towards SMFT Charges 2% on seniorage Charges | 2% |  | 20.02 | 20 | 0
22 | Provision towards Haritha Nidhi | 0.01% |  | 5261.2253 | 5261 | 0
23 | Sub total of S.No 14 to 18 |  |  | 585317.3283 | 585317 | 0
24 | Provision towards GST 18% on Seniorage Charges | 18% |  | 105357.1191 | 105357 | 0
25 | Provision towards Unforseen items and rounding off (LS) - Inaugration Expenses |  |  | 200000 | 200000 | 0
| Sub total of S.No 22 to 25 |  |  | 890674.4474 | 890674 | 0
|  |  | 53764958.6032 | 65077623.1074 | 11316848 | 4184

## SEIGNORAGE
S.No | Item Name | UOM | QTY | QTY |  |  | Co-efficients |  |  | Rates |  |  | Amount |  |  | Total Amount
|  |  |  | Sand (QTY) | Metal (QTY) | Brick (QTY) | Sand | Metal | Bricks | Sand Rate | Metal Rate | Brick Rate | Sand Amount | Metal Amount | Brick Amount
1 | Brick masonry for panel walls in superstructure with CM 1:8 prop: Aerated Cellular Autoclaved Concrete Blocks conforming to IS:2185 Part-3 - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600 x 200 x 200 mm including cost and conveyance of all materials like cement, screened sand, bricks, water etc., to site, including sales and other taxes on all materials and such as labour charges, like mixing cement mortar, scaffolding charges, constructing masonry, lift charges, curing, etc.,complete for finished item of work. TSSS No.501 and 504. 2nd Floor at MGM Warangal | 77.69 | Cum | 13.6294 |  | 5513.4483 | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 239.8773 | 0 | 169.3731 | 409
2 | Reinforced Masonry for partition walls 100 mm thick in CM 1:4 prop. Aerated Cellular Autoclaved Concrete Blocks conforming to IS:2185 Part-3 - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600 x 200 x 100 mm and placing 2Nos. of 6mm M.S plain rods in every third layer with free ends of the reinforcement pegged into mortar joints of main brick walls where applicable including cost and conveyance of all materials like cement, steel, sans, brick, water etc., to site, including sales and other taxes excluding GST on all materials, all operational, incidents charges, constructing masonry, lift charges, curing, complete for finished item of work. TSSS No. of 509. 2nd Floor at MGM Warangal | 324.93 | Sqm | 5.1303 |  | 2305.94 | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 90.2935 | 0 | 70.8385 | 161
3 | Providing Mild steel MS steel bars Fe 250 grade as per IS 432 of different diameters including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying including sales and other taxes on all materials etc. , complete for finished item of work. TSSS No.126 For RBM walls 6mm dia: 2nd Floor at MGM Warangal | 0 | MT |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
4 | Plastering 20mm thick in two coats using screened sand with base coat of 16mm thick in CM1:6 and top coat of 4mm thick in CM1:4 with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales and other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., complete for finished item of work SS 901,903and 904 2ND Floor at MGM Warangal | 182.18 | Sqm | 4.0983 |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 72.1305 | 0 | 0 | 72
5 | Plastering 12mm thick in two coats using screened sand with base coat of 8mm thick in CM 1:6 and top coat of 4mm thick in CM 1:4 with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales and other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and complete for finished item of work. SS 901,903 and 904. 2ND Floor at MGM Warangal | 1415.32 | Sqm | 18.9313 |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 333.1912 | 0 | 0 | 333
6 | Providing and laying screed plain cement concrete as per site condition for floor bedding using high quality aggregates including base preparation, compaction, levelling, all lead and lifts, rough finishing at the top surface, curing, shuttering if necessary etc., complete as directed . at MGM Warangal | 0 | Sqm |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
7 | Providing Thermo Mechanically Treated ( TMT) ( Fe-500/500D/550D from primery producer TATA, SAIL, VSP, JSW Steel, Goel steel, Jindal panther, X- Vega & balaji Shakthi as per IS 1786-2008) of Different Diameters RCC Works , including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and sizes and typing and lap - spacing with binding wire of 18 SWG, Forming grills for reinforcement work as per approved design and drawings, including and conveyanace of steel bars, including all wastages such as overlaps, coupling, chairs, spacer bars including cost and conveyance of binding wire cover blocks and incidential, operational, labour charges such as cutting bending, placing in position, typing incliding sales and other taxes on all materials etc., and overheads & contractors profit completefor finished item of work | 0.3 |  |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
8 | Supply and placing of the Design Mix Concrete M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Weight Batcher / Concrete mixer with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials, centering using Casurina Ballies, Bamboos, Wooden Reapers, Runners, Wood Posts, Steel Plates etc., including all operational, incidental and labour charges such as weigh batching, machine mixing, lifting of concrete manually, laying concrete, curing, overheads & contractors profit etc., complete but excluding cost of steel and its fabrication charges for finished item of work (APSS No. 402) | 0.75 |  | 0.1875 | 0.375 |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 3.3 | 22.5 | 0 | 26
|  |  |  | 41.9768 | 0.375 | 7819.3883 | [8 empty] | Total | 1001
[5 empty] | Brick Masonary |  | Partition walls |  | Plastering 20 mm |  | Plastering 12 mm |  | M25
[5 empty] | Proportion | 1:08 |  | 324.93 | QTY | 182.18 | Qty | 1415.32 | Qty | 0.75
[5 empty] | QTY | 77.69 | QTY | 32.493 |  | 2.9149 |  | 11.3226 | Ratio | 1:01
[5 empty] | V of 1 brick | 0.014091 | Ratio | 1:04 | dry v | 3.8768 | dry v | 15.059 | sand | 0.1875
[5 empty] | no of bricks | 5513.4483 | V of 1 brick | 0.014091 | Ratio | 1:06 | Ratio | 1:06 | Metal | 0.375
[5 empty] | v of 1 brick | 0.012 | no of bricks | 2305.94 | cement | 0.55383 | cement | 2.1513
[5 empty] | qty | 66.1614 | v of 1 brick | 0.012 | sand | 3.323 | sand | 12.9077
[5 empty] | mortor qty | 11.5286 | qty | 27.6713 | Ratio | 1:04 | Ratio | 1:04
[5 empty] | dry v | 15.3331 | mortor qty | 4.8217 |  | 0.72872 |  | 5.6613
[5 empty] | Cement | 1.7037 | dry v | 6.4129 | dry v | 0.9692 | dry v | 7.5295
[5 empty] | Sand | 13.6294 | Cement | 1.2826 | cement | 0.19384 | cement | 1.5059
[7 empty] | Sand | 5.1303 | sand | 0.77536 | sand | 6.0236
[9 empty] | T sand qty | 4.0983 | T sand qty | 18.9313

## SEIGNORAGE (2)
S.No | Item Name | UOM | QTY | QTY |  |  | Co-efficients |  |  | Rates |  |  | Amount |  |  | Total Amount
|  |  |  | Sand (QTY) | Metal (QTY) | Brick (QTY) | Sand | Metal | Bricks | Sand Rate | Metal Rate | Brick Rate | Sand Amount | Metal Amount | Brick Amount
1 | Brick masonry for panel walls in superstructure with CM 1:8 prop: Aerated Cellular Autoclaved Concrete Blocks conforming to IS:2185 Part-3 - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600 x 200 x 200 mm including cost and conveyance of all materials like cement, screened sand, bricks, water etc., to site, including sales and other taxes on all materials and such as labour charges, like mixing cement mortar, scaffolding charges, constructing masonry, lift charges, curing, etc.,complete for finished item of work. TSSS No.501 and 504. 2nd Floor at MGM Warangal | 77.69 | Cum | 13.6294 |  | 5513.4483 | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 239.8773 | 0 | 169.3731 | 409
2 | Reinforced Masonry for partition walls 100 mm thick in CM 1:4 prop. Aerated Cellular Autoclaved Concrete Blocks conforming to IS:2185 Part-3 - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600 x 200 x 100 mm and placing 2Nos. of 6mm M.S plain rods in every third layer with free ends of the reinforcement pegged into mortar joints of main brick walls where applicable including cost and conveyance of all materials like cement, steel, sans, brick, water etc., to site, including sales and other taxes excluding GST on all materials, all operational, incidents charges, constructing masonry, lift charges, curing, complete for finished item of work. TSSS No. of 509. 2nd Floor at MGM Warangal | 324.93 | Sqm | 5.1303 |  | 2305.94 | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 90.2935 | 0 | 70.8385 | 161
3 | Providing Mild steel MS steel bars Fe 250 grade as per IS 432 of different diameters including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying including sales and other taxes on all materials etc. , complete for finished item of work. TSSS No.126 For RBM walls 6mm dia: 2nd Floor at MGM Warangal | 0 | MT |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
4 | Plastering 20mm thick in two coats using screened sand with base coat of 16mm thick in CM1:6 and top coat of 4mm thick in CM1:4 with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales and other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., complete for finished item of work SS 901,903and 904 2ND Floor at MGM Warangal | 182.18 | Sqm | 4.0983 |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 72.1305 | 0 | 0 | 72
5 | Plastering 12mm thick in two coats using screened sand with base coat of 8mm thick in CM 1:6 and top coat of 4mm thick in CM 1:4 with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales and other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and complete for finished item of work. SS 901,903 and 904. 2ND Floor at MGM Warangal | 1415.32 | Sqm | 18.9313 |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 333.1912 | 0 | 0 | 333
6 | Providing and laying screed plain cement concrete as per site condition for floor bedding using high quality aggregates including base preparation, compaction, levelling, all lead and lifts, rough finishing at the top surface, curing, shuttering if necessary etc., complete as directed . at MGM Warangal | 0 | Sqm |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
7 | Providing Thermo Mechanically Treated ( TMT) ( Fe-500/500D/550D from primery producer TATA, SAIL, VSP, JSW Steel, Goel steel, Jindal panther, X- Vega & balaji Shakthi as per IS 1786-2008) of Different Diameters RCC Works , including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and sizes and typing and lap - spacing with binding wire of 18 SWG, Forming grills for reinforcement work as per approved design and drawings, including and conveyanace of steel bars, including all wastages such as overlaps, coupling, chairs, spacer bars including cost and conveyance of binding wire cover blocks and incidential, operational, labour charges such as cutting bending, placing in position, typing incliding sales and other taxes on all materials etc., and overheads & contractors profit completefor finished item of work | 0.3 |  |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
8 | Supply and placing of the Design Mix Concrete M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Weight Batcher / Concrete mixer with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) from approved quarry including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials, centering using Casurina Ballies, Bamboos, Wooden Reapers, Runners, Wood Posts, Steel Plates etc., including all operational, incidental and labour charges such as weigh batching, machine mixing, lifting of concrete manually, laying concrete, curing, overheads & contractors profit etc., complete but excluding cost of steel and its fabrication charges for finished item of work (APSS No. 402) | 0.75 |  | 0.1875 | 0.375 |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 3.3 | 22.5 | 0 | 26
|  |  |  | 41.9768 | 0.375 | 7819.3883 | [8 empty] | Total | 1001
[5 empty] | Brick Masonary |  | Partition walls |  | Plastering 20 mm |  | Plastering 12 mm |  | M25
[5 empty] | Proportion | 1:08 |  | 324.93 | QTY | 182.18 | Qty | 1415.32 | Qty | 0.75
[5 empty] | QTY | 77.69 | QTY | 32.493 |  | 2.9149 |  | 11.3226 | Ratio | 1:01
[5 empty] | V of 1 brick | 0.014091 | Ratio | 1:04 | dry v | 3.8768 | dry v | 15.059 | sand | 0.1875
[5 empty] | no of bricks | 5513.4483 | V of 1 brick | 0.014091 | Ratio | 1:06 | Ratio | 1:06 | Metal | 0.375
[5 empty] | v of 1 brick | 0.012 | no of bricks | 2305.94 | cement | 0.55383 | cement | 2.1513
[5 empty] | qty | 66.1614 | v of 1 brick | 0.012 | sand | 3.323 | sand | 12.9077
[5 empty] | mortor qty | 11.5286 | qty | 27.6713 | Ratio | 1:04 | Ratio | 1:04
[5 empty] | dry v | 15.3331 | mortor qty | 4.8217 |  | 0.72872 |  | 5.6613
[5 empty] | Cement | 1.7037 | dry v | 6.4129 | dry v | 0.9692 | dry v | 7.5295
[5 empty] | Sand | 13.6294 | Cement | 1.2826 | cement | 0.19384 | cement | 1.5059
[7 empty] | Sand | 5.1303 | sand | 0.77536 | sand | 6.0236
[9 empty] | T sand qty | 4.0983 | T sand qty | 18.9313