## seignorage (hidden)
S.No | Item S.No | Item Code | Item Name | UOM | QTY | QTY |  |  | Co-efficients |  |  | Rates |  |  | Amount |  |  | Total Amount
[6 empty] | Sand (QTY) | Metal (QTY) | Brick (QTY) | Sand | Metal | Bricks | Sand Rate | Metal Rate | Brick Rate | Sand Amount | Metal Amount | Brick Amount
1 | 49 | IVF049 | Dismantling, clearing away and carefully stacking useful materials for re- use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges, etc., complete. Brick Masonry at Gandhi Hospital | Cum | 32.677 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
2 | 50 | IVF050 | Dismantling doors, windows and clear storey windows, Ventilators etc., wood or steel shutters including Chowkhats, architraves, hold fasts and other attachments etc., and stacking them within 100m lead including labour charge etc., and complete for finished item of work. Not exceeding 3 sqm in area: Doors 1.00x2.60M at Gandhi Hospital | No | 2 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
3 | 51 | IVF051 | Dismantling doors, windows and clear storey windows, Ventilators etc., wood or steel shutters including Chowkhats, architraves, hold fasts and other attachments etc., and stacking them within 100m lead including labour charge etc., and complete for finished item of work. Exceeding 3 sqm in area: Doors 1.50x2.60M at Gandhi Hospital | No | 5 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
4 | 52 | IVF052 | Conveyance of un-useful excavated earth to a distance of 21 KM for disposal including hire charges of T and P, labour charges etc., complete for finished item of work. Dismantled Brick masonry at Gandhi Hospital | Cum | 48.7 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
5 | 53 | IVF053 | Brick masonry for panel walls in superstructure with CM 1:8 prop: Aerated Cellular Autoclaved Concrete Blocks conforming to IS:2185 Part-3 - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600 x 200 x 200 mm including cost and conveyance of all materials like cement, screened sand, bricks, water etc., to site, including sales and other taxes on all materials and such as labour charges, like mixing cement mortar, scaffolding charges, constructing masonry, lift charges, curing, etc.,complete for finished item of work. TSSS No.501 and 504. 5th Floor at Gandhi Hospital | Cum | 15.27 | 2.67 |  | 1084 | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 46.992 | 0 | 33.3005 | 80.2925
7 | 54 | IVF054 | Reinforced Masonry for partition walls 100 mm thick in CM 1:4 prop. Aerated Cellular Autoclaved Concrete Blocks conforming to IS:2185 Part-3 - 1984 and IS:6441-1972 of Compressive strength 3 N/mm2 600 x 200 x 100 mm and placing 2Nos. of 6mm M.S plain rods in every third layer with free ends of the reinforcement pegged into mortar joints of main brick walls where applicable including cost and conveyance of all materials like cement, steel, sans, brick, water etc., to site, including sales and other taxes excluding GST on all materials, all operational, incidents charges, constructing masonry, lift charges, curing, complete for finished item of work. TSSS No. of 509.5th Floor at Gandhi Hospital | Sqm | 191.03 | 3.01 |  | 1356 | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 52.976 | 0 | 41.6563 | 94.6323
8 | 55 | IVF055 | Providing Mild steel MS steel bars Fe 250 grade as per IS 432 of different diameters including labour charges for straightening, cutting, bending to required sizes and shapes, placing in position with cover blocks of approved materials and size and tying and lap-splicing with binding wire of 18 SWG, forming grills for reinforcement work as per approved designs and drawings, including cost and conveyance of steel bars, including all wastages such as overlaps, couplings, chairs, spacer bars including cost and conveyance of binding wire, cover blocks and all incidental, operational, labour charges such as cutting, bending, placing in position, tying including sales and other taxes on all materials etc. , complete for finished item of work. TSSS No.126 For RBM walls 6mm dia: 5th Floor at Gandhi Hospital | MT | 0.1 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
9 | 56 | IVF056 | Plastering 20mm thick in two coats using screened sand with base coat of 16mm thick in CM1:6 and top coat of 4mm thick in CM1:4 with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales and other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., complete for finished item of work .SS 901,903and 904 5th Floor at Gandhi Hospital | Sqm | 11.04 | 0.248 |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 4.3648 | 0 | 0 | 4.3648
10 | 57 | IVF057 | Plastering 12mm thick in two coats using screened sand with base coat of 8mm thick in CM 1:6 and top coat of 4mm thick in CM 1:4 with dubara sponge finishing including cost and conveyance of all materials like cement, sand, water etc., to site, including sales and other taxes on all materials, and all operational, incidental charges on materials and including cost of all labour charges for mixing mortar, finishing, scaffolding, lift charges, curing, including cutting grooves as directed by Engineer-in-charge etc., and complete for finished item of work. SS 901,903 and 904. 5th Floor at Gandhi Hospital | Sqm | 547.15 | 7.31 |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 128.656 | 0 | 0 | 128.656
12 | 59 | IVF059 | Providing and laying screed plain cement concrete as per site condition for floor bedding using high quality aggregates including base preparation, compaction, levelling, all lead and lifts, rough finishing at the top surface, curing, shuttering if necessary etc., complete as directed . at Gandhi Hospital | Cum | 0 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
39 | 15 | IVF015 | Dismantling of unreinforced cement concrete, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete | [5 empty] | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
40 | 16 | IVF016 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete Old Cement Mortor (Plaster) | [5 empty] | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
41 | 17 | IVF017 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Executive Engineer duly taking actual premeasurements before dismantling including all labour charges , overheads & contractor profit etc., complete. Reinforced Cement Concrete | [5 empty] | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
42 | 18 | IVF018 | Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707) | [5 empty] | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
308
[6 empty] | Brick Masonary |  | Partition walls |  | Plastering 20 mm |  | Plastering 12 mm
[6 empty] | Proportion | 1:08 |  | 191.03 | QTY | 11.04 | Qty | 547.15
[6 empty] | QTY | 15.27 | QTY | 19.103 |  | 0.17664 |  | 4.3772
[6 empty] | V of 1 brick | 0.014091 | Ratio | 1:04 | dry v | 0.23493 | dry v | 5.8217
[6 empty] | no of bricks | 1083.6704 | V of 1 brick | 0.014091 | Ratio | 1:06 | Ratio | 1:06
[6 empty] | v of 1 brick | 0.012 | no of bricks | 1355.688 | cement | 0.033562 | cement | 0.83167
[6 empty] | qty | 13.004 | v of 1 brick | 0.012 | sand | 0.20137 | sand | 4.99
[6 empty] | mortor qty | 2.266 | qty | 16.2683 | Ratio | 1:04 | Ratio | 1:04
[6 empty] | dry v | 3.0137 | mortor qty | 2.8347 |  | 0.04416 |  | 2.1886
[6 empty] | Cement | 0.33486 | dry v | 3.7702 | dry v | 0.058733 | dry v | 2.9108
[6 empty] | Sand | 2.6789 | Cement | 0.75404 | cement | 0.011747 | cement | 0.58217
[8 empty] | Sand | 3.0162 | sand | 0.046986 | sand | 2.3287
[10 empty] | T sand qty | 0.24836 | T sand qty | 7.3187
555

## Revised Estimate-SECTIONS
REVISED ESTIMATE OF IVF-5TH FLOOR, MCH BUILDING, GANDHI HOSPITAL
S. No | Item S.No | Item Code | DESCRIPTION | As per Agreement |  |  |  | As per Work Done Estimate |  |  |  | EXCESS | REMARKS
|  |  |  | QTY | UNIT | RATE | AMOUNT RS. | QTY | UNIT | RATE | AMOUNT RS.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 15
Equipment Supplemental Works
1 |  |  | Fowler Two Function Bed with ABS Panel, and accessories in Pre/post Operative Ward and Semen Collection room | 0 | Nos |  |  | 5 | Nos | 39000 | 195000 | 195000 | This item is executed since it is required for ICMR Clearance. | EQPS
2 |  |  | Bed side Table with ABS Plastic body construction in Pre/post Operative Ward and Semen Collection room | 0 | Nos |  |  | 5 | Nos | 9000 | 45000 | 45000 | This item is executed since it is required for ICMR Clearance. | EQPS
3 |  |  | Corporate Deluxe Locker with SS 304 grade Top of size 508 x 406 x 762 mm in Sample and Injection room. | 0 | Nos |  |  | 1 | Nos | 8400 | 8400 | 8400 | This item is executed since it is required for ICMR Clearance. | EQPS
4 |  |  | Bed side stand with full SS 304 grade constructionof size 406 x 203 x 762 mm in Sample and Injection room. | 0 | Nos |  |  | 1 | Nos | 9300 | 9300 | 9300 | This item is executed since it is required for ICMR Clearance. | EQPS
5 |  |  | Bed side stand with full GI Powder coated constructionof size 406 x 203 x 762 mm in Semen Collection Room | 0 | Nos |  |  | 1 | Nos | 4200 | 4200 | 4200 | This item is executed since it is required for ICMR Clearance. | EQPS
6 |  |  | Cryo Can 11 Ltr without wheels in Cryo room | 0 | Nos |  |  | 1 | Nos | 32000 | 32000 | 32000 | This item is executed since it is required for ICMR Clearance. | EQPS
7 |  |  | 3-Bay Surgical Scrub Station/Sink with accessories at Sterile Corridor | 0 |  |  |  | 1 | Nos | 97000 | 97000 | 97000 | This item is executed since it is required for ICMR Clearance. | EQPS
8 |  |  | Supply of Sample collection bed of size 1850x620x700 mm in Sample and Injection room | 0 | Nos |  |  | 1 | Nos | 29000 | 29000 | 29000 | This item is executed since it is required for ICMR Clearance. | EQPS
9 |  |  | Supply of a Sample collection chair of size 800x580x700 mm in Sample and Injection room | 0 | Nos |  |  | 1 | Nos | 16200 | 16200 | 16200 | This chair is mandatory for a patient and executed since it is required for ICMR Clearance. | EQPS
10 |  |  | Supply and installation of Stainless Steel 304 grade CSSD Rectangular Working table of size 1200x480x1050 mm with in-built sink in Autoclave room | 0 | Nos |  |  | 1 | Nos | 46000 | 46000 | 46000 | An autoclave needs a CSSD table. Hence executed | EQPS
11 |  |  | Writing board made of Pressed wood coated with melamine surface in Counselling rooms | 0 | Nos |  |  | 2 | Nos | 2100 | 4200 | 4200 | This is mandatory as per ICMR guidelines, hence work is executed as per the instructions of Enduser. | EQPS
12 |  |  | Providing MDF 18 mm thick wooden table of size 900x450 mm at Reception and Ultrasound room | 0 | Nos |  |  | 2 | Nos | 14500 | 29000 | 29000 | This table is necessary to place the computer for ultrasound machine.hence item is executed. | EQPS
13 |  |  | Supply of a 3-seater sofa upholstered with PU leather, with a high-quality finish at Entrance corridor | 0 | Nos |  |  | 2 | Nos | 24000 | 48000 | 48000 | Executed as per instructions of higher officials & enduser. | EQPS
14 |  |  | SS-304 working table of size 685x685x762 mm in Embryology lab | 0 | Nos |  |  | 2 | Nos | 16300 | 32600 | 32600 | It is necessary to place the equipments hence, work is executed as per the instructions of Higher officials. | EQPS
15 |  |  | SS-304 working table of size 457x457x762 mm in Andrology Lab | 0 | Nos |  |  | 1 | Nos | 14500 | 14500 | 14500 | It is necessary to place the equipments hence, work is executed as per the instructions of Higher officials. | EQPS
16 |  |  | SS-304 working table of size 610x610x762 mm in in Andrology Lab | 0 | Nos |  |  | 1 | Nos | 15100 | 15100 | 15100 | It is necessary to place the equipments hence, work is executed as per the instructions of Enduser. | EQPS
17 |  |  | SS-304 working table of size 660x610x762 mm in Embryology Lab | 0 | Nos |  |  | 1 | Nos | 15800 | 15800 | 15800 | It is necessary to place the equipments hence, work is executed as per the instructions of Higher officials. | EQPS
18 |  |  | Supply and fixing of Powder coated GI stand with 4 nos height adjustable racks of size 670x410x1570 mm in IVF OT |  |  |  |  | 1 | Nos | 80000 | 80000 | 80000 | It is necessary to place the equipments hence, work is executed as per the instructions of Higher officials. this stand is necessary to place the Hysterscopy & Laproscopy set | EQPS
19 |  |  | The Multipurpose Electro Hydraulic Mobile OT Table in Major OT |  |  |  |  | 1 | Nos | 210000 | 210000 | 210000 | This work is executed as per the instructions of higher officials | EQPS
[7 empty] | 0 |  |  | PART-A | 931300 | 931300
CIVIL WORKS
20 | 51 | IVF051 | Dismantling doors, windows Exceeding 3 sqm in area: Doors 1.50x2.60M at Gandhi Hospital | 5 | No | 468 | 2340 | 7 | No | 468 | 3276 | 936 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
21 | 53 | IVF053 | Brick masonry for panel walls in superstructure with CM 1:8 prop: Aerated Cellular Autoclaved Concrete Blocks 5th Floor at Gandhi Hospital | 12 | Cum | 16055 | 192660 | 15.27 | Cum | 16055 | 245160 | 52500 | As per the site condition & floor plans approved, the Qty. exceeded and now proposed as AE | C
22 | 65 | IVF065 | Flooring with soluble salt porcelain vitrified tiles screen printed and polished of size 600 x 600 mm and thickness between 8 to 10mm at 5th Floor at Gandhi Hospital | 225 | Sqm | 1725 | 388125 | 374.81 | Sqm | 1725 | 646547 | 258422 | As per the site condition & floor plans approved, the Qty. exceeded and hence proposed as AE | C
23 | 68 | IVF068 | Providing dadooing to walls with glazed full body porcelain wall tiles of size 300 x 600 mm in 5th Floor at Gandhi Hospital | 40 | Sqm | 1423 | 56920 | 103.77 | Sqm | 1423 | 147665 | 90745 | As per the site condition and instructions of Higher officials, daddoing provided at corridor area near the reception. Hence the qty is exceeded and hence proposed as AE | C
24 | 90 | IVF090 | Single leaf clean room Doors : Size 900 X 2100 mm with 300 mm x 300 mm View panel at Gandhi Hospital | 1 | No | 28700 | 28700 | 3 | No | 28700 | 86100 | 57400 | As per the instructions of Higher officials Autoclave Room & UPS Room Mandates the scientific door, the Qty. exceeded and now proposed as AE | C
Civil Supplementary Works
25 |  |  | Supply and application of one coat water based cement primer of interior grade I for internal walls in 5th floor (for Ceiling) at Gandhi Hospital |  |  |  |  | 536.11 | Sqm | 85 | 45569 | 45569 | This work is executed as per the instructions of higher officials | CS
26 |  |  | Dismantling of unreinforced cement concrete |  |  |  |  | 3.89 | Cum | 4036 | 15700 | 15700 | The work was taken up as per approved floor plan drawings and in contingent with the main work and hence proposed as supplemental item. | CS
27 |  |  | Dismantling, clearing away of Old Cement Mortor (Plaster) |  |  |  |  | 37.13 | Sqm | 13 | 483 | 483 | The work was taken up as per approved floor plan drawings and in contingent with the main work and hence proposed as supplemental item. | CS
28 |  |  | Dismantling, clearing away of Reinforced Cement Concrete |  |  |  |  | 0.7 | Cum | 4424 | 3097 | 3097 | The work was taken up as per approved floor plan drawings and in contingent with the main work and hence proposed as supplemental item. | CS
29 |  |  | Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles |  |  |  |  | 107.18 | Rmt | 162 | 17363 | 17363 | This work was executed as per the requirement and instructions from higher officials | CS
30 |  |  | Providing of Factory made prelaminated FPVC (Foamed Polyvinyl Chloride) Door frame of the size 105x40mm with Maximum shutter size of : 910 x 2030 mm |  |  |  |  | 23.463 | Sqm | 9241 | 216822 | 216822 | To maitain low VOC in Fertility center, wooden doors are replaced with ABS doors as per MOM dated: 01-08-2023. (copy Attached) | CS
31 |  |  | Flooring with 16 to 18 mm thick high polished granite stone slabs black colour (for Reception Table). |  |  |  |  | 10.17 | Sqm | 5839 | 59383 | 59383 | This work is executed as per the TSMSIDC Higher officials in lieu of reception table. | CS
32 |  |  | 50 LPH storage type RO of dimensions 525 x 425 x 1450 mm in Autoclave room |  |  |  |  | 1 | Nos | 75000 | 75000 | 75000 | Autoclave needs clean water as per ICMR guidelines, hence this item is takenup. | CS
33 |  |  | Supply and placing of the Design Mix Concrete M 25 grade corresponding to IS 456 (for Lintels) |  |  |  |  | 0.43 | Cum | 15969 | 6867 | 6867 | This work is exectued as per site conditions. | CS
34 |  |  | Supply and fixing of Dress Hangers of size 450mm length with 8 Nos hooks (in change rooms). |  |  |  |  | 5 | Nos | 510 | 2550 | 2550 | This item is executed as requested by the Enduser. | CS
35 |  |  | Supplying and fixing Rectangular Mirror Frameless of size 457 .2 mm x 609.6 mm (For Change room) |  |  |  |  | 5 | Nos | 1775 | 8875 | 8875 | This item is executed as requested by the Enduser. | CS
36 |  |  | Supply of Venetian blinds Vertical blinds 100 mm wide with all accessories. (For semen collection room & Counselling room Windows) |  |  |  |  | 5.01 | Sqm | 2187 | 10957 | 10957 | This item is executed as requested by the Enduser. | CS
37 |  |  | Name Plates (Room Names) as approved by the Engineer In-charge. |  |  |  |  | 31 | Nos | 600 | 18600 | 18600 | This item is executed as requested by the Enduser. | CS
38 |  |  | Supply and fixing of High Quality IVF Procedural photos placed between two transparent acrylic boards fixed with studs at four corners to the PVC frame placed on DBs. (2' x 2' and above) (At Entrance and Entrance corridor) |  |  |  |  | 14 | Nos | 9000 | 126000 | 126000 | This work is executed as per the instructions of Enduser & TSMSIDC Higher Officials. | CS
39 |  |  | Providing, Fabricating and fixing full height V-board partitions of overall thickness of 75mm |  |  |  |  | 89.11 | Sqm | 1625 | 144804 | 144804 | This work is mandatory in contigent to the main work. Hence, executed. | CS
40 |  |  | Supply and fixing of doors as per approved drawings with (WPC) single extruded Door Frame section of 100*65 MM and30mm thick Wood Plastic Composite (WPC) Door shutter (800mm x 2100mm) (For Wash Rooms). |  |  |  |  | 6.72 | Sqm | 6734 | 45252 | 45252 | To maitain low VOC in Fertility center, wooden doors are replaced with WPC doors as per MOM dated: 01-08-2023. (copy Attached) | CS
41 |  |  | Wall Paneling 14mm thick Indoor WPC louvers providing & Fixing full height said 12mm SHERA Board panneling till slab with wooden framing in line and level including fling joints and joint calls and neccesary hardware (In Reception) |  |  |  |  | 18.58 | Sqm | 15500 | 287990 | 287990 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
42 |  |  | 2 WPC Louvers Ceiling Praviding and fixing WPC Louvers to the Celling in Reception |  |  |  |  | 7.58 | Sqm | 17450 | 132271 | 132271 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
43 |  |  | Providing and fixing of wooden box celling at the top of Reception table |  |  |  |  | 2.58 | Sqm | 11335 | 29244 | 29244 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
44 |  |  | Back Pannelling with laminate Finish of 1 mm thick Providing & Fixing full height solid 12mm BWF 710 GURIAN PLY Board panneling till slab in Reception |  |  |  |  | 7.5 | Sqm | 10500 | 78750 | 78750 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
45 |  |  | Providing and fixing ISI marked Magnetic 25mm Block Board door shutters for UPS room |  |  |  |  | 1 | Nos | 13800 | 13800 | 13800 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
46 |  |  | Providing and fixing PVC frames on the walls for covering the area over DB Boxes (At Entrance and Entrance corridor) |  |  |  |  | 4.45 | Sqm | 6473 | 28805 | 28805 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
47 |  |  | Providing and Fixing of (25X25) mm WPC corner L-Patties at the topper edge of the wall tile cladding |  |  |  |  | 38 | Rmt | 230 | 8740 | 8740 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
48 |  |  | Providing and Fixing of SS-ROSE GOLD corner & L-Patties at the SIDE edge of the wall tile cladding (At Entrance corridor) |  |  |  |  | 7 | Nos | 1500 | 10500 | 10500 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
49 |  |  | Providing and fixing of Door Frame panneling with 18mm BWP 710 Gurjan Ply and 8mm thick beeding half rounded on the both sides with 1mm thick laminate Finish with necessary handware and Polishing. (At Entrance) |  |  |  |  | 11.58 | Rmt | 2166 | 25082 | 25082 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
50 |  |  | Providing and fixing the 60mm Thick Box framing as the back support for the name plate installed of 18mm BWP 710 Gurjan and 1mm thick high glossy laminate finish (At Entrance) |  |  |  |  | 1.32 | Sqm | 11012 | 14536 | 14536 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
51 |  |  | Providing and Fixing of 32mm Double Flush Door with frame 8mm beeding on its edges on four sides with polishing finish and 1 mm thick laminate on the both sides of which including ISI marked Stainless Steel centre lock and butt hinges with necessary screws and tower bolt complete for (1500 x 200 mm door) (At Entrance) |  |  |  |  | 1 | Nos | 50400 | 50400 | 50400 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
52 |  |  | Providing and fixing of Side wall decor Frame for photo hangings panneling with 18mm BWP 710 Gurjan Ply and 8mm thick beeding half rounded on the both sides with 1mm thick laminate finish with necessary hardware and Polishing. (At Entrance) |  |  |  |  | 10.97 | Rmt | 2170 | 23805 | 23805 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
53 |  |  | Supply and fixing of Wall paper as approved by the Engineer In-charge. (1. 1 x 2 x 4350 x 85 mm & 2. 1 x 2 x 820 x 85 mm) (At Entrance) |  |  |  |  | 2 | Nos | 5175 | 10350 | 10350 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
54 |  |  | Supply and fixing of Main IVF logo with LED arcylic board fixed with LEDs inside and electrical connections as approved by the Engineer In-charge ( 520 mm dia & 50 mm thick) (In Reception) |  |  |  |  | 1 | Nos | 11475 | 11475 | 11475 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
55 |  |  | Supply and fixing of Main Entrance LED 3D Arcylic letter board fixed with LEDs inside and electrical connections as approved by the Engineer In-charge (2890 mm x 465 mm) (At Entrance) |  |  |  |  | 1 | Nos | 44250 | 44250 | 44250 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
56 |  |  | Providing and fixing Aluminium Extruded Section Body Tubular Type Hydraulic Door Closer (For all ABS doors) |  |  |  |  | 8 | Nos | 2819 | 22552 | 22552 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
57 |  |  | Supplying and fixing of windows / in open court yards using 25mm x 6mm MS flat alround and 10mm MS square bars (for Window Grills) |  |  |  |  | 10.8435 | Sqm | 1569 | 17013 | 17013 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | CS
58 |  |  | AHU shed with provision for fencing, door with lock- key arrangement on Terrace Floor) |  |  |  |  | 1 | Iob | 300000 | 300000 | 300000 | This work is proposed as safety measure for AHU's keeping in view of temparature of outdoor and weather conditions. Technically 5° to 6° C temprature will be reduced which will decrease the power bill also. | CS
59 |  |  | Supply of Sun Control film to the glazed windows (For Windows & Door view Windows) |  |  |  |  | 14.55 | Sqm | 381 | 5544 | 5544 | the work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | cs
[7 empty] | 668745 |  |  | PART-A | 3041177 | 2372432
PLUMBING WORKS
60 | 75 | IVF075 | Supply and fixing of Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes 22.20mm OD pipe at Gandhi Hospital | 75 | Rmt | 229 | 17175 | 105.4 | Rmt | 229 | 24137 | 6962 | The qty is not utilised as per site condition. Hence savings | P
Plumbing Supplemental Works
61 |  |  | Supplying and fixing of 3" (75mm) Nahany trap with jali | 0 |  |  |  | 5 | Nos | 133 | 665 | 665 | This work is executed as per Site Conditions. | PS
62 |  |  | Supplying and fixing 50 mm Nominal Bore GI pipe Medium Grade properties (For Autoclave) |  |  |  |  | 35.1 | Rmt | 599 | 21025 | 21025 | This work is mandatory for autoclave to let out the steam outside the premises. Hence executed. | PS
[7 empty] | 17175 |  |  | PART-A | 45827 | 28652
ELECTRICAL WORKS
63 | 96 | IVF096 | Supply and laying of ISI 25mm outer dia medium grade with IS:9537-part 3 rigid PVC pipe concealed in wall at Gandhi Hospital | 200 | Rmt | 116 | 23200 | 415.5 | Rmt | 116 | 48198 | 24998 | Item quantiy was increased to provide and lay main circuits for Switch boards and sockets in IVF | E
64 | 97 | IVF097 | Supply and laying of ISI 25mm outer dia medium grade with IS:9537-part 3 rigid PVC pipe surface on wall at Gandhi Hospital | 500 | Rmt | 107 | 53500 | 1060.2 | Rmt | 107 | 113441 | 59941 | Item quantiy was increased to provide and lay main circuits for Switch boards and sockets in IVF | E
65 | 98 | IVF098 | Wiring with 2 runs of 22/0.3mm 1.5 Sq.mm FRLS / HFFR P.V.C. insulated flexible copper cable ISI MARK in existing pipe with 6A Modular switch at Gandhi Hospital | 110 | Pts | 945 | 103950 | 146 | Pts | 945 | 137970 | 34020 | Item quanity was increased so as to provide electrical points in corridor, wards, rooms and OT's of IVF | E
66 | 99 | IVF099 | Supply and fixing of 6A ISI Mark 3/2 pin Modular socket with 6A 1way Modular switch at Gandhi Hospital | 12 | No | 675 | 8100 | 30 | No | 675 | 20250 | 12150 | Item quanity was increased so as to provide common sockets to the siwtch boards in corridor, rooms, wards and OT's of IVF | E
67 | 104 | IVF104 | Supply and run of 3 of 2.5 sq.mm 36/0.3mm phase neutral and earth FRLS / HFFR PVC insulated flexible copper cable at Gandhi Hospital | 600 | Rmt | 177 | 106200 | 637.1 | Rmt | 177 | 112767 | 6567 | Item quanity was increased so as to provide and laying of 2.5 sqmm 3 runs wire from Distribution boards to Switch boards and sockets in corridor, rooms, wards and OT's of IVF | E
68 | 105 | IVF105 | Supply and 3 runs of 4.0 sq mm 56/0.3 mm phase neutral and earth FRLS / HFFR PVC insulated flexible copper cable at Gandhi Hospital | 1200 | Rmt | 255 | 306000 | 1349.1 | Rmt | 255 | 344021 | 38021 | Item quanity was increased so as to provide and laying of 4 sqmm 3 runs wire from Distribution boards to power sockets and air consitioners points in corridor, rooms, wards and OT's of IVF | E
69 | 106 | IVF106 | Supply and run of 5 of 6.0 Sqmm 90/0.3 mm 3 phases, neutral and earth FRLS / HFFR PVC insulated flexible copper cable at Gandhi Hospital | 60 | Rmt | 606 | 36360 | 333.3 | Rmt | 606 | 201980 | 165620 | Qty increased as the no. of DB's increased and the main circuits from Main VTPN to DB increased | E
70 | 107 | IVF107 | Supply and run of 5 of 10.0 Sqmm 140/0.3 mm 3 phases, neutral and earth FRLS / HFFR PVC insulated flexible copper cable at Gandhi Hospital | 40 | Rmt | 967 | 38680 | 145.1 | Rmt | 967 | 140312 | 101632 | Qty increased as the no. of DB's increased and the main circuits from Main VTPN to DB increased | E
71 | 109 | IVF109 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 at Gandhi Hospital | 3 | No | 18325 | 54975 | 8 | No | 18325 | 146600 | 91625 | Qty increased to accomadate all the circuits of switch board, sockets, power sockets and air condition points in the DB | E
72 | 115 | IVF115 | Supply and Transportation 36W Edge lit, 2 feet x2 feet 600mm x600mm slim panel LED luminaire At Gandhi Hospital | 30 | No | 4350 | 130500 | 40 | No | 4350 | 174000 | 43500 | Qty increased so as to provide adequate lighting in corridor, ward, Minor OT, change room, Entrance area, Reception,Andrology lab and Cryo room | E
73 | 119 | IVF119 | Supply and fixing of Modular type Stepped electronic regulator | 12 | No | 827 | 9924 | 14 | No | 827 | 11578 | 1654 | Qty increased as the no of fans executed are 14. hence 2 nos AE increased. | E
74 | 122 | IVF122 | SITC of Hot dip galvanized perforated cable tray of 300 mm Wide sizes At Gandhi Hospital | 80 | Rmt | 1310 | 104800 | 85.4 | Rmt | 1310 | 111874 | 7074 | Qty increased as per site condition for laying of main cables over the false ceiling | E
75 | 124 | IVF124 | Supply and fixing of 12V 65 AH SMF battery including wire leads. Makes: Quanta / Racket / Exide. At Gandhi Hospital | 20 | No | 20584 | 411680 | 32 | No | 20584 | 658688 | 247008 | As the UPS with isolation transformer requires min 32 nos of batteries to increase uptime of 60 minutes from 30 minutes considering the load. hence the Qty. exceeded and proposed as AE | E
76 | 129 | IVF129 | Supply and installation of 25x3 GI flat for body earthing of DBs and Cable tray which is laid in 100mm cable tray At Gandhi Hospital | 100 | Rmt | 163 | 16300 | 168.7 | Rmt | 163 | 27498 | 11198 | Qty increased as the earthing flat is running from ground floor to 5th Floor of MCH Block. Hence quantity increased | E
77 | 131 | IVF131 | Supply and installation of 4 sqmm Copper wire for Earthing of DBs Equipment At Gandhi Hospital | 80 | Rmt | 83 | 6640 | 286 | Rmt | 83 | 23738 | 17098 | Qty increased so as to connect earthing from panel to VTPN and from VTPN to DB's | E
78 | 136 | IVF136 | Supply, Lying and testing of 4Cx4 sqmm PVC Insulated Cable 1100V grade armoured Copper cable with ISI mark at Gandhi Hospital | 80 | Rmt | 356 | 28480 | 125 | Rmt | 356 | 44500 | 16020 | Qty increased to provide cables to AHU 67 mts and Heater 58mts | E
Electrical Supplemental Works
79 |  |  | Supply and Transportation 56W Clean room Light fixture, 2' x2' (600mm x600mm) LED luminaire (In Embryology lab and IVF OT) |  |  |  |  | 12 | Nos | 17241 | 206892 | 206892 | During site inspection, EE (Electrical) has instructed to provide 56W lights to attain required illumination. Hence executed. | ES
80 |  |  | Supply and Transportation of 48" ( 1200 mm) High Speed Fan Sweep Celing Fan with all accessories etc., complete. Make Havells S S 390 |  |  |  |  | 14 | Nos | 4317 | 60438 | 60438 | The EE (Electrical) during site inspection instructed to provide regular high speed fans since maintaining BLDC fans in governement instutions is not viable. Hence executed | ES
81 |  |  | Labour charges for fixing of ceiling fan and regulator including transportation and giving connections with twin core wire etc., complete. |  |  |  |  | 14 | Nos | 185 | 2590 | 2590 | As per Instructions of EE (Electrical) during site inspection, regular high speed fans were provided. Hence executed | ES
82 |  |  | Supply and erecting 19/20mm steel tube down rod of one meter length with bolts & nuts duly painted with matching colour of fan complete |  |  |  |  | 14 | Nos | 162 | 2268 | 2268 | As difference in false ceilling one meter down rods are used as per site conditions | ES
83 |  |  | Supply & fixing of 2nos6A, 2 in one socket - 2 Nos with 6A switch control - 2 Nos modular type |  |  |  |  | 30 | Nos | 1178 | 35340 | 35340 | 6Amp socket was required as per site conditions. Hence executed | ES
84 |  |  | Supply,Transportation of 15" (375mm) ISI, 900 RPM Heavy duty exhaust fan with metallic blades |  |  |  |  | 1 | Nos | 4310 | 4310 | 4310 | It is essential to provide heavy duty exhaust fan in Autoclave room. Hence executed | ES
85 |  |  | Labour charges for fixing the exhaust fan in wall with necessary connections |  |  |  |  | 1 | Nos | 788 | 788 | 788 | As it is mandatory in Autoclave room hence executed | ES
86 |  |  | Supply and fixing of 12 Way SPN DB with IP 43 Protection as per IS:13032 |  |  |  |  | 1 | No | 9444 | 9444 | 9444 | It is mandatory to provide 12 Way SPN DB for UPS. Hence executed | ES
87 |  |  | Supply and fixing of cable adapteres box with cover for DBs including, massanory work etc., complete., |  |  |  |  | 8 | Nos | 5085 | 40680 | 40680 | It is mandatory to provide cable adapters to connect RAW power with UPS power. Hence executed | ES
88 |  |  | Supply and Installation of control cum transmission wiring of size 4C x 2.5 Sqmm copper wire |  |  |  |  | 20 | Rmt | 289 | 5780 | 5780 | It is mandatory required for VRV Sysytem | ES
89 |  |  | Supply and Installation of control cum transmission wiring of size 2C x 1.5 Sqmm copper wire |  |  |  |  | 190 | Rmt | 173 | 32870 | 32870 | It is mandatory required for VRV System | ES
90 |  |  | 4C x 1.5 Sqmm Copper Flexible Cable For Condensing Unit to Electrical Panel |  |  |  |  | 74.1 | Rmt | 130 | 9633 | 9633 | It is mandatory required for AHU's connection System | ES
91 |  |  | Supply and fixing of FP Metal Enclosure with IP 20 Protection DB Make with 1 No 63A, 10 KA FP MCB |  |  |  |  | 1 | Nos | 4203 | 4203 | 4203 | It is mandatory required to connect Powre supply to autoclave | ES
92 |  |  | POINT WIRING and LIGHT FIXTURES & FITTINGS Providing Point wiring for Light Concealed Type with 2 x 1.0 Sq.mm. Copper. |  |  |  |  | 13 | Nos | 1200 | 15600 | 15600 | work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | ES
93 |  |  | Proving and fixing Profile lights at wpc Louvers |  |  |  |  | 10.66 | Rmt | 1182 | 12600.12 | 12600.12 | work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | ES
94 |  |  | Proving and fixing Track lights at side wall décor frame with 4 fixtures and 2 tracks |  |  |  |  | 1 | Job | 9600 | 9600 | 9600 | work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | ES
95 |  |  | External Profile light at Name Plate |  |  |  |  | 2.89 | Rmt | 1182 | 3415.98 | 3415.98 | work was taken up at reception and entrance area as per the instructions issued by the End user and TSMSIDC higher officials. | ES
[7 empty] | 1439289 |  |  | PART-A | 2773867.1 | 1334578.1
Fire Fighting Supplimental Works
96 |  |  | Supply, Installation, testing and commissioning of EN54-2 Listed and LPCB approved based analog addressable fire control panel |  | Nos |  |  | 1 | Nos | 291366 | 291366 | 291366 | It is necessary to monitor fire alaram detectors in case of emergency. This work is executed as per the instructions of TSMSIDC Higher officials | FFS
[7 empty] | 0 |  |  | PART-A | 291366 | 291366
Air Conditioning Works
97 | 149 | IVF149 | Supply, transportation and installation of split AC unit 1.5 TR inverter type 3 Star at Gandhi Hospital | 1 | No | 48000 | 48000 | 2 | No | 48000 | 96000 | 48000 | Qty increased so as to provide AC in UPS room and Andrology lab | AC
98 | 153 | IVF153 | SITC of air cooled condensing units with two scroll compressors, air cooled condenser, 8.5 TR capacity At Gandhi Hospital | 1 | No | 182000 | 182000 | 2 | No | 182000 | 364000 | 182000 | Qty increased as one AHU unit has been placed for Backup to IVF center | AC
99 | 163 | IVF163 | SITC of SS perforated return raiser grilles with 10 microns filters with collar dampers At Gandhi Hospital | 2 | Sqm | 26300 | 52600 | 3.29 | Sqm | 26300 | 86527 | 33927 | Qty increased as per site condition | AC
100 | 164 | IVF164 | Extruded Al. powder coated EXHAUST / RETURN discrete grilles At Gandhi Hospital | 1 | Sqm | 8125 | 8125 | 1.25 | Sqm | 8125 | 10156 | 2031 | Qty increased as per site condition | AC
101 | 166 | IVF166 | SITC of Magnehelic gauges across pre and fine filter at AHUs including mounting arrangement, SS nozzles, food grade PVC tubing, etc. At Gandhi Hospital | 2 | No | 10500 | 21000 | 3 | No | 10500 | 31500 | 10500 | Qty increased as per site condition | AC
102 | 171 | IVF171 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with self-adhesive tapes 25mm Thick for Supply air duct running inside the building. at Gandhi Hospital | 40 | Sqm | 785 | 31400 | 75.04 | Sqm | 785 | 58906 | 27506 | Qty increased so as to provide proper covering from Dampness and moisture to copper pipe of IVF units and AHU units | AC
103 | 176 | IVF176 | VRF Indoor Units : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units 1.5 TR At Gandhi Hospital | 4 | No | 35000 | 140000 | 5 | No | 35000 | 175000 | 35000 | Qty increased to provide 1 no VRF AC in UPS Room | AC
104 | 179 | IVF179 | Supply, Installation , Testing and Commissioning of Refnet joints to be provided in refrigerant pipe line. Material of construction for fittings shall be similar to refrigerant piping. At Gandhi Hospital | 10 | Set | 6191 | 61910 | 11 | Set | 6191 | 68101 | 6191 | Qty increased as per site condition | AC
105 | 180 | IVF180 | Supply and Installation of control cum transmission wiring of size 3C x 1.5 Sqmm copper wire At Gandhi Hospital | 150 | Rmt | 320 | 48000 | 165 | Rmt | 320 | 52800 | 4800 | Qty increased as per site condition | AC
106 | 181 | IVF181 | Supply and Installation of cabling of size 2C x 1 Sqmm copper wire At Gandhi Hospital | 100 | Rmt | 255 | 25500 | 120 | Rmt | 255 | 30600 | 5100 | As per the site requirement, Qty. exceeded and hence proposed as AE | AC
Air Conditioning Supplimental Works
107 |  |  | Supply and installation of 2.2 TR 3 Star Split AC |  |  |  |  | 1 | Nos | 72225 | 72225 | 72225 | The item is provided in the reception area as per the instructions issued by the End user and TSMSIDC higher officials. Hence executed | ACS
108 |  |  | SITC of CPVC drain piping with supports, clamps of the following size. 25mm Dia at Gandhi Hospital |  |  |  |  | 66 | Rmt | 200 | 13200 | 13200 | This work is executed as contingency work to the above 2.2 TR AC. | ACS
109 |  |  | Supply & Installation of MS Angle for Duct Support, Cable Tray Support and Condensing Unit Stand of size 40 X 40 x 5 mm Thick. |  |  |  |  | 92.2 | Kg | 190 | 17518 | 17518 | It is mandatorly required for support duct hence this work is executed as per the instructions of TSMSIDC Higher officials. | ACS
110 |  |  | Supply & Installation of MS Angle for Duct Support, Cable Tray Support and Condensing Unit Stand of size 25 X 25 x 5 mm Thick. |  |  |  |  | 25.5 | Kg | 190 | 4845 | 4845 | It is mandatorily required to support the duct & cable tray. Hence this work is executed as per the instructions of TSMSIDC Higher officials. | ACS
111 |  |  | Supply and installation of Canvas Connections For AHUS |  |  |  |  | 2 | Nos | 6500 | 13000 | 13000 | Its mandatorly required for support duct hence this work is executed as per the instructions of TSMSIDC Higher officials. | ACS
[7 empty] | 618535 |  |  | PART-A | 1094378 | 475843
MGPS WORKs
112 | 183 | IVF183 | SITC of Oxygen Outlets Imported At Gandhi Hospital | 4 | each | 2506 | 10024 | 6 | each | 2506 | 15036 | 5012 | Qty. increased as per the site requirement hence proposed as AE | G
113 | 184 | IVF184 | SITC of Oxygen Flow meter with Humidifier- Imported At Gandhi Hospital | 4 | each | 1805 | 7220 | 6 | each | 1805 | 10830 | 3610 | Qty. increased as per the site requirement hence proposed as AE | G
114 | 187 | IVF187 | SITC of C02 Manifold for 2 Cylinders, At Gandhi Hospital | 1 | Set | 20750 | 20750 | 2 | Set | 20750 | 41500 | 20750 | Additional Manifold is provided to supply CO2 at 2-3 bar pressure to IVF OT. | G
115 | 188 | IVF188 | SITC of C02 Outlets with matching probes, - Imported At Gandhi Hospital | 4 | each | 2506 | 10024 | 6 | each | 2506 | 15036 | 5012 | Qty. increased as per the site requirement hence proposed as AE | G
116 | 189 | IVF189 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 12mm COPPER PIPE at Gandhi Hospital | 24 | Rmt | 642 | 15408 | 38.3 | Rmt | 642 | 24589 | 9181 | Qty. increased as per the site requirement hence proposed as AE | G
117 | 190 | IVF190 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 15mm COPPER PIPE at Gandhi Hospital | 114 | Rmt | 824 | 93936 | 157.7 | Rmt | 824 | 129945 | 36009 | Qty. increased as per the site requirement hence proposed as AE | G
118 | 191 | IVF191 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 22mm COPPER PIPE at Gandhi Hospital | 36 | Rmt | 1191 | 42876 | 79.5 | Rmt | 1191 | 94685 | 51809 | Qty. increased as per the site requirement hence proposed as AE | G
119 | 192 | IVF192 | SITC of MEDICAL Grade BS EN: 13348 Kite Marked 28mm COPPER PIPE at Gandhi Hospital | 18 | Rmt | 1473 | 26514 | 27 | Rmt | 1473 | 39771 | 13257 | Qty. increased as per the site requirement hence proposed as AE | G
120 | 195 | IVF195 | SITC of Medical Line Valve, - Indian 15mm 0D at Gandhi Hospital | 3 | each | 1938 | 5814 | 8 | each | 1938 | 15504 | 9690 | Qty. increased as per the site requirement hence proposed as AE | G
MGPS Supplemental Works
121 |  |  | Fully Automatic Control Panel for Oxygen System: Supply, installation and commissioning of Fully Automatic control panel for unintrupted Oxygen supply | 0 | Set |  |  | 1 | Set | 175180 | 175180 | 175180 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user | GS
122 |  |  | Trigas Emergency Manifold: SITC of Emergency Trigas Manifold maximum for 1+1 D-type Gas Cylinders complete with separate NRVs, tail pipes and brass fittings for each cylinders. | 0 | Set |  |  | 1 | Set | 9620 | 9620 | 9620 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user. | GS
123 |  |  | Fully Automatic Control Panel for Trigas System: Supply, installation and commissioning of Fully Automatic control panel for unintrupted Nirous Oxide supply. | 0 | Set |  |  | 1 | Set | 175180 | 175180 | 175180 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user. | GS
124 |  |  | Fully Automatic Control Panel for CO2 System: Supply, installation and commissioning of Fully Automatic control panel for unintrupted Nirous Oxide supply. | 0 | Set |  |  | 1 | Set | 175180 | 175180 | 175180 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user. | GS
125 |  |  | SITC of Medical Air-4 Outlet with matching probe as per HTM-2022/02-01 of UK/ NFPA 99C of USA as per enclosed technical Specification. | 0 | Nos |  |  | 6 | Nos | 12470 | 74820 | 74820 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user. | GS
126 |  |  | 12 mm Valve for 12 mm OD Pipe Note: New item added | 0 | Nos. |  |  | 3 | Nos. | 930 | 2790 | 2790 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user. | GS
127 |  |  | Supply and installation of 46.7 liter size CO2 cylinders | 0 | Nos. |  |  | 2 | Nos | 20850 | 41700 | 41700 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user. | GS
128 |  |  | Supply and installation of 46.7 liter size O2 cylinders | 0 | Nos. |  |  | 2 | Nos | 17850 | 35700 | 35700 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user. | GS
129 |  |  | Supply and installation of 46.7 liter size Trigas cylinders | 0 | Nos. |  |  | 2 | Nos | 29250 | 58500 | 58500 | This work is executed as per the necessity of medical gases in IVF Center under the instructions of End user. | GS
130 |  |  | Supply and installation of 46.7 liter size N2O cylinders | 0 | Nos. |  |  | 2 | Nos | 33000 | 66000 | 66000 | This work is executed as per the Necessity of medical gases in IVF Center under the instructions of Enduser letter enclosed | GS
[7 empty] | 232566 |  |  | PART-A | 1201566 | 969000
[6 empty] | TOTAL (PART-A) | 2976310 |  |  |  | 9379481.1 | 6403171.1
[8 empty] | As Per Agreement |  | Excess | 6403171.1
[8 empty] | As Per RE |  | Less | 3451717
[8 empty] | Difference |  | Difference | 2951454.1

## CS-1 (hidden)
Comparitive statement
Name of the work: Design, fabrication, establishing & commissioning of In-Vitro Fertility Centers (IVFCs) along with allied services on Turnkey basis at Gandhi Hospital, Secunderabad.
S.No | Description |  | As per Agreement | As per workdone | Excess | Less | Net difference
Agreement works (Part-A)
1 | Equipment |  | #REF! | #REF! | #REF! | #REF!
2 | Civil Works |  | #REF! | #REF! | #REF! | #REF!
3 | Plumbing works |  | #REF! | #REF! | #REF! | #REF!
4 | Electrical works |  | #REF! | #REF! | #REF! | #REF!
5 | ELV works |  | #REF! | #REF! | #REF! | #REF!
6 | Fire Fighting works |  | #REF! | #REF! | #REF! | #REF!
7 | Air Conditioning works |  | #REF! | #REF! | #REF! | #REF!
8 | MGPS works |  | #REF! | #REF! | #REF! | #REF!
| Sub Total (Part-A) |  | #REF! | #REF! | #REF! | #REF!
Supplemental works (Part-B)
9 | Equipment |  | #REF! | #REF! | #REF! | #REF!
10 | Civil works |  | #REF! | #REF! | #REF! | #REF!
11 | Plumbing works |  | #REF! | #REF! | #REF! | #REF!
12 | Electrical works |  | #REF! | #REF! | #REF! | #REF!
13 | Fire Fighting works |  | #REF! | #REF! | #REF! | #REF!
14 | Air Conditioning works |  | #REF! | #REF! | #REF! | #REF!
15 | MGPS works |  | #REF! | #REF! | #REF! | #REF!
| Sub Total (Part-B) |  | #REF! | #REF! | #REF! | #REF!
| Total (Part-A+Part-B) |  | #REF! | #REF! | #REF! | #REF! | #REF!
16 | Provision towards Engineering Supervision Charges @ 4% on RE Value | 4% | #REF! | #REF! | #REF! | #REF!
| GST @ 18% |  | #REF! | #REF! | #REF! | #REF!
| Total |  | #REF! | #REF! | #REF! | #REF!
17 | Labour Cess @ 1% on Basic Price of Revised Estimate | 1% |  | #REF! | #REF! | #REF!
18 | NAC @ 0.1% on Basic Price of Revised estimate | 0.1% |  | #REF! | #REF! | #REF!
19 | Provision towards seigniorage Charges on Civil Component |  |  | 308 | 308 | 0
20 | Provision towards DMF Charges 30% on Seniorage Charges | 30% |  | 92.4 | 92.4 | 0
21 | Provision towards SMFT Charges 2% on seigniorage Charges | 2% |  | 6.16 | 6.16 | 0
22 | Provision towards Haritha Nidhi @ 0.01% | 0.01% |  | #REF! | #REF! | #REF!
23 | Subtotal of S. No 17 to 22 |  |  | #REF! | #REF! | #REF!
24 | Provision towards GST 18% on Subtotal @ S. No. 23 | 18% |  | #REF! | #REF! | #REF!
25 | Provision towards Inauguration charges |  |  | 200000 | 200000 | 0
26 | Provision towards Unforeseen items and rounding off (LS) |  | 1181324 |  | 0 | 1181324 |  | 55000000
| Sub total of S.No 23 to 26 |  |  | #REF! | #REF! | #REF! |  | #REF!
| Grand Total |  | #REF! | #REF! | #REF! | #REF! | #REF!
#REF!
|  | As per Admn. Sanction |  | #REF! | Excess | #REF!
|  | As per Work done |  | #REF! | Less | #REF!
|  | Difference |  | #REF! | Difference | #REF!
T.A DY. EXECUTIVE ENGINEER EXECUTIVE ENGINEER CHIEF ENGINEER
1938 nos bricks

## ABSTRACT-1 (hidden)
Name of the work: Design, fabrication, establishing & commissioning of In-Vitro Fertility Centers (IVFCs) along with allied services on Turnkey basis at Gandhi Hospital, Secunderabad, MGM Hospital, Warangal & MGMH Petlaburj, Hyd.
COMPARITIVE STATEMENT FOR GENERAL ABSTRACT
S.No | Description |  | As per Agreement | As per workdone | Excess | Less | Remarks
Agreement works (Part-A)
1 | Equipment |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
2 | Civil Works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
3 | Plumbing works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
4 | Electrical works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
5 | ELV works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
6 | Fire Fighting works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
7 | Air Conditioning works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
8 | MGPS works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
| Sub Total (Agreement Part-A) |  | #REF! | #REF! | #REF! | #REF!
Supplimental works (Part-B)
9 | Equipment supplimental |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
10 | Civil supplimental works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
11 | Plumbing supplimental works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
12 | Electrical supplimental works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
13 | Fire Fighting supplimental works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
14 | Air Conditioning supplimental works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
15 | MGPS supplimental works |  | #REF! | #REF! | #REF! | #REF! | The details is given in the comparative Statement
| Sub Total (Supplimental Part-B) |  | #REF! | #REF! | #REF! | #REF!
| Total (Part-A+Part-B) |  | #REF! | #REF! | #REF! | #REF!
| GST @ 18% |  | #REF! | #REF! | #REF! | #REF!
| Total |  | #REF! | #REF! | #REF! | #REF!
16 | Labour Cess @ 1% on Basic Price of Revised Estimate | 1% |  | #REF! | #REF! | #REF!
17 | NAC @ 0.1% on Basic Price of Revised estimate | 0.1% |  | #REF! | #REF! | #REF!
18 | Provision towards Seniorage Charges on Civil Component |  |  | 308 | 308 | 0
19 | Provision towards DMF Charges 30% on Seniorage Charges | 30% |  | 92.4 | 92.4 | 0
20 | Provision towards SMFT Charges 2% on seniorage Charges | 2% |  | 6.16 | 6.16 | 0
21 | Provision towards Haritha Nidhi | 0.01% |  | #REF! | #REF! | #REF!
22 | Sub total of S.No 14 to 18 |  |  | #REF! | #REF! | #REF!
23 | Provision towards GST 18% on Seniorage Charges | 18% |  | #REF! | #REF! | #REF!
24 | Provision towards Engineering Supervision Charges @ 4% on RE Value | 4% | #REF! | #REF! | #REF! | #REF!
25 | Provision towards Unforseen items and rounding off (LS) |  |  |  | 0 | 0
| Sub total of S.No 22 to 25 |  |  | #REF! | #REF! | #REF!
| Grand Total |  | #REF! | #REF! | #REF! | #REF!
|  | As Per Agreement |  | #REF! | Excess | #REF!
|  | As Per RE |  | #REF! | Less | #REF!
|  | Difference |  | #REF! | Difference | #REF!
| DY.EXECUTIVE ENGINEER |  | EXECUTIVE ENGINEER |  |  | SUPERINTENDING ENGINEER
| TSMSIDC, MEDCHAL MALKAJGIRI |  | TSMSISDC, HYDERAVAD DIVISION |  |  | TSMSISDC, HYDERABAD CIRCLE
1938 nos bricks