## SUMMARY
CLIENT :
PROJECT : IVF CETER_3RD FLOOR_PETLABURJ
DOC NAME : LOAD SUMMARY SHEET
DOC NUMBER : MECS/2023/IVF/PTB/ELE/02
DATE : 14.12.2023
REVISION R0
SL.No | DESCRIPTION | CONNECTING LOAD (KW) | DIVERSITY FACTOR | MAXIMUM LOAD (KW)
1 | Lighting Load | 1.3995 | 0.9 | 1.2596
2 | RAW power Load | 12.2691 | 0.8 | 9.8152
3 | Autoclave | 5 | 0.8 | 4
4 | Emergency Lighting Load | 0.96305 | 0.9 | 0.86674
5 | UPS power Load | 11.9804 | 0.8 | 9.5843
6 | AC Loads | 44.75 | 0.8 | 35.8
| TOTAL | 76.362 |  | 61.3259
Load in KW |  | 76.362 | KW | 61.3259
5% miscellaneous Load |  | 3.8181 |  | 3.0663
Total Load in KW |  | 80.1801 | KW | 64.3922
Group Diversity @80% |  |  | KW | 51.5137
Total KVA at 0.80 P.F |  |  | KVA | 64.3922
(As per the Load Calculation we required 65KVA Load from Floor Panel with 100% DG backup
UPS LOAD CALCULATION
Total Maximum Demand |  |  | 10.451 | KW
Group Diversity @80% |  |  | 8.3608 | KW
Total KVA at 0.80 Power Factor |  |  | 10.451 | KVA
Considering 70% Efficiency on UPS Selection |  |  | 14.9301 | KVA
(As the near by UPS rating available in market is 20KVA ) .So we recommend = 1 no's 20KVA.
No of Batteries
Total Rated KVA |  |  | 20 | KVA
Battery Power |  |  | 65 | AH
Battery Voltage |  |  | 12 | V
Backup Time |  |  | 0.5 | Hour
No of Batteries |  |  | 32 | Nos
As the Recommended Batteries are 30Nos of 65AH for Each 20KVA UPS

## Room Book
CLIENT :
| PROJECT : |  |  |  |  | IVF CENTER_3RD FLOOR_PETLABURJ
| DOC NAME : |  |  |  |  | USER REQUIRED SPECS
| DOC NUMBER : |  |  |  |  | MECS/2023/IVF/PTB/ELE/01
| DATE : |  |  |  |  | 14.12.2023
| REVISION |  |  |  |  | R0
[8 empty] | ELECTRICAL | [14 empty] | LV SYSTEMS
Sl.No | Description of the room | Room size in mtrs |  |  | Area |  | F/C HT | Lux Levels | Room Index | Wattage light | Fixtures Lumen | No of Fixtures | No of Fixtures | Raw power Lighting |  | UPS power Lighting |  | FANS |  | AC SOCKET | RAW POWER SOCKET | UPS | LAN/Data | Tele phone | ACS | CCTV | FA SYSTEM | Nursical Point
[18 empty] | CEILING | EXHAUST | 6A | 6/16A | 6/16A
|  | L | W | H | ( Sqmtr ) | ( Sqfts) | ( Ft ) | (Lux) |  | (watts) |  | ( Nos ) | ( Nos ) | ( Nos ) | (watts) | ( Nos ) | (watts) | ( Nos) | ( Nos) |  |  |  | ( Nos) | ( Nos) | ( Nos) | ( Nos) | ( Nos) | ( Nos)
THIRD FLOOR
1 | Lobby | 3.4 | 2.4 | 3 | 8.16 | 87.8016 | 3 | 200 | 0.46897 | 36 | 3600 | 1.7496 | 2 | 1 | 36 | 1 | 36 | [8 empty] | 1 | 2
2 | IVF Waiting Area | 3.33 | 6.35 | 3 | 21.1455 | 227.5256 | 3 | 200 | 0.72815 | 36 | 3600 | 2.9201 | 2 | 1 | 36 | 1 | 36 | 1 | [7 empty] | 1 | 2
3 | Senior Facult/Professor Room | 3.53 | 3.31 | 3 | 11.6843 | 125.7231 | 3 | 200 | 0.56941 | 24 | 2400 | 3.095 | 4 | 3 | 72 | 1 | 24 |  |  | 1 | 2 | 2 | 1 | 1 |  |  | 2
4 | 2.4M Wide Corridor | 7.24 | 2.4 | 3 | 17.376 | 186.9658 | 3 | 200 | 0.60083 | 36 | 3600 | 2.908 | 2 | 1 | 36 | 1 | 36 | [8 empty] | 1 | 3
5 | Counseling Room-1 | 2.15 | 3.2 | 3 | 6.88 | 74.0288 | 3 | 300 | 0.42866 | 24 | 2400 | 3.6312 | 2 | 1 | 24 | 1 | 24 | 1 |  | 1 | 2 | 2 | 1 | 1 |  |  | 1 | 1
6 | Ultrasound | 2.96 | 3 | 3 | 8.88 | 95.5488 | 3 | 200 | 0.49664 | 24 | 2400 | 2.6968 | 4 | 3 | 72 | 1 | 24 | 1 |  | 1 | 8 |  | 1 |  |  |  | 1
7 | Toilet | 1.2 | 1.8 | 3 | 2.16 | 23.2416 | 3 | 150 | 0.24 | 12 | 1200 | 2.0362 | 2 | 1 | 12 | 1 | 12 |  | 1
8 | 1.2M Wide Corridor | 1.2 | 3.46 | 3 | 4.152 | 44.6755 | 3 | 200 | 0.297 | 24 | 2400 | 2.1086 | 2 | 1 | 24 | 1 | 24 | [9 empty] | 1
9 | Counseling Room-2 | 3.32 | 3.35 | 3 | 11.122 | 119.6727 | 3 | 300 | 0.55582 | 24 | 2400 | 4.5271 | 2 | 1 | 24 | 1 | 24 | 1 |  | 1 | 2 | 2 | 1 | 1 |  |  | 1
10 | Anesthestist Room | 2.08 | 3.2 | 3 | 6.656 | 71.6186 | 3 | 300 | 0.4202 | 24 | 2400 | 3.5837 | 2 | 1 | 24 | 1 | 24 | 1 |  | 1 | 2 | 2 | 1 | 1 |  |  | 1
11 | Embryologist Room | 2.08 | 3.15 | 3 | 6.552 | 70.4995 | 3 | 300 | 0.41759 | 24 | 2400 | 3.5498 | 2 | 1 | 24 | 1 | 24 | 1 |  | 1 | 2 | 2 | 1 | 1 |  |  | 1
12 | Semi-Sterile Area | 7.16 | 2.4 | 3 | 17.184 | 184.8998 | 3 | 200 | 0.59916 | 36 | 3600 | 2.8839 | 3 | 2 | 72 | 1 | 36 | [8 empty] | 1 | 4
13 | Autoclave | 3.77 | 2.5 | 3 | 9.425 | 101.413 | 3 | 300 | 0.50106 | 36 | 3600 | 2.8371 | 1 | 0 | 0 | 1 | 36 |  |  |  | 4 |  | 1 |  |  |  | 2
14 | Clean Store | 2.3 | 3.85 | 3 | 8.855 | 95.2798 | 3 | 300 | 0.47995 | 24 | 2400 | 4.1742 | 2 | 1 | 24 | 1 | 24 |  |  |  |  | 2 |  |  |  | 1 | 1
15 | Waiting Room | 2.46 | 1.8 | 3 | 4.428 | 47.6453 | 3 | 200 | 0.34648 | 24 | 2400 | 1.9276 | 1 | 0 | 0 | 1 | 24 |  |  | 1 | 2
16 | Sperm Collection Room | 3.77 | 4.05 | 3 | 15.2685 | 164.2891 | 3 | 200 | 0.65083 | 24 | 2400 | 3.5385 | 3 | 2 | 48 | 1 | 24 | 1 |  | 1 | 6 |  | 2 |  |  |  | 2
17 | Toilet | 1.2 | 1.8 | 3 | 2.16 | 23.2416 | 3 | 150 | 0.24 | 12 | 1200 | 2.0362 | 1 | 1 | 12 | 0 | 0 |  | 1
18 | Sterile Area | 11.98 | 2.4 | 3 | 28.752 | 309.3715 | 3 | 200 | 0.66648 | 36 | 3600 | 4.3379 | 3 | 2 | 72 | 1 | 36 | [7 empty] | 1 | 1 | 4
19 | Andrology Lab | 5.73 | 6.35 | 3 | 36.3855 | 391.508 | 3 | 300 | 1.004 | 36 | 3600 | 5.4661 | 3 | 2 | 72 | 1 | 36 | 1 |  | 2 | 12 |  | 2 | 1 |  | 1 | 2
20 | Cryo Room | 2.21 | 2.8 | 3 | 6.188 | 66.5829 | 3 | 300 | 0.41171 | 36 | 3600 | 2.267 | 1 | 0 | 0 | 1 | 36 |  |  | 1 | 4
21 | OT-1 | 5.73 | 3.35 | 3 | 19.1955 | 206.5436 | 3 | 400 | 0.70468 | 42 | 4200 | 4.6955 | 6 | 0 | 0 | 6 | 252 |  |  |  |  | 12 | 2 |  |  |  | 2
22 | IVF/ICSI/Embriology Lab | 5.03 | 6.35 | 3 | 31.9405 | 343.6798 | 3 | 400 | 0.93557 | 36 | 3600 | 6.8658 | 6 | 0 | 0 | 6 | 216 |  |  |  |  | 20 | 2 | 1 |  |  | 1
23 | OT-2 | 5.02 | 6.35 | 3 | 31.877 | 342.9965 | 3 | 400 | 0.93454 | 42 | 4200 | 5.8798 | 6 | 0 | 0 | 6 | 252 |  |  | 2 |  | 14 | 2 |  |  |  | 1
24 | Pre Operative Ward | 3.43 | 6.35 | 3 | 21.7805 | 234.3582 | 3 | 300 | 0.74235 | 24 | 2400 | 6.638 | 6 | 4 | 96 | 2 | 48 | 1 |  | 1 |  | 10 | 3 | 1 |  |  | 2 | 1
25 | Post Operative Ward | 3.58 | 6.46 | 3 | 23.1268 | 248.8444 | 3 | 300 | 0.76782 | 24 | 2400 | 6.8145 | 4 | 3 | 72 | 1 | 24 | 1 |  | 1 |  | 12 | 2 |  |  |  | 1 | 1
26 | Toilet | 1.2 | 1.8 | 3 | 2.16 | 23.2416 | 3 | 150 | 0.24 | 12 | 1200 | 2.0362 | 1 | 1 | 12 | 0 | 0 |  | 1
27 | Store Room | 3.58 | 2.5 | 3 | 8.95 | 96.302 | 3 | 200 | 0.49068 | 24 | 2400 | 2.7511 | 2 | 1 | 24 | 1 | 24 | 1 |  |  | 4 | [5 empty] | 1
28 | Manifold Room | 3.14 | 6.35 | 3 | 19.939 | 214.5436 | 3 | 200 | 0.70035 | 24 | 2400 | 4.2941 | 4 | 3 | 72 | 1 | 24 | 1 |  | 1 | 6 |  | 1 |  |  |  | 2
29 | Electrical Room | 3.14 | 3.17 | 3 | 9.9538 | 107.1029 | 3 | 200 | 0.52582 | 24 | 2400 | 2.8552 | 1 | 0 | 0 | 1 | 24 | [9 empty] | 1
30 | UPS Room | 3.14 | 3.06 | 3 | 9.6084 | 103.3864 | 3 | 200 | 0.51658 | 24 | 2400 | 2.8054 | 1 | 0 | 0 | 1 | 24 |  |  | 2 | [6 empty] | 2
31 | 1.2M Wide Corridor | 1.2 | 5.06 | 3 | 6.072 | 65.3347 | 3 | 200 | 0.32332 | 24 | 2400 | 2.8326 | 2 | 1 | 24 | 1 | 24 | [9 empty] | 1
32 | Change Room-1 | 1.91 | 1.49 | 3 | 2.8459 | 30.6219 | 3 | 200 | 0.27901 | 24 | 2400 | 1.5385 | 1 | 0 | 0 | 1 | 24 |  |  |  | 2 | [5 empty] | 1
33 | Change Room-2 | 1.91 | 1.49 | 3 | 2.8459 | 30.6219 | 3 | 200 | 0.27901 | 24 | 2400 | 1.5385 | 1 | 0 | 0 | 1 | 24 |  |  |  | 2 | [5 empty] | 1
34 | Toilet | 1.2 | 2.51 | 3 | 3.012 | 32.4091 | 3 | 200 | 0.27062 | 12 | 1200 | 3.3575 | 1 | 1 | 12 | 0 | 0 |  | 1
35 | Blood Collection & Injection Room | 2.08 | 3.85 | 3 | 8.008 | 86.1661 | 3 | 200 | 0.45014 | 24 | 2400 | 2.6833 | 2 | 1 | 24 | 1 | 24 | 1 |  | 1 | 4 |  | 1 | 1 |  |  | 1
36 | Reception/ Registration | 3.14 | 3.2 | 3 | 10.048 | 108.1165 | 3 | 200 | 0.52829 | 24 | 2400 | 2.8688 | 2 | 1 | 24 | 1 | 24 | 1 |  | 1 | 3 | 3 | 1 | 1 |  |  | 2
37 | Record Room | 2.39 | 1.8 | 3 | 4.302 | 46.2895 | 3 | 200 | 0.34224 | 24 | 2400 | 1.8959 | 2 | 1 | 24 | 1 | 24 |  |  |  | 4 | [5 empty] | 1
38 | Staff Change Room-1 | 2.35 | 1.63 | 3 | 3.8305 | 41.2162 | 3 | 200 | 0.32081 | 24 | 2400 | 1.8009 | 2 | 1 | 24 | 1 | 24 | 1 |  |  | 2 | [5 empty] | 1
39 | Staff Change Room-2 | 2.35 | 1.51 | 3 | 3.5485 | 38.1819 | 3 | 200 | 0.30643 | 24 | 2400 | 1.7466 | 2 | 1 | 24 | 1 | 24 | 1 |  |  | 2 | [5 empty] | 1
40 | 1.3M Wide Corridor | 1.3 | 4.67 | 3 | 6.071 | 65.324 | 3 | 200 | 0.33897 | 24 | 2400 | 2.7014 | 2 | 1 | 24 | 1 | 24 | [9 empty] | 2
41 | Patient Change Room | 2.35 | 1.98 | 3 | 4.653 | 50.0663 | 3 | 200 | 0.3582 | 24 | 2400 | 1.9593 | 2 | 1 | 24 | 1 | 24 | 1 |  |  | 2 | [5 empty] | 1
| TOTAL | [11 empty] | 100 | 46 | 1164 | 54 | 1668 | 17 | 4 | 20 | 77 | 83 | 25 | 10 | 1 | 7 | 55 | 3
| Total Load in KW | [13 empty] | 0.67206 |  | 0.96305 | 0.58891 | 0.13857 | 1.1547 | 11.1143 | 11.9804
| Third floor Lighting Loads in KW | [12 empty] | 1.3995 | KW
| Third floor floor Raw Power Loads in KW | [12 empty] | 12.2691 | KW
| Third floor floor UPS Lighting Loads in KW | [12 empty] | 0.96305 | KW
| Third floor floor UPS Power Loads in KW | [12 empty] | 11.9804 | KW

## AC Load Sheet
CLIENT :
PROJECT : IVF CENTER_3RD FLOOR_PETLABURJ
DOC NUMBER : MECS/2023/IVF/PTB/ELE/02
DATE : 09.12.2023
REVISION R0
AC LOAD
S.NO | NAME | QTY | POWER IN KW | TOTAL LOAD IN KW | CONNECTED LOAD IN KW | DIVERSITY | MAXIMUM LOAD IN KW
1 | 12HP ODU-1 | 1 | 16 | 16 | 16 | 0.8 | 12.8
2 | 10HP ODU-1 | 1 | 14 | 14 | 14 | 0.8 | 11.2
3 | 11 KW ODU For AHU (1w+1s) | 2 | 11 | 22 | 11 | 0.8 | 8.8
4 | AHU | 1 | 3.75 | 3.75 | 3.75 | 0.8 | 3
| Total Load |  |  | 55.75 | 44.75 |  | 35.8