## SUMMARY
CLIENT :
PROJECT : IVF CETER_3RD FLOOR_PETLABURJ
DOC NAME : LOAD SUMMARY SHEET
DOC NUMBER : MECS/2023/IVF/PTB/ELE/02
DATE : 29.11.2023
REVISION R0
SL.No | DESCRIPTION | CONNECTING LOAD (KW) | DIVERSITY FACTOR | MAXIMUM LOAD (KW)
1 | Lighting Load | 1.2333 | 0.9 | 1.1099
2 | RAW power Load | 8.7182 | 0.8 | 6.9746
3 | Autoclave | 5 | 0.8 | 4
3 | Emergency Lighting Load | 0.82448 | 0.9 | 0.74203
4 | UPS power Load | 13.5681 | 0.8 | 10.8545
5 | AC Loads | 34 | 0.8 | 27.2
| TOTAL | 63.3441 |  | 50.8811
Load in KW |  | 63.3441 | KW | 50.8811
5% miscellaneous Load |  | 3.1672 |  | 2.5441
Total Load in KW |  | 66.5113 | KW | 53.4251
Group Diversity @80% |  |  | KW | 42.7401
Total KVA at 0.90 P.F |  |  | KVA | 47.489
(As per the Load Calculation we required 50KVA Load from Floor Panel with 100% DG backup
UPS LOAD CALCULATION
Total Maximum Demand |  |  | 11.5965 | KW
Group Diversity @80% |  |  | 9.2772 | KW
Total KVA at 0.80 Power Factor |  |  | 11.5965 | KVA
Considering 70% Efficiency on UPS Selection |  |  | 16.5665 | KVA
(As the near by UPS rating available in market is 20KVA ) .So we recommend = 1 no's 20KVA.
No of Batteries
Total Rated KVA |  |  | 20 | KVA
Battery Power |  |  | 42 | AH
Battery Voltage |  |  | 12 | V
Backup Time |  |  | 0.5 | Hour
No of Batteries |  |  | 29.7619 | Nos
As the Recommended Batteries are 30Nos of 42AH for Each 20KVA UPS

## URS
CLIENT :
| PROJECT : |  |  |  |  | IVF CENTER_3RD FLOOR_PETLABURJ
| DOC NAME : |  |  |  |  | USER REQUIRED SPECS
| DOC NUMBER : |  |  |  |  | MECS/2023/IVF/PTB/ELE/01
| DATE : |  |  |  |  | 29.11.2023
| REVISION |  |  |  |  | R0
[8 empty] | ELECTRICAL | [14 empty] | LV SYSTEMS
Sl.No | Description of the room | Room size in mtrs |  |  | Area |  | F/C HT | Lux Levels | Room Index | Wattage light | Fixtures Lumen | No of Fixtures | No of Fixtures | Raw power Lighting |  | UPS power Lighting |  | FANS |  | AC SOCKET | RAW POWER SOCKET | UPS | LAN/Data | Tele phone | PA System | CCTV | FA SYSTEM | Nursical Point
[18 empty] | CEILING | EXHAUST | 6A | 6/16A | 6/16A
|  | L | W | H | ( Sqmtr ) | ( Sqfts) | ( Ft ) | (Lux) |  | (watts) |  | ( Nos ) | ( Nos ) | ( Nos ) | (watts) | ( Nos ) | (watts) | ( Nos) | ( Nos) |  |  |  | ( Nos) | ( Nos) | ( Nos) | ( Nos) | ( Nos) | ( Nos)
FIFTH FLOOR
1 | 3M Wide Corridor | 5.96 | 3 | 3 | 17.88 | 192.3888 | 3 | 200 | 0.66518 | 36 | 3600 | 2.7029 | 3 | 2 | 72 | 1 | 36 |  |  |  | 1 |  |  |  | 1 | 1 | 1
2 | UPS Room | 2.1 | 2.06 | 3 | 4.326 | 46.5478 | 3 | 200 | 0.34663 | 24 | 2400 | 1.8824 | 1 | 0 | 0 | 1 | 24 |  |  | 1 | 2 | 2 |  |  | 1 |  | 1
3 | Electrical Room | 2.1 | 2.06 | 3 | 4.326 | 46.5478 | 3 | 200 | 0.34663 | 24 | 2400 | 1.8824 | 1 | 0 | 0 | 1 | 24 |  |  |  | 2 |  |  |  | 1 |  | 1
4 | 3M Wide Corridor | 3 | 9.29 | 3 | 27.87 | 299.8812 | 3 | 200 | 0.7559 | 36 | 3600 | 3.7074 | 3 | 2 | 72 | 1 | 36 |  |  |  | 2 |  |  |  | 1 | 1 | 2
5 | Reception & Nurse Station | 3.4 | 3 | 3 | 10.2 | 109.752 | 3 | 200 | 0.53125 | 24 | 2400 | 2.8959 | 2 | 1 | 24 | 1 | 24 | 1 |  | 1 | 2 | 4 | 2 | 1 | 1 |  | 1 | 1
6 | Record Room | 3.2 | 3 | 3 | 9.6 | 103.296 | 3 | 200 | 0.51613 | 24 | 2400 | 2.8054 | 2 | 1 | 24 | 1 | 24 |  |  |  | 2 |  |  |  | 1 |  | 1
7 | 1.2M Wide Corridor | 3.4 | 1.2 | 3 | 4.08 | 43.9008 | 3 | 200 | 0.29565 | 24 | 2400 | 2.0814 | 2 | 1 | 24 | 1 | 24 |  |  |  | 1 |  |  |  | 1 |  | 1
8 | Counseling Room-1 | 3.28 | 2.69 | 3 | 8.8232 | 94.9376 | 3 | 300 | 0.49264 | 24 | 2400 | 4.052 | 4 | 3 | 72 | 1 | 24 | 1 |  | 1 | 2 | 2 | 2 | 1 | 1 |  | 1
9 | Counseling Room-2 | 3.28 | 2.69 | 3 | 8.8232 | 94.9376 | 3 | 300 | 0.49264 | 24 | 2400 | 4.052 | 4 | 3 | 72 | 1 | 24 | 1 |  | 1 | 2 | 2 | 2 | 1 | 1 |  | 1
10 | Ultrasound | 3.2 | 6.16 | 3 | 19.712 | 212.1011 | 3 | 300 | 0.70199 | 24 | 2400 | 6.3529 | 6 | 4 | 96 | 2 | 48 | 1 |  | 1 | 4 | 4 | 2 |  | 1 |  | 1
11 | Toilet | 1.88 | 1.16 | 3 | 2.1808 | 23.4654 | 3 | 200 | 0.23912 | 12 | 1200 | 2.7511 | 1 | 1 | 12 |  | 0 |  | 1 |  | 2
12 | Semi-Sterile Area | 3 | 3.73 | 3 | 11.19 | 120.4044 | 3 | 300 | 0.55423 | 36 | 3600 | 3.0452 | 2 | 1 | 36 | 1 | 36 |  |  |  | 1 |  |  |  | 1 | 1 | 1
13 | 1.2M Wide Corridor | 3.4 | 1.2 | 3 | 4.08 | 43.9008 | 3 | 300 | 0.29565 | 24 | 2400 | 3.1222 | 3 | 2 | 48 | 1 | 24 |  |  |  | 1 |  |  |  | 1 |  | 1
14 | Change Room-1 | 1 | 1.7 | 3 | 1.7 | 18.292 | 3 | 300 | 0.20988 | 24 | 2400 | 1.8326 | 1 | 0 | 0 | 1 | 24 |  |  |  | 2 |  |  |  | 1 |  | 1
15 | Chang Room-2 | 1 | 1.7 | 3 | 1.7 | 18.292 | 3 | 300 | 0.20988 | 24 | 2400 | 1.8326 | 1 | 0 | 0 | 1 | 24 |  |  |  | 2 |  |  |  | 1 |  | 1
17 | Toilet | 1.2 | 2.42 | 3 | 2.904 | 31.247 | 3 | 200 | 0.2674 | 12 | 1200 | 3.276 | 2 | 1 | 12 | 1 | 12 |  |  |  | 1
18 | Sperm Collection Room | 3.45 | 2.35 | 3 | 8.1075 | 87.2367 | 3 | 300 | 0.46595 | 24 | 2400 | 3.9367 | 4 | 3 | 72 | 1 | 24 | 1 |  | 1 | 2 |  |  |  | 1 |  | 1
19 | Toilet | 1.88 | 1.15 | 3 | 2.162 | 23.2631 | 3 | 200 | 0.23784 | 12 | 1200 | 2.7421 | 1 | 1 | 12 |  | 0 |  | 1 |  | 2
20 | Blood Collection & Injection Room | 3.03 | 2.75 | 3 | 8.3325 | 89.6577 | 3 | 300 | 0.48054 | 24 | 2400 | 3.9231 | 4 | 3 | 72 | 1 | 24 | 1 |  | 1 | 2 | 2 | 1 | 1 | 1 |  | 1
21 | Sterile Area | 3 | 9.21 | 3 | 27.63 | 297.2988 | 3 | 300 | 0.7543 | 36 | 3600 | 5.5249 | 3 | 2 | 72 | 1 | 36 |  |  |  |  | 2 |  |  | 1 | 1 | 2
22 | Andrology Lab | 6.48 | 3.21 | 3 | 20.8008 | 223.8166 | 3 | 400 | 0.71554 | 36 | 3600 | 5.8462 | 4 | 3 | 108 | 1 | 36 | 1 |  | 1 |  | 12 | 2 | 1 |  |  | 1
23 | Cryo Room | 2.43 | 1.6 | 3 | 3.888 | 41.8349 | 3 | 400 | 0.32159 | 36 | 3600 | 2.4314 | 1 |  | 0 | 1 | 36
24 | Autoclave | 3.35 | 3 | 3 | 10.05 | 108.138 | 3 | 300 | 0.52756 | 36 | 3600 | 2.8733 | 2 | 1 | 36 | 1 | 36 | 1 |  | 1 | 2 | 2 | 1 |  | 1 |  | 1
25 | Manifold Room | 2.5 | 3 | 3 | 7.5 | 80.7 | 3 | 300 | 0.45455 | 36 | 3600 | 2.4887 | 1 |  | 0 | 1 | 36 |  |  | 1 |  | 2 | 1 |  | 1 |  | 1
26 | OT-2 | 6.48 | 6.55 | 3 | 42.444 | 456.6974 | 3 | 500 | 1.0858 | 54 | 5400 | 6.551 | 6 | 0 | 0 | 6 | 324 |  |  |  |  | 16 |  |  |  |  | 1
27 | IVF/ICSI/Embriology Lab | 6.48 | 4.19 | 3 | 27.1512 | 292.1469 | 3 | 400 | 0.84821 | 36 | 3600 | 6.4374 | 6 | 4 | 144 | 2 | 72 | 1 |  |  |  | 14 | 4 |  | 1 |  | 1
28 | OT-1 | 6.48 | 5 | 3 | 32.4 | 348.624 | 3 | 500 | 0.94077 | 54 | 5400 | 5.7717 | 6 | 0 | 0 | 6 | 324 |  |  |  | 2 | 16 |  | 1 |  |  | 1
29 | Pre/Post OP | 6.6 | 5.6 | 3 | 36.96 | 397.6896 | 3 | 300 | 1.0098 | 24 | 2400 | 8.2805 | 8 | 5 | 120 | 3 | 72 | 3 |  | 1 | 14 | 14 | 6 | 1 | 1 |  | 1 | 1
30 | Toilet | 1.2 | 2.1 | 3 | 2.52 | 27.1152 | 3 | 200 | 0.25455 | 12 | 1200 | 2.9864 | 1 | 1 | 12 |  | 0 |  | 1 |  | 2
31 | Store Room | 2.17 | 2.06 | 3 | 4.4702 | 48.0994 | 3 | 200 | 0.35226 | 24 | 2400 | 1.914 | 1 | 1 | 24 |  | 0 |  |  |  | 1 |  |  |  | 1 |  | 1
| TOTAL | [11 empty] | 86 | 46 | 1236 | 40 | 1428 | 12 | 3 | 11 | 56 | 94 | 23 | 7 | 22 | 4 | 27 | 2
| Total Load in KW | [13 empty] | 0.71363 |  | 0.82448 | 0.4157 | 0.10393 | 0.6351 | 8.0831 | 13.5681
| Fifth floor Lighting Loads in KW | [12 empty] | 1.2333 | KW
| Fifth floor Raw Power Loads in KW | [12 empty] | 8.7182 | KW
| Fifth floor UPS Lighting Loads in KW | [12 empty] | 0.82448 | KW
| Fifth floor UPS Power Loads in KW | [12 empty] | 13.5681 | KW