## Sheet1
1 OT LOAD DETAILS
S.No | Description | Load in KW | UOM
1 | AC POWER LOAD
2 | AHU 11 TR | 26 | KW
3 | Industrial Socket | 7.6 | KW
4 | UPS LOAD |  | KW
5 | Touch Screen Control Panel | 0.15 | KW
6 | X Ray View screen | 0.15 | KW
7 | Hatch Box | 0.15 | KW
8 | Double Dome OT Light | 1 | KW
9 | Triple Dome OT Light | 1.5 | KW
10 | HD Monitor | 0.15 | KW
11 | Automatic Sliding Main Door 1.8 x 2.1Mtr | 0.15 | KW
12 | Automatic Sliding OT Passage Door 1.5 x2.1 Mtr | 0.15 | KW
13 | Peripheral Light | 0.288 | KW
14 | Power Socket/Switch | 4.96 | KW
15 | View Window | 0.35 | KW
16 | Medical Gas Pendant Anesthesia | 1.5 | KW
17 | Medical Gas Pendant Sugeon | 1.5 | KW
18 | RAW POWER LOAD |  | KW
19 | High End OT Table | 1 | KW
20 | High End Anesthesia Workstation | 0.75 | KW
21 | Suction Apparatus | 0.05 | KW
22 | 7-Para Monitors | 0.1 | KW
23 | Syringe Pumps | 0.05 | KW
24 | Infusion Pumps | 0.05 | KW
25 | Continuous Cardiac Out Put Monitor with Flow Trek | 3 | KW
26 | Advance 4k Laproscopy set for Donar Surgery | 1 | KW
27 | 4K HD Mounted video recorder | 0.25 | KW
28 | Cautery machine with combined Ultrasonic with bipolar energy source for both laproscopic and Open Surgery (Olympus/Jhonson & Jhonson) (or) Ultrasonic cutting & Coagulation device with advance bipolar sealing system (Harmonic scalpel) | 1 | KW
| Total Load | 52.848 | KW
| Diversity Factor (0.8) | 42.2784 | KW
| Total KVA at 0.8 P.F | 52.848 | KVA
| Miscellaneous loads 10% | 5.2848 | KVA
| Total KVA | 58.1328 | KVA