## SUMMARY
CLIENT :
PROJECT :GANDHI HOSPITAL_8TH FLOOR
DOC NAME : LOAD SUMMARY SHEET
DOC NUMBER : MECS/2023/GH/8TH/ELE/05
DATE : 12.01.2024
REVISION R3
SL.No | DESCRIPTION | CONNECTING LOAD (KW) | DIVERSITY FACTOR | MAXIMUM LOAD (KW)
1 | Lighting Load | 4.3793 | 0.9 | 3.9414
2 | RAW power Load | 66.1085 | 0.7 | 46.276
3 | Emergency Lighting Load | 1.2471 | 0.9 | 1.1224
4 | UPS power Load | 36.9515 | 0.7 | 25.8661
5 | AC Loads | 73.8 | 0.8 | 59.04
6 | Equipment in CSSD | 77.5982 | 0.8 | 62.0785
7 | OT Medical Equipment UPS load in kw (total 6 OTs) | 38.9388 | 0.8 | 31.151
8 | TIR Medical Equipment UPS load in kw (total 3 TIRs) | 14.664 | 0.8 | 11.7312
9 | Integrated Room UPS Loads | 3.0572 | 0.8 | 2.4457
10 | OT & TIR AC & Other Load in KW | 294.4 | 0.8 | 235.52
11 | Lift Load (1No each 26KW) | 26 | 0.8 | 20.8
| TOTAL | 637.1446 |  | 499.9723
Load in KW |  | 637.1446 | KW | 499.9723
Total Load in KW |  |  | KW | 499.9723
Group Diversity @80% |  |  | KW | 399.9778
Total KVA at 0.80 P.F |  |  | KVA | 499.9723
80% loading on tranformer capacity |  |  | KVA | 624.9654
(As per the Load Calculation we required 630KVA Transformer with 100% DG backup
UPS LOAD CALCULATION
1 | Emergency Lighting Load | 1.2471 | 0.9 | 1.1224
2 | UPS power Load | 36.9515 | 0.7 | 25.8661
Total Maximum Demand |  |  |  | 26.9885
Total KVA at 0.85 Power Factor |  |  |  | 31.7511
Considering 80% Efficiency on UPS Selection |  |  |  | 39.6889
(As the near by UPS rating available in market is 20KVA ) .So we recommend = 2 no's 20KVA.
No of Batteries
Total Rated KVA |  |  | 20 | KVA
Battery Power |  |  | 150 | AH
Battery Voltage |  |  | 12 | V
Backup Time |  |  | 1.5 | Hour
No of Batteries |  |  | 30.8333 | Nos
As the Recommended Batteries are 32Nos of 150AH for Each 20KVA UPS
EACH OT UPS LOAD CALCULATION
1 | OT Medical Equipment UPS load in kw (Total 6 OTs) | 38.9388 | 0.8 | 31.151
Total Maximum Demand |  |  |  | 31.151
Total KVA at 0.85 Power Factor |  |  |  | 36.6483
Considering 80% Efficiency on UPS Selection |  |  |  | 45.8104
(As the near by UPS rating available in market is 10KVA ) .So we recommend = 1 no's 10KVA each OT. ( total 6Nos 10KVA UPS for 6 OTs)
No of Batteries
Total Rated KVA |  |  | 10 | KVA
Battery Power |  |  | 150 | AH
Battery Voltage |  |  | 12 | V
Backup Time |  |  | 4 | Hour
No of Batteries |  |  | 31.1111 | Nos
As the Recommended Batteries are 32Nos of 150AH for Each 10KVA UPS
EACH TIR UPS LOAD CALCULATION
1 | TIR Medical Equipment UPS load in kw (Total 3 TIRs) | 14.664 | 0.8 | 11.7312
2 | Integrated Room UPS Loads | 3.0572 | 0.8 | 2.4457
Total Maximum Demand |  |  |  | 14.1769
Total KVA at 0.85 Power Factor |  |  |  | 16.6787
Considering 80% Efficiency on UPS Selection |  |  |  | 20.8484
(As the near by UPS rating available in market is 10KVA ) .So we recommend = 1 no's 10KVA each TIR. ( total 3Nos 10KVA UPS for 3 TIRs)
No of Batteries
Total Rated KVA |  |  | 10 | KVA
Battery Power |  |  | 150 | AH
Battery Voltage |  |  | 12 | V
Backup Time |  |  | 4 | Hour
No of Batteries |  |  | 31.1111 | Nos
As the Recommended Batteries are 32Nos of 150AH for Each10KVA UPS

## URS
CLIENT :
| PROJECT : | GANDHI HOSPITAL_8TH FLOOR
| DOC NAME : | USER REQUIRED SPECS
| DOC NUMBER : | MECS/2023/GH/8TH/ELE/01
| DATE : | 09.01.2023
| REVISION | R2
[8 empty] | ELECTRICAL | [14 empty] | LV SYSTEMS
Sl.No | Description of the room | Room size in mtrs |  |  | Area |  | F/C HT | Lux Levels | Room Index | Wattage light | Fixtures Lumen | No of Fixtures | No of Fixtures | Raw power Lighting |  | UPS power Lighting |  | FANS |  | AC SOCKET | RAW POWER SOCKET | UPS | LAN/Data | Tele phone | PA System | CCTV | FA SYSTEM | Nursical Point
[18 empty] | CEILING | EXHAUST | 20A | 6/16A | 6/16A
|  | L | W | H | ( Sqmtr ) | ( Sqfts) | ( Ft ) | (Lux) |  | (watts) |  | ( Nos ) | ( Nos ) | ( Nos ) | (watts) | ( Nos ) | (watts) | ( Nos) | ( Nos) |  |  |  | ( Nos) | ( Nos) | ( Nos) | ( Nos) | ( Nos) | ( Nos)
EIGHTH FLOOR
1 | Toilet | 5.74 | 3.3 | 3 | 18.942 | 203.8159 | 3 | 200 | 0.69845 | 12 | 1200 | 8.181 | 16 | 11 | 132 | 5 | 60 |  |  |  | 2
2 | Electrical Room | 6.72 | 2.7 | 3 | 18.144 | 195.2294 | 3 | 200 | 0.64204 | 24 | 2400 | 4.2624 | 2 | 1 | 24 | 1 | 24 |  |  |  | 2 |  |  |  | 1 |  | 1
3 | Reception | 5.15 | 2.43 | 3 | 12.5145 | 134.656 | 3 | 200 | 0.55033 | 24 | 2400 | 3.4299 | 2 | 1 | 1
4 | UPS Room | 3.23 | 5 | 3 | 16.15 | 173.774 | 3 | 200 | 0.65411 | 24 | 2400 | 3.724 | 2
5 | Entry Corridor | 2.9 | 6.08 | 3 | 17.632 | 189.7203 | 3 | 200 | 0.65449 | 36 | 3600 | 2.7089 | 2 | 1 | 36 | 1 | 36 |  |  |  | 1 |  |  |  | 1 | 1 | 1
6 | Corridor-1 | 10.03 | 2.9 | 3 | 29.087 | 312.9761 | 3 | 200 | 0.74986 | 36 | 3600 | 3.9005 | 4 | 3 | 108 | 1 | 36 |  |  |  | 2 |  |  |  | 1 |  | 2
7 | Waiting Area | 6.53 | 5.26 | 3 | 34.3478 | 369.5823 | 3 | 300 | 0.9711 | 36 | 3600 | 5.3348 | 6 | 4 | 144 | 2 | 72 | 2 |  |  | 2 |  |  |  | 1 | 1 | 1
8 | Trolley Bay | 3.27 | 5.26 | 3 | 17.2002 | 185.0742 | 3 | 200 | 0.67215 | 24 | 2400 | 3.8597 | 4 | 3 | 72 | 1 | 24 |  |  |  | 1 |  |  |  | 1 |  | 1
9 | Corridor-2 | 10.52 | 2.9 | 3 | 30.508 | 328.2661 | 3 | 200 | 0.75777 | 36 | 3600 | 4.0483 | 3 | 2 | 72 | 1 | 36 |  |  |  | 1 |  |  |  | 1 | 1 | 2
10 | MOT'S Integration & Control Panel Room | 10.32 | 5.74 | 3 | 59.2368 | 637.388 | 3 | 300 | 1.2295 | 36 | 3600 | 7.267 | 8 | 5 | 180 | 3 | 108 | 3 |  | 2 | 4 | 4 |  |  | 1 |  | 2
11 | Corridor-3 | 16.66 | 2.9 | 3 | 48.314 | 519.8586 | 3 | 200 | 0.82335 | 36 | 3600 | 5.9005 | 5 | 3 | 108 | 2 | 72 |  |  |  | 3 |  |  |  | 2 | 2 | 3
12 | Post OP I.C.U | 14.27 | 5.74 | 3 | 81.9098 | 881.3494 | 3 | 300 | 1.3645 | 36 | 3600 | 9.0543 | 8 | 5 | 180 | 3 | 108 | 12 |  | 2 | 34 | 90 | 12 | 1 | 1 |  | 2
13 | Toilet | 3.22 | 5.74 | 3 | 18.4828 | 198.8749 | 3 | 200 | 0.6876 | 12 | 1200 | 8.1086 | 8 | 7 | 84 | 1 | 12 |  | 1 |  | 1
14 | Janitor | 1.48 | 1.81 | 3 | 2.6788 | 28.8239 | 3 | 200 | 0.27141 | 12 | 1200 | 2.9774 | 1 |  | 0 | 1 | 12 |  |  |  | 1
15 | Corridor-4 | 2.9 | 10.66 | 3 | 30.914 | 332.6346 | 3 | 200 | 0.75993 | 36 | 3600 | 4.0905 | 4 | 3 | 108 | 1 | 36 |  |  |  | 2 |  |  |  | 1 | 2 | 2
16 | Staircase | 5.83 | 6.83 | 3 | 39.8189 | 428.4514 | 3 | 200 | 1.0484 | 36 | 3600 | 3.819 | 4 | 2 | 72 | 2 | 72
17 | Electrical Room | 5.9 | 2.1 | 3 | 12.39 | 133.3164 | 3 | 200 | 0.51625 | 24 | 2400 | 3.6199 | 4 | 2 | 48 | 2 | 48 |  |  |  | 2 |  |  |  | 1 |  | 1
18 | Corridor-5 | 2.9 | 28.43 | 3 | 82.447 | 887.1297 | 3 | 200 | 0.87719 | 36 | 3600 | 9.451 | 10 | 7 | 252 | 3 | 108 |  |  |  | 4 |  |  |  | 2 | 4 | 5
19 | Anesthetist Lounge | 5.19 | 5.74 | 3 | 29.7906 | 320.5469 | 3 | 300 | 0.90853 | 36 | 3600 | 4.9457 | 3 | 2 | 72 | 1 | 36 | 1 |  | 1 | 3 | 2 | 2 | 1 | 1 |  | 1
20 | Toilet | 1.4 | 1.47 | 3 | 2.058 | 22.1441 | 3 | 200 | 0.23902 | 12 | 1200 | 2.5973 | 1 | 1 | 12 |  | 0 |  | 1 |  | 1
21 | Surgeon's Lounge | 5.19 | 5.74 | 3 | 29.7906 | 320.5469 | 3 | 300 | 0.90853 | 36 | 3600 | 4.9457 | 4 | 3 | 108 | 1 | 36 | 1 |  | 1 | 3 | 2 | 2 | 1 | 1 |  | 1
22 | Toilet | 1.4 | 1.6 | 3 | 2.24 | 24.1024 | 3 | 200 | 0.24889 | 12 | 1200 | 2.7149 | 1 | 1 | 12 |  | 0 |  | 1 |  | 1
23 | Corridor-6 | 15.12 | 2.9 | 3 | 43.848 | 471.8045 | 3 | 200 | 0.8111 | 36 | 3600 | 5.4359 | 5 | 3 | 108 | 2 | 72 |  |  |  | 3 |  |  |  | 2 | 1 | 3
24 | Clean Store | 3 | 3.18 | 3 | 9.54 | 102.6504 | 3 | 200 | 0.51456 | 36 | 3600 | 1.8643 | 1 |  | 0 | 1 | 36 |  |  |  | 1 |  |  |  | 1 |  | 1
25 | Sterile Store Room | 5.74 | 5.74 | 3 | 32.9476 | 354.5162 | 3 | 200 | 0.95667 | 36 | 3600 | 3.463 | 4 | 3 | 108 | 1 | 36 |  |  |  | 2 | 2 |  |  | 1 |  | 1
26 | Point of Care Lab | 7.74 | 5.74 | 3 | 44.4276 | 478.041 | 3 | 400 | 1.0986 | 36 | 3600 | 8.1327 | 6 | 4 | 144 | 2 | 72 | 2 |  | 1 | 2 | 2 |  |  | 1 |  | 1
27 | Wash Area | 4.57 | 1.8 | 3 | 8.226 | 88.5118 | 3 | 200 | 0.43046 | 12 | 1200 | 5.7647 | 2 | 1 | 12 | 1 | 12 |  |  |  | 1
28 | Lab Store | 4.57 | 3.84 | 3 | 17.5488 | 188.8251 | 3 | 200 | 0.69555 | 24 | 2400 | 3.8054 | 4 | 3 | 72 | 1 | 24 |  |  |  | 2 |  |  |  | 1 |  | 1
29 | Corridor-7 | 28.14 | 2.9 | 3 | 81.606 | 878.0806 | 3 | 200 | 0.87635 | 36 | 3600 | 9.3635 | 9 | 6 | 216 | 3 | 108 |  |  |  | 3 |  |  |  | 2 | 4 | 5
30 | Staircase | 9.03 | 7.4 | 3 | 66.822 | 719.0047 | 3 | 200 | 1.3557 | 36 | 3600 | 4.9563 | 6 | 4 | 144 | 2 | 72
31 | CSSD | 6.25 | 5.74 | 3 | 35.875 | 386.015 | 3 | 300 | 0.99736 | 24 | 2400 | 8.138 | 6 | 4 | 96 | 2 | 48 | 1 |  | 1 | 4 | 4 |  |  | 1 |  | 1
32 | Clean Utility | 1.8 | 2.83 | 3 | 5.094 | 54.8114 | 3 | 200 | 0.36674 | 24 | 2400 | 2.095 | 1 |  | 0 | 1 | 24 |  |  |  | 1 |  |  |  | 1 |  | 1
33 | Dirty Utility | 1.8 | 5.74 | 3 | 10.332 | 111.1723 | 3 | 200 | 0.45676 | 24 | 2400 | 3.4118 | 3 | 2 | 48 | 1 | 24 |  |  |  | 1 |  |  |  | 1 |  | 1
34 | Toilet | 3.65 | 4.83 | 3 | 17.6295 | 189.6934 | 3 | 200 | 0.69298 | 12 | 1200 | 7.6742 | 5 | 4 | 48 | 1 | 12 |  | 2 |  | 1
35 | General Store | 3.42 | 3.35 | 3 | 11.457 | 123.2773 | 3 | 200 | 0.56411 | 24 | 2400 | 3.0633 | 4 | 3 | 72 | 1 | 24 |  |  |  | 2 |  |  |  | 1 |  | 1
36 | Corridor-8 | 2.9 | 18.07 | 3 | 52.403 | 563.8563 | 3 | 200 | 0.83298 | 36 | 3600 | 6.3258 | 6 | 4 | 144 | 2 | 72 |  |  |  | 4 |  |  |  | 2 | 2 | 3
37 | Passage | 5.74 | 1.68 | 3 | 9.6432 | 103.7608 | 3 | 200 | 0.43321 | 24 | 2400 | 3.3575 | 3 | 2 | 48 | 1 | 24 |  |  |  | 1 |  |  |  | 1 |  | 1
38 | Toilet | 6.43 | 3.35 | 3 | 21.5405 | 231.7758 | 3 | 200 | 0.73417 | 12 | 1200 | 8.8507 | 7 | 6 | 72 | 1 | 12 |  | 2 |  | 2
39 | Transplant I.C.U | 5.74 | 14.27 | 3 | 81.9098 | 881.3494 | 3 | 300 | 1.3645 | 36 | 3600 | 9.0543 | 10 | 6 | 216 | 4 | 144 | 12 |  | 2 | 34 | 94 | 13 | 1 | 1 |  | 2
40 | Corridor-9 | 2.9 | 11.79 | 3 | 34.191 | 367.8952 | 3 | 200 | 0.77583 | 36 | 3600 | 4.4314 | 4 | 3 | 108 | 1 | 36 |  |  |  | 2 |  |  |  | 1 | 1 | 2
41 | Room | 5.74 | 8.85 | 3 | 50.799 | 546.5972 | 3 | 300 | 1.1606 | 36 | 3600 | 6.6018 | 6 | 4 | 144 | 2 | 72 | 6 |  | 2 | 12 | 48 | 6 | 1 | 1 |  | 2
42 | Toilet | 5.74 | 3.35 | 3 | 19.229 | 206.904 | 3 | 200 | 0.70513 | 12 | 1200 | 8.2262 | 7 | 6 | 72 | 1 | 12 |  | 3 |  | 2
43 | H.O.D. Room-1 | 5.74 | 3.3 | 3 | 18.942 | 203.8159 | 3 | 300 | 0.69845 | 24 | 2400 | 6.1357 | 5 | 4 | 96 | 1 | 24 | 1 |  | 1 | 2 | 2 | 2 | 1 | 1 |  | 1
44 | Toilet | 1.4 | 1.6 | 3 | 2.24 | 24.1024 | 3 | 200 | 0.24889 | 12 | 1200 | 2.7149 | 1 | 1 | 12 |  | 0 |  | 1 |  | 1
45 | Counselling Room | 5.74 | 2.4 | 3 | 13.776 | 148.2298 | 3 | 300 | 0.56413 | 24 | 2400 | 5.5249 | 3 | 2 | 48 | 1 | 24 | 1 |  | 1 | 2 | 2 | 2 | 1 | 1 |  | 1
46 | Durty Nurses Room | 5.74 | 2.4 | 3 | 13.776 | 148.2298 | 3 | 300 | 0.56413 | 24 | 2400 | 5.5249 | 2 | 1 | 24 | 1 | 24 | 1 |  |  | 2 | 2 | 2 | 1 | 1 |  | 1
47 | Toilet | 1.4 | 1.6 | 3 | 2.24 | 24.1024 | 3 | 200 | 0.24889 | 12 | 1200 | 2.7149 | 1 | 1 | 12 |  | 0 |  | 1 |  | 1
48 | Change Rooms | 5.74 | 5.6 | 3 | 32.144 | 345.8694 | 3 | 300 | 0.94486 | 24 | 2400 | 7.6968 | 7 | 2 | 48 | 5 | 120 |  |  |  | 5 |  |  |  | 1 |  | 5
49 | Corridor-10 | 17.86 | 2.9 | 3 | 51.794 | 557.3034 | 3 | 200 | 0.83163 | 36 | 3600 | 6.2624 | 6 | 4 | 144 | 2 | 72 |  |  |  | 3 |  |  |  | 2 | 2 | 3
50 | Doctors Room | 6.1 | 3.5 | 3 | 21.35 | 229.726 | 3 | 300 | 0.74132 | 24 | 2400 | 6.5158 | 5 | 3 | 72 | 1 | 24 | 1 |  | 1 | 2 | 2 | 2 | 1 | 1 |  | 1
51 | Toilet | 1.4 | 1.6 | 3 | 2.24 | 24.1024 | 3 | 200 | 0.24889 | 12 | 1200 | 2.7149 | 1 | 1 | 12 |  | 0 |  | 1 |  | 1
| TOTAL | [11 empty] | 232 | 154 | 4165 | 74 | 2160 | 44 | 13 | 15 | 169 | 256 | 43 | 9 | 41 | 21 | 63 | 0
| Total Load in KW | [13 empty] | 2.4047 |  | 1.2471 | 1.5242 | 0.45035 | 17.321 | 48.7875 | 36.9515
| Eighth floor Lighting Loads in KW | [12 empty] | 4.3793 | KW
| Eighth floor Raw Power Loads in KW | [12 empty] | 66.1085 | KW
| Eighth floor UPS Lighting Loads in KW | [12 empty] | 1.2471 | KW
| Eighth floor UPS Power Loads in KW | [12 empty] | 36.9515 | KW

## AC LOADS
CLIENT :
PROJECT : |  | GANDHI HOSPITAL_8TH FLOOR
DOC NAME : |  | USER REQUIRED SPECS
DOC NUMBER : |  | MECS/2023/GH/8TH/ELE/02
DATE : |  | 09.01.2023
REVISION |  | R2
AC LOADS FOR COMMON AREAS
S.NO | DESCRIPTION | QTY | POWER IN KW | TOTAL LOAD | CONNTECTED LOAD IN KW
1 | 5.5TR Ductable ODU Unit | 3 | 6.6 | 19.8 | 19.8
2 | 8.5TR Ductable ODU Unit | 4 | 10.2 | 40.8 | 40.8
3 | 11TR Ductable ODU Unit | 1 | 13.2 | 13.2 | 13.2
| HVAC Load |  |  |  | 73.8

## CSSD LOADS
CLIENT :
PROJECT : |  | GANDHI HOSPITAL_8TH FLOOR
DOC NAME : |  | USER REQUIRED SPECS
DOC NUMBER : |  | MECS/2023/GH/8TH/ELE/03
DATE : |  | 09.01.2023
REVISION |  | R2
List of Items under State Organ Transplant Center (SOTC) at Gandhi Hospital.
Sl. No. | Name of the Equipment | Qty | Phase | Approx. Power(KW)
1 | High End OT Tables | 3 | Single Phase | 3
2 | Mid Range OT Tables (C-Arm compatible) | 1 | Single Phase | 2
3 | High End Anesthesia Work Station | 4 | Single Phase | 3
4 | High End Diathermy with Ligasure (FT 10) | 4 | Single Phase | 3
5 | Suction Apparatus | 8 | Single Phase | 0.37
6 | CRRT | 1 | Single Phase | 0.4
7 | Mobile X-Ray Unit | 1 | Single Phase | 5
8 | HD Machine | 4 | Single Phase | 0.4
9 | Defibrillator | 3 | Single Phase | 2
10 | ECG Machines | 3 | Single Phase | 1
11 | Intra Operative Ultra Sound With Doppler | 1 | Single Phase | 3
12 | High End Fowler Beds | 5 | Single Phase | 3
13 | 7-PARA Monitors | 12 | Single Phase | 1
14 | Regular Monitors | 12 | Single Phase | 1
15 | ABG Machine | 1 | Single Phase | 3
16 | Cell Counter | 1 | Single Phase | 3
17 | Fully Automatic Auto Analyzer (200 Tests) | 1 | Single Phase | 3
18 | Portable RO Unit | 1 | Single Phase | 7
19 | Ultrasonic Nebulizer Machine | 4 | Single Phase | 0.5
20 | Mid range C-arm for kidney | 1 | Single Phase | 3.5
21 | High End C-Arm | 1 | Single Phase | 3.5
22 | Syringe Pumps | 40 | Single Phase | 0.5
23 | Infusion Pumps | 25 | Single Phase | 0.5
24 | Bayer Hugger Machine | 6 | Single Phase | 1
25 | DVT Pumps | 12 | Single Phase | 0.3
26 | Continuous Cardiac Out Put Monitor With Flow Trek | 1 | Single Phase | 3
27 | Refrigerator -80 Degree C | 1 | Single Phase | 3
28 | Refrigerator 480 Litrs | 5 | Single Phase | 5
29 | Ice Maker | 1 | Single Phase | 0.2
30 | Plasma Sterilizer | 1 | Single Phase | 1
31 | Fluid warmers (hotline) | 10 | Single Phase | 0.5
32 | High End Teaching Microscope | 1 | Single Phase | 2
33 | Digital Video Broncho scope (Adult & Pediatric) | 1 | Single Phase | 2
34 | VYTEK | 1 | Single Phase | 3
35 | BACTALERT | 1 | Single Phase | 3
36 | Frozen Section Lica | 1 | Single Phase | 3
37 | Antigen Retriever | 1 | Single Phase | 3
38 | Immuno Flouroscence | 1 | Single Phase | 3
39 | Pediatric Endoscope Set | 1 | Single Phase | 5
40 | Endo Washer | 1 | Single Phase | 3
41 | Co2 Insufflator For Endo Compatible | 1 | Single Phase | 1
42 | Spiral Enteroscope | 1 | Single Phase | 2
43 | High Definition Laparoscopic Set for Donor Nephrectomy - List Enclosed | 1 | Single Phase | 5
44 | Cautery machine with combined Ultrasonic with bipolar energy source for both Laparoscopic and Open Surgery (Olympus/ Johnson & Johnson) (OR) Ultrasonic Cutting & Coagulation device with advance bipolar sealing system (Harmonic scalpel) | 1 | Single Phase | 1
45 | CUSA | 1 | Single Phase | 0.5
46 | Advanced 4k Laparoscopy Set For Donor Surgery | 1 | Single Phase | 1
47 | Argon Plasma Coagulator | 1 | Single Phase | 0.5
48 | Rapid Infusor | 1 | Single Phase | 0.2
49 | Head Light Ultra Mini | 2 | Single Phase | 0.1
50 | 4K HD Head Mounted Video Recorder | 1 | Single Phase | 0.25
51 | TEG with Coagulation Analyzer | 1 | Single Phase | 0.2
52 | High End Suction Operators | 4 | Single Phase | 0.5
53 | Harmonic Scalpel | 2 | Single Phase | 0.5
54 | Plasmapheresis Machine | 1 | Single Phase | 0.5
55 | High End Operating Micro Scope | 1 | Single Phase | 0.5
56 | High End Digital Weight Recording Machine | 2 | Single Phase | 0.5
57 | Radiofrequency Ablator | 1 | Single Phase | 0.25
58 | Fibre Optic Choledocho Scope | 1 | Single Phase | 0.25
| Total Single Phase Load in KW |  | Single Phase | 108.42
| Total 3PH Load in KW |  | 3 Phase | 62.5982
59 | High End Auto Clave | 1 | 3 Phase | 10
60 | ETO Sterilizer | 1 | 3 Phase | 5
| Total Connecting Load 3PH Load in KW |  | 3 Phase | 77.5982

## OT & TIR LOADS
CLIENT : MPS ASTA CONSORTIUM
PROJECT :GANDHI HOSPITAL_8TH FLOOR
DOC NAME : OT & TIR Loads
DOC NUMBER : MECS/2023/GH/8TH/ELE/04
DATE : 05.01.2024
REVISION R1
SL.No | DESCRIPTION | LOAD IN WATTS (W) | Total Qty | CONNECTING LOAD (W)
Modular Operation Theatre
1 | Touch Screen Control Panel | 150 | 6 | 900
2 | X Ray View screen | 150 | 6 | 900
3 | Hatch Box | 150 | 6 | 900
4 | Double Dome OT Light | 1000 | 4 | 4000
5 | Triple Dome OT Light | 1500 | 2 | 3000
6 | HD Monitor | 150 | 6 | 900
7 | Automatic Sliding Main Door 1.8 x 2.1Mtr | 150 | 6 | 900
8 | Automatic Sliding OT Passage Door 1.5 x2.1 Mtr | 150 | 2 | 300
9 | Peripheral Light | 36 | 48 | 1728
10 | Power Socket/Switch | 650 | 48 | 31200
11 | View Window | 350 | 11 | 3850
12 | Medical Gas Pendant Anesthesia | 1500 | 6 | 9000
13 | Medical Gas Pendant Sugeon | 1500 | 6 | 9000
14 | PeripheralLights(Corridoor) | 36 | 24 | 864
| ( Total Watt ) |  |  | 67442
| ( Total Kilowatt ) ( Single Phase ) |  |  | 67.442
| ( Total Kilowatt ) ( Three Phase ) |  |  | 38.9388
SL.No | DESCRIPTION | Electrical LOAD (Watt) | Total Qty | MAXIMUM LOAD (W)
TIRs
1 | Power Socket/Switch | 650 | 24 | 15600
2 | Bed Head Panel | 2500 | 3 | 7500
3 | Automatic Sliding Main Door 1.8 x 2.1Mtr | 150 | 3 | 450
4 | Glass Slinding Door | 150 | 3 | 450
5 | Peripheral Light | 36 | 18 | 648
6 | X Ray View screen | 150 | 5 | 750
| ( Total Watt ) |  |  | 25398
| ( Total Kilowatt ) ( Single Phase ) |  |  | 25.398
| ( Total Kilowatt ) ( Three Phase ) |  |  | 14.664
3 Phase Raw Power
SL.No | DESCRIPTION 3 Phase Raw Power | Electrical LOAD (KiloWatt) | Total Qty | MAXIMUM LOAD (KW)
1 | Industrial Socket (MOT) | 7.6 | 6 | 45.6
2 | AHU 11 TR (MOT) | 26 | 6 | 156
3 | Industrial Socket (TIR) | 7.6 | 3 | 22.8
4 | AHU 8.5 TR(TIR) | 20 | 1 | 20
5 | AHU 11 TR(TIR) | 25 | 2 | 50
| Total KW ( 3 Phase ) |  |  | 294.4
SL.No | DESCRIPTION | Electrical LOAD (Watt) | Total Qty | MAXIMUM LOAD (W)
Integration
1 | Medical Grade Monitors 32 inch 4 K Resolution | 100 | 6 | 600
2 | Ceiling/Wall mounted CCTV Room Camera | 25 | 17 | 425
3 | Wall mounted large screen display 55 inch (Commercial Grade) | 150 | 3 | 450
4 | Wireless Microphone | 25 | 1 | 25
5 | Digital mixer Amplifier | 500 | 1 | 500
6 | Ceiling Mounted Speakers | 20 | 9 | 180
7 | Video Conferencing System | 100 | 1 | 100
8 | Home Theatre Power Conditioner, 230 V | 1100 | 1 | 1100
9 | Amplifier (8 Channel) | 600 | 1 | 600
10 | HiFi Active Sub Woofer | 200 | 1 | 200
11 | 4K Laser Projection TV | 350 | 1 | 350
12 | Equalization & Loud Speaker Control System | 350 | 1 | 350
13 | Sound Analog Mixer | 25 | 1 | 25
14 | Wall mounted LED TV43 inchesFull HD | 130 | 3 | 390
| ( Total Watt ) |  |  | 5295
| ( Total Kilowatt ) ( Single Phase ) |  |  | 5.295
| ( Total Kilowatt ) ( Three Phase ) |  |  | 3.0572
| TOTAL | 4436 |  | 48578
Load in KW |  | 4436 | KW | 48578
Total Load in KW |  |  | KW | 48578
Group Diversity @85% |  |  | KW | 41291.3
Total KVA at 0.80 P.F |  |  | KVA | 51614.125
80% loading on tranformer capacity |  |  | KVA | 64517.6562
(As per the Load Calculation we required 800 KVA Transformer with 100% DG backup)
UPS LOAD CALCULATION
Total Maximum Demand |  |  | #REF! | KW
Total KVA at 0.80 Power Factor |  |  | #REF! | KVA
Considering 70% Efficiency on UPS Selection |  |  | #REF! | KVA
(As the near by UPS rating available in market is 10KVA ) .So we recommend = 10 no's 10KVA & 2 no's 20KVA
No of Batteries
Total Rated KVA |  |  | 10 | KVA
Battery Power |  |  | 120 | AH
Battery Voltage |  |  | 12 | V
Backup Time |  |  | 0.5 | Hour
No of Batteries |  |  | 32 | Nos
As the Recommended Batteries are 32Nos of 120AH for Each 10KVA UPS
As the Recommended Batteries are 32Nos of 120AH for Each 20KVA UPS