## SUMMARY
CLIENT :
PROJECT :GANDHI HOSPITAL_8TH FLOOR
DOC NAME : LOAD SUMMARY SHEET
DOC NUMBER : MECS/2023/GH/8TH/ELE/02
DATE : 15.03.2023
REVISION R0
SL.No | DESCRIPTION | CONNECTING LOAD (KW) | DIVERSITY FACTOR | MAXIMUM LOAD (KW)
1 | Lighting Load | 4.5242 | 0.9 | 4.0718
2 | RAW power Load | 46.9111 | 0.7 | 32.8378
3 | Emergency Lighting Load | 1.7945 | 0.9 | 1.615
4 | UPS power Load | 30.6005 | 0.7 | 21.4203
5 | AC Loads | 100 | 0.8 | 80
7 | Medical Equipment Load | 15 | 0.6 | 9
| TOTAL | 198.8303 |  | 148.9449
Load in KW |  | 198.8303 | KW | 148.9449
Total Load in KW |  |  | KW | 148.9449
Group Diversity @75% |  |  | KW | 111.7087
Total KVA at 0.90 P.F |  |  | KVA | 124.1208
(As per the Load Calculation we required 125KVA Load from Floor Panel with 100% DG backup
UPS LOAD CALCULATION
Total Maximum Demand |  |  | 23.0353 | KW
Total KVA at 0.80 Power Factor |  |  | 28.7942 | KVA
Considering 80% Efficiency on UPS Selection |  |  | 35.9927 | KVA
(As the near by UPS rating available in market is 40KVA ) .So we recommend = 1 no's 40KVA.
No of Batteries
Total Rated KVA |  |  | 40 | KVA
Battery Power |  |  | 48 | AH
Battery Voltage |  |  | 12 | V
Backup Time |  |  | 0.5 | Hour
No of Batteries |  |  | 49.1898 | Nos
As the Recommended Batteries are 50Nos of 48AH for Each 40KVA UPS

## URS
CLIENT :
| PROJECT : | GANDHI HOSPITAL_8TH FLOOR
| DOC NAME : | USER REQUIRED SPECS
| DOC NUMBER : | MECS/2023/GH/8TH/ELE/01
| DATE : | 16.03.2023
| REVISION | R0
[8 empty] | ELECTRICAL | [14 empty] | LV SYSTEMS
Sl.No | Description of the room | Room size in mtrs |  |  | Area |  | F/C HT | Lux Levels | Room Index | Wattage light | Fixtures Lumen | No of Fixtures | No of Fixtures | Raw power Lighting |  | UPS power Lighting |  | FANS |  | AC SOCKET | RAW POWER SOCKET | UPS | LAN/Data | Tele phone | PA System | CCTV | FA SYSTEM | Nursical Point
[18 empty] | CEILING | EXHAUST | 20A | 6/16A | 6/16A
|  | L | W | H | ( Sqmtr ) | ( Sqfts) | ( Ft ) | (Lux) |  | (watts) |  | ( Nos ) | ( Nos ) | ( Nos ) | (watts) | ( Nos ) | (watts) | ( Nos) | ( Nos) |  |  |  | ( Nos) | ( Nos) | ( Nos) | ( Nos) | ( Nos) | ( Nos)
EIGHTH FLOOR
1 | Gents Toilet | 10.99 | 7.09 | 3 | 77.9191 | 838.4095 | 3 | 200 | 1.4366 | 12 | 1200 | 16.362 | 16 | 11 | 132 | 5 | 60 |  |  |  | 2
2 | Electrical Room | 4.5 | 2.5 | 3 | 11.25 | 121.05 | 3 | 200 | 0.53571 | 24 | 2400 | 3.1674 | 2 | 1 | 24 | 1 | 24 |  |  |  | 2 |  |  |  | 1 |  | 1
3 | Entry Corridor | 2.9 | 6.08 | 3 | 17.632 | 189.7203 | 3 | 200 | 0.65449 | 36 | 3600 | 2.7089 | 2 | 1 | 36 | 1 | 36 |  |  |  | 1 |  |  |  | 1 | 1 | 1
4 | Corridor-1 | 10.03 | 2.9 | 3 | 29.087 | 312.9761 | 3 | 200 | 0.74986 | 36 | 3600 | 3.9005 | 4 | 3 | 108 | 1 | 36 |  |  |  | 2 |  |  |  | 1 |  | 2
5 | Waiting Area | 6.53 | 5.26 | 3 | 34.3478 | 369.5823 | 3 | 300 | 0.9711 | 24 | 2400 | 8.0023 | 6 | 4 | 96 | 2 | 48 | 2 |  |  | 2 |  |  |  | 1 | 1 | 1
6 | Trolley Bay | 3.27 | 5.26 | 3 | 17.2002 | 185.0742 | 3 | 200 | 0.67215 | 24 | 2400 | 3.8597 | 4 | 3 | 72 | 1 | 24 |  |  |  | 1 |  |  |  | 1 |  | 1
7 | Corridor-2 | 10.52 | 2.9 | 3 | 30.508 | 328.2661 | 3 | 200 | 0.75777 | 36 | 3600 | 4.0483 | 3 | 2 | 72 | 1 | 36 |  |  |  | 1 |  |  |  | 1 | 1 | 2
8 | MOT'S Integration & Control Panel Room | 10.32 | 5.74 | 3 | 59.2368 | 637.388 | 3 | 300 | 1.2295 | 36 | 3600 | 7.267 | 8 | 5 | 180 | 3 | 108 | 3 |  | 2 | 4 | 4 |  |  | 1 |  | 2
9 | Corridor-3 | 16.66 | 2.9 | 3 | 48.314 | 519.8586 | 3 | 200 | 0.82335 | 36 | 3600 | 5.9005 | 5 | 3 | 108 | 2 | 72 |  |  |  | 3 |  |  |  | 2 | 2 | 3
10 | Post OP I.C.U | 14.27 | 5.74 | 3 | 81.9098 | 881.3494 | 3 | 400 | 1.3645 | 36 | 3600 | 12.0724 | 12 | 8 | 288 | 4 | 144 |  |  | 2 | 34 | 34 | 12 | 1 | 1 |  | 2
11 | Toilet | 3.22 | 5.74 | 3 | 18.4828 | 198.8749 | 3 | 200 | 0.6876 | 12 | 1200 | 8.1086 | 8 | 7 | 84 | 1 | 12 |  | 1 |  | 1
12 | Janitor | 1.48 | 1.81 | 3 | 2.6788 | 28.8239 | 3 | 200 | 0.27141 | 12 | 1200 | 2.9774 | 1 |  | 0 | 1 | 12 |  |  |  | 1
13 | Corridor-4 | 2.9 | 10.66 | 3 | 30.914 | 332.6346 | 3 | 200 | 0.75993 | 36 | 3600 | 4.0905 | 4 | 3 | 108 | 1 | 36 |  |  |  | 2 |  |  |  | 1 | 2 | 2
14 | Staircase | 5.83 | 6.83 | 3 | 39.8189 | 428.4514 | 3 | 200 | 1.0484 | 36 | 3600 | 3.819 | 4 | 2 | 72 | 2 | 72
15 | Electrical Room | 5.9 | 2.1 | 3 | 12.39 | 133.3164 | 3 | 200 | 0.51625 | 24 | 2400 | 3.6199 | 4 | 2 | 48 | 2 | 48 |  |  |  | 2 |  |  |  | 1 |  | 1
16 | Corridor-5 | 2.9 | 28.43 | 3 | 82.447 | 887.1297 | 3 | 200 | 0.87719 | 36 | 3600 | 9.451 | 10 | 7 | 252 | 3 | 108 |  |  |  | 4 |  |  |  | 2 | 4 | 5
17 | OT-1 | 5.74 | 6.96 | 3 | 39.9504 | 429.8663 | 3 | 500 | 1.0486 | 42 | 4200 | 8.2094 | 8 | 5 | 210 | 3 | 126 |  |  |  |  | 16 |  |  |  |  | 1
18 | OT-2 | 5.74 | 6.96 | 3 | 39.9504 | 429.8663 | 3 | 500 | 1.0486 | 42 | 4200 | 8.2094 | 8 | 5 | 210 | 3 | 126 |  |  |  |  | 16 |  |  |  |  | 1
19 | OT-3 | 5.74 | 6.96 | 3 | 39.9504 | 429.8663 | 3 | 500 | 1.0486 | 42 | 4200 | 8.2094 | 8 | 5 | 210 | 3 | 126 |  |  |  |  | 16 |  |  |  |  | 1
20 | OT-4 | 5.74 | 6.96 | 3 | 39.9504 | 429.8663 | 3 | 500 | 1.0486 | 42 | 4200 | 8.2094 | 8 | 5 | 210 | 3 | 126 |  |  |  |  | 16 |  |  |  |  | 1
21 | OT-5 | 5.74 | 6.96 | 3 | 39.9504 | 429.8663 | 3 | 500 | 1.0486 | 42 | 4200 | 8.2094 | 8 | 5 | 210 | 3 | 126 |  |  |  |  | 16 |  |  |  |  | 1
22 | OT-6 | 5.74 | 6.96 | 3 | 39.9504 | 429.8663 | 3 | 500 | 1.0486 | 42 | 4200 | 8.2094 | 8 | 5 | 210 | 3 | 126 |  |  |  |  | 16 |  |  |  |  | 1
23 | Anesthetist Lounge | 5.19 | 5.74 | 3 | 29.7906 | 320.5469 | 3 | 300 | 0.90853 | 36 | 3600 | 4.9457 | 3 | 2 | 72 | 1 | 36 | 1 |  | 1 | 3 | 2 | 2 | 1 | 1 |  | 1
24 | Toilet | 1.4 | 1.47 | 3 | 2.058 | 22.1441 | 3 | 200 | 0.23902 | 12 | 1200 | 2.5973 | 1 | 1 | 12 |  | 0 |  | 1 |  | 1
25 | Surgeon's Lounge | 5.19 | 5.74 | 3 | 29.7906 | 320.5469 | 3 | 300 | 0.90853 | 36 | 3600 | 4.9457 | 4 | 3 | 108 | 1 | 36 | 1 |  | 1 | 3 | 2 | 2 | 1 | 1 |  | 1
26 | Toilet | 1.4 | 1.6 | 3 | 2.24 | 24.1024 | 3 | 200 | 0.24889 | 12 | 1200 | 2.7149 | 1 | 1 | 12 |  | 0 |  | 1 |  | 1
27 | Corridor-6 | 15.12 | 2.9 | 3 | 43.848 | 471.8045 | 3 | 200 | 0.8111 | 36 | 3600 | 5.4359 | 5 | 3 | 108 | 2 | 72 |  |  |  | 3 |  |  |  | 2 | 1 | 3
28 | Clean Store | 3 | 3.18 | 3 | 9.54 | 102.6504 | 3 | 200 | 0.51456 | 36 | 3600 | 1.8643 | 1 |  | 0 | 1 | 36 |  |  |  | 1 |  |  |  | 1 |  | 1
29 | Sterile Store Room | 5.74 | 5.74 | 3 | 32.9476 | 354.5162 | 3 | 200 | 0.95667 | 36 | 3600 | 3.463 | 4 | 3 | 108 | 1 | 36 |  |  |  | 2 | 2 |  |  | 1 |  | 1
30 | Point of Care Lab | 7.74 | 5.74 | 3 | 44.4276 | 478.041 | 3 | 400 | 1.0986 | 36 | 3600 | 8.1327 | 6 | 4 | 144 | 2 | 72 | 2 |  | 1 | 2 | 2 |  |  | 1 |  | 1
31 | Wash Area | 4.57 | 1.8 | 3 | 8.226 | 88.5118 | 3 | 200 | 0.43046 | 12 | 1200 | 5.7647 | 2 | 1 | 12 | 1 | 12 |  |  |  | 1
32 | Lab Store | 4.57 | 3.84 | 3 | 17.5488 | 188.8251 | 3 | 200 | 0.69555 | 24 | 2400 | 3.8054 | 4 | 3 | 72 | 1 | 24 |  |  |  | 2 |  |  |  | 1 |  | 1
33 | Corridor-7 | 28.14 | 2.9 | 3 | 81.606 | 878.0806 | 3 | 200 | 0.87635 | 36 | 3600 | 9.3635 | 9 | 6 | 216 | 3 | 108 |  |  |  | 3 |  |  |  | 2 | 4 | 5
34 | Staircase | 9.03 | 7.4 | 3 | 66.822 | 719.0047 | 3 | 200 | 1.3557 | 36 | 3600 | 4.9563 | 6 | 4 | 144 | 2 | 72
35 | CSSD | 6.25 | 5.74 | 3 | 35.875 | 386.015 | 3 | 300 | 0.99736 | 24 | 2400 | 8.138 | 6 | 4 | 96 | 2 | 48 | 1 |  | 1 | 4 | 4 |  |  | 1 |  | 1
36 | Clean Utility | 1.8 | 2.83 | 3 | 5.094 | 54.8114 | 3 | 200 | 0.36674 | 24 | 2400 | 2.095 | 1 |  | 0 | 1 | 24 |  |  |  | 1 |  |  |  | 1 |  | 1
37 | Dirty Utility | 1.8 | 5.74 | 3 | 10.332 | 111.1723 | 3 | 200 | 0.45676 | 24 | 2400 | 3.4118 | 3 | 2 | 48 | 1 | 24 |  |  |  | 1 |  |  |  | 1 |  | 1
38 | Toilet | 3.65 | 4.83 | 3 | 17.6295 | 189.6934 | 3 | 200 | 0.69298 | 12 | 1200 | 7.6742 | 5 | 4 | 48 | 1 | 12 |  | 2 |  | 1
39 | General Store | 3.42 | 3.35 | 3 | 11.457 | 123.2773 | 3 | 200 | 0.56411 | 24 | 2400 | 3.0633 | 4 | 3 | 72 | 1 | 24 |  |  |  | 2 |  |  |  | 1 |  | 1
40 | Corridor-8 | 2.9 | 18.07 | 3 | 52.403 | 563.8563 | 3 | 200 | 0.83298 | 36 | 3600 | 6.3258 | 6 | 4 | 144 | 2 | 72 |  |  |  | 4 |  |  |  | 2 | 2 | 3
41 | Passage | 5.74 | 1.68 | 3 | 9.6432 | 103.7608 | 3 | 200 | 0.43321 | 24 | 2400 | 3.3575 | 3 | 2 | 48 | 1 | 24 |  |  |  | 1 |  |  |  | 1 |  | 1
42 | Toilet | 6.43 | 3.35 | 3 | 21.5405 | 231.7758 | 3 | 200 | 0.73417 | 12 | 1200 | 8.8507 | 7 | 6 | 72 | 1 | 12 |  | 2 |  | 2
43 | Transplant I.C.U | 5.74 | 14.27 | 3 | 81.9098 | 881.3494 | 3 | 500 | 1.3645 | 36 | 3600 | 15.0905 | 15 | 10 | 360 | 5 | 180 |  |  | 2 | 34 | 34 | 13 | 1 | 1 |  | 2
44 | Corridor-9 | 2.9 | 11.79 | 3 | 34.191 | 367.8952 | 3 | 200 | 0.77583 | 36 | 3600 | 4.4314 | 4 | 3 | 108 | 1 | 36 |  |  |  | 2 |  |  |  | 1 | 1 | 2
45 | Room | 5.74 | 8.85 | 3 | 50.799 | 546.5972 | 3 | 300 | 1.1606 | 36 | 3600 | 6.6018 | 6 | 4 | 144 | 2 | 72 | 2 |  | 2 | 12 | 12 | 6 | 1 | 1 |  | 2
46 | Toilet | 5.74 | 3.35 | 3 | 19.229 | 206.904 | 3 | 200 | 0.70513 | 12 | 1200 | 8.2262 | 7 | 6 | 72 | 1 | 12 |  | 3 |  | 2
47 | H.O.D. Room-1 | 5.74 | 3.3 | 3 | 18.942 | 203.8159 | 3 | 300 | 0.69845 | 24 | 2400 | 6.1357 | 5 | 4 | 96 | 1 | 24 | 1 |  | 1 | 2 | 2 | 2 | 1 | 1 |  | 1
48 | Toilet | 1.4 | 1.6 | 3 | 2.24 | 24.1024 | 3 | 200 | 0.24889 | 12 | 1200 | 2.7149 | 1 | 1 | 12 |  | 0 |  | 1 |  | 1
49 | Counselling Room | 5.74 | 2.4 | 3 | 13.776 | 148.2298 | 3 | 300 | 0.56413 | 24 | 2400 | 5.5249 | 3 | 2 | 48 | 1 | 24 | 1 |  | 1 | 2 | 2 | 2 | 1 | 1 |  | 1
50 | Durty Nurses Room | 5.74 | 2.4 | 3 | 13.776 | 148.2298 | 3 | 300 | 0.56413 | 24 | 2400 | 5.5249 | 2 | 1 | 24 | 1 | 24 | 1 |  |  | 2 | 2 | 2 | 1 | 1 |  | 1
51 | Toilet | 1.4 | 1.6 | 3 | 2.24 | 24.1024 | 3 | 200 | 0.24889 | 12 | 1200 | 2.7149 | 1 | 1 | 12 |  | 0 |  | 1 |  | 1
52 | Change Rooms | 5.74 | 5.6 | 3 | 32.144 | 345.8694 | 3 | 300 | 0.94486 | 24 | 2400 | 7.6968 | 7 | 2 | 48 | 5 | 120 |  |  |  | 5 |  |  |  | 1 |  | 5
53 | Corridor-10 | 17.86 | 2.9 | 3 | 51.794 | 557.3034 | 3 | 200 | 0.83163 | 36 | 3600 | 6.2624 | 6 | 4 | 144 | 2 | 72 |  |  |  | 3 |  |  |  | 2 | 2 | 3
54 | Doctors Room | 6.1 | 3.5 | 3 | 21.35 | 229.726 | 3 | 300 | 0.74132 | 24 | 2400 | 6.5158 | 5 | 3 | 72 | 1 | 24 | 1 |  | 1 | 2 | 2 | 2 | 1 | 1 |  | 1
55 | Toilet | 1.4 | 1.6 | 3 | 2.24 | 24.1024 | 3 | 200 | 0.24889 | 12 | 1200 | 2.7149 | 1 | 1 | 12 |  | 0 |  | 1 |  | 1
56 | T.I.R-1 | 6.2 | 3.4 | 3 | 21.08 | 226.8208 | 3 | 300 | 0.73194 | 24 | 2400 | 6.5158 | 6 | 4 | 96 | 2 | 48 | 1 |  | 1 | 4 | 4 | 2 | 1 | 1 |  | 1
57 | T.I.R-2 | 5.19 | 5.74 | 3 | 29.7906 | 320.5469 | 3 | 300 | 0.90853 | 24 | 2400 | 7.4186 | 6 | 4 | 96 | 2 | 48 | 1 |  | 1 | 4 | 4 | 2 | 1 | 1 |  | 1
58 | T.I.R-3 | 5.19 | 5.74 | 3 | 29.7906 | 320.5469 | 3 | 300 | 0.90853 | 24 | 2400 | 7.4186 | 6 | 4 | 96 | 2 | 48 | 1 |  | 1 | 4 | 4 | 2 | 1 | 1 |  | 1
| TOTAL | [11 empty] | 303 | 202 | 5916 | 100 | 3108 | 19 | 13 | 18 | 181 | 212 | 49 | 12 | 44 | 21 | 72 | 0
| Total Load in KW | [13 empty] | 3.4157 |  | 1.7945 | 0.6582 | 0.45035 | 20.7852 | 26.1259 | 30.6005
| Eighth floor Lighting Loads in KW | [12 empty] | 4.5242 | KW
| Eighth floor Raw Power Loads in KW | [12 empty] | 46.9111 | KW
| Eighth floor UPS Lighting Loads in KW | [12 empty] | 1.7945 | KW
| Eighth floor UPS Power Loads in KW | [12 empty] | 30.6005 | KW