## HVAC
Comparative Statement HVAC - IVF Centre
|  |  |  | New Freezing point |  | Pavani Engineers |  | VJ Engineers
S.No | Details | Qty | Unit | Unit Rate | Amount (Rs.) | Unit Rate | Amount (Rs.) | Unit Rate | Amount (Rs.)
1 | Supply, transportation and installation of split AC unit 1.5 TR inverter type 3 Star capable of delivering 18000 BTU/hr and above with high wall mounted indoor unit and outdoor condencing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord , built-in stabilizer (Voltage range 160- 264 volts) and cordless remote control.Makes : Daikin / Thoshiba / O General | 1 | Nos | 52500 | 52500 | 44363 | 44363 | 49640 | 49640
2 | Supply, transportation and installation of split AC unit 1.0 TR inverter type minimum 3 Star capable of delivering 12000 BTU/hr and above with high wall mounted indoor unit and outdoor condensing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord , built-in stabilizer (Voltage range 160- 264 volts) and cordless remote control.Makes : Daikin / Thoshiba / O General | 1 | Nos | 42360 | 42360 | 37651 | 37651 | 43750 | 43750
3 | Modular Double skin floor mounted EUROVENT Certified Air Handling Unit 2000CFM / 5.5 TR / 150mm SP made out of 45 + 2mm thick PUF insulated panels (Thermal break aluminium profile frame work) with 0.8mm thick pre painted / powder coated inner & outer skins comprising of mixing box with fresh air & return air dampers, pre filters with 10 & 5 microns combination filters in single frame, Interlaced/Intertwined DX Cooling Coil suitable for connecting 2 nos of 5.5TR capacity (1W+1S) out door condensing units, SS304 drain pan with , blower section with Nicotra / Kruger make direct drive/ Plug type fan, vibration isolators, EFF1 motor & blower section with on/off switches to operate from outside, limit switch for the fan section access door with a view port, fine filter section with 3 microns filters (inspection doors for all filter and fan sections) and damper at the outlet of unit. Ports for differential pressure gauges across all filters & blower to measure differential pressure.AHU Make : VTS / Systemair, Make - Blower - Nicotra / Kruger ; Motor - Crompton Greaves / Siemens ; Filter - Thermodyne / Freudenberg / Ultrafil | 1 | Nos | 593196.5 | 593196.5 | 555329 | 555329 | 675200 | 675200
4 | SITC of filter module made out of heavy duty aluminum powder coated extrusion with minimum of 13G . and to house 610 mm X 610 mm HEPA Filter @ 0.3 microns , 99.9997, H-14 Grade, Filter loading from clean room side with bewel gear arrangement damper with access from clean room suitable to house the following filter sizes pressure drop & Integrity testing ports into room. Includes SS capsule perforated diffuser. This includes all required supports and accessories etc. Capacity 1000 CFM. | 6 | Nos | 34797 | 208782 | 39494 | 236964 | 47630 | 285780
5 | SITC of air cooled condensing units with two scroll compressors, air cooled condenser, power panel, vibration isolating pads, stand for ODU, thermostat, etc. of the following capacities. The nominal capacity of the condensing unit shall be as under. Air cooled condensing unit shall have horizontal discharge. All refrigerant piping accessories sight glass, drier, expansion valve, etc. shall be supplied with the condensing units and suitable to connect above AHUs. Refrigerant shall be R 407C / R 410A. Necessary thermostat, control wiring, etc. shall be included. Derating of the unit shall not be more than 15% under 45 deg. C ambient temperature. Condensing unit shall be capable of operating up 50 deg. C ambient temperature. 5.5 TR capacity | 1 | Nos | 185000 | 185000 | 171884 | 171884 | 215500 | 215500
6 | SITC of Flange type, Flame proof FLP duct heaters of 3 kW capacity with Mineral Filled AISI SS304/SS321 Sheathed Tubular Heater with GI Helical fins, Tube dia 8.2mm min and Helical Finn dia 25mm min,enclosed in the frame, FLP Terminal box etc,Nickel Chromium Inner Element, Silicon Sealing to Restrict Moisture pickup,Silver brazed mounting plate etc, and heters shall be controlled with PID thyrestor controller based on the anlog oput put signal of 0-10 V DC of controller . And this should have saftey thermostat and cutouts & air stat etc all safety controles. The capacities as follows and sizes of the heaters shall be as per the duct sizes and approved drawing. | 1 | Nos | 225000 | 225000 | 192972 | 192972 | 285604 | 285604
7 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class 'O' nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection,etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 | [5 empty] | 0
| mm. Copper pipe size shall be as per OEM standards. | [5 empty] | 0
a. | Liquid Line | 20 | Rmt | 900 | 18000 | 960 | 19200 | 920 | 18400
b. | Suction Line | 20 | Rmt | 1150 | 23000 | 1122 | 22440 | 1050 | 21000
0
8 | SITC of CPVC drain ping with supports, clamps and 9 mm thk. Nitrile | 20 | Rmt | 335.5 | 6710 |  | 0
| rubber tube insulation of the following sizes. Insulation shall have factory laminated glass cloth. | [5 empty] | 0
a. | 32mm Dia | 50 | Rmt | 575 | 28750 | 633 | 31650 | 435 | 21750
b. | 25mm Dia | 50 | Rmt | 450 | 22500 | 484 | 24200 | 390 | 19500
9 | SITC of Factory fabricated and boxed GI ducting using class Aluminum Sheets / coils, should be fabricated as per SMACNA, galvanised hardware & supports, silicon sealant at all longitudinal joints, Galvanized /GI Electroplated iron angle flanges for all the joints, bracing angles and minimum 5mm thick neoprene rubber gasket.- Duct pressure testing at 75mm to be carried out before insulatiting the duct. pressure testing to be done as per SMACNA. Procedure to be approved by consultant. | [5 empty] | 0
a. | 20G - 1.0 mm Thick | 30 | Sqm | 2600 | 78000 | 2486 | 74580 | 2160 | 64800
b. | 22G – 0.8 mm Thick | 250 | Sqm | 2300 | 575000 | 2224 | 556000 | 1950 | 487500
10 | Aluminium low leakage aerofoil design volume control dampers (Suitable for manual & motorised operation) | 2 | Sqm | 16500 | 33000 | 14929 | 29858 | 12560 | 25120
11 | CBRI approved 16G GI Spring return actuated fire dampers rated for 90 minutes with limit switch. | 2 | Sqm | 22000 | 44000 | 24367 | 48734 | 32745 | 65490
12 | SITC of SS perforated return raiser grilles with 10 microns filters with collar dampers | 2 | Sqm | 22500 | 45000 | 24762 | 49524 | 29511 | 59022
13 | Extruded Al. powder coated EXHAUST / RETURN discrete grilles | 1 | Sqm | 9000 | 9000 | 7779 | 7779 | 12500 | 12500
14 | SITC of Collar Dampers made of Al. extrusions with black powder coating for Grilles / Diffusers | 1 | Sqm | 8000 | 8000 | 7238 | 7238 | 9660 | 9660
15 | SITC of Magnehelic gauges across pre & fine filter at AHUs including mounting arrangement, SS nozzles, food grade PVC tubing, etc. | 2 | Nos | 12500 | 25000 | 9828 | 19656 | 12470 | 24940
16 | SITC of Magnehelic gauges to measure the room differential pressures in operation theatres with SS mounting box, SS nozzles, food grade PVC tubing, etc. | 2 | Nos | 14800 | 29600 | 12116 | 24232 | 16333 | 32666
17 | SITC of Aluminium powder coated Fresh air & Exhaust Louvers of non vision type with nylon mosquito net etc | 1 | Sqm | 10550 | 10550 | 9672 | 9672 | 7988 | 7988
18 | Supply, laying of Class O Nitrile rubber with factory laminated Glass cloth, all joints shall be covered with slef adhesive tapes. | [5 empty] | 0
a. | 32mm Thick for Exposed Supply Air duct and finished with UV Protective Paint. | 130 | Sqm | 1200 | 156000 | 1152 | 149760 | 950 | 123500
b. | 25mm Thick for Exposed Return Air Duct and finished with UV Protective Paint. | 130 | Sqm | 1050 | 136500 | 1010 | 131300 | 850 | 110500
c. | 25mm Thick for Supply air duct running inside the building. | 40 | Sqm | 700 | 28000 | 741 | 29640 | 942 | 37680
d. | 19mm Thick for Return air running inside the building. | 40 | Sqm | 625 | 25000 | 619 | 24760 | 868 | 34720
19 | Condensing units - VRF/VRV System : Supply, Installation, Nitrogen testing , Vacuuming and Commissioning of air cooled variable refrigerant flow modular type condensing units, each comprising of multiple scroll compressors all inverter driven, full charge of refrigerant gas (R-410a) including additional gas filling , lubricating oil and all accessories as per the specifications. The condensing units shall be suitable to work on cooling mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B . The COP of the system shall be greater than 4 under ARI conditions for 100% load . The condensing units shall be suitable for operation on 415 ± 10% volts, 50Hz, 3 phase AC power supply and , outdoor units to be mounted on MS platform with suitable Vibration Isolation pads to avoid vibrations. All the supports and angle base frame structure to be duly black painted with synthetic epoxy paint. the condensing units shall be of following capacities: The VRF ODU should be capable of working with total capacity of connected indoor units ranging between 100% to 140% of ODU capacity . COP minimum 3.5 | [5 empty] | 0
a. | 14 HP | 1 | Set | 366000 | 366000 | 306930 | 306930 | 349040 | 349040
20 | VRF Indoor Units : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 ±6% volts, 50Hz, 1 phase AC power supply. | [5 empty] | 0
a | 0.8 Tr | 2 | Nos | 33195 | 66390 | 28860 | 57720 | 27450 | 54900
b | 1.0 Tr | 4 | Nos | 33910 | 135640 | 28860 | 115440 | 32500 | 130000
c | 1.5 Tr | 4 | Nos | 38802 | 155208 | 33020 | 132080 | 36320 | 145280
21 | Cassette Units : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling mode.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 ±6% volts, 50Hz, 1 phase AC power supply. | [5 empty] | 0
a | 3.0 Tr – 4 way | 1 | Nos | 55959 | 55959 | 46670 | 46670 | 56675 | 56675
22 | Supply, Installation, Testing and Commissioning of Hard copper REFRIGERANT PIPING of 16swg various sizes with necessary supports, fittings, interconnecting the liquid and suction lines between the aircooled outdoor units and the indoor units. The piping shall be carried out of Hard drawn copper pipes of type 'K with soldered / brazed socket fittings. Isolating valves shall be provided to isolate each compressor, strainers, sight glass and any other component requiring proper operation and maintenance. Both the suction and liquid lines shall be insulated with 19mm thick closed cell insulation for above 25mm dia , 13mm thick for pipes below 25mm dia . The insulation finished with treated woven glass fiber reinforced covering for inside Piping and including making required holes in the wall and re finishing and water tight of holes after laying holes as per the specifications and approved drawings. | 1 | Lot | 420000 | 420000 | 383344 | 383344 | 465229 | 465229
23 | Supply, Installation , Testing and Commissioning of Refnet joints to be provided in refrigerant pipe line. Material of construction for fittings shall be similar to refrigerant piping. | 10 | Sets | 6200 | 62000 | 5928 | 59280 | 4790 | 47900
24 | Supply & Installation of control cum transmission wiring of size 3C x 1.5 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing & accessories as | 150 | Rmt | 300 | 45000 | 301 | 45150 | 245 | 36750
25 | Supply & Installation of cabling of size 2C x 1 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing & accessories as per the approved routing. | 100 | Rmt | 250 | 25000 | 240 | 24000 | 185 | 18500
| GRAND TOTAL EXCL. OF GST @18% ON WORKS CONTRACT |  |  |  | 3939645.5 |  | 3670000 |  | 4036484
| Commercial Rank |  |  |  | L2 |  | L1 |  | L3
We found Pavani Engineers quote the lowest price in the market and same has been adopted in price estaimation as the rates are reasonable

## Panels
Comparative Statement (MAIN PANEL & AC PANEL for IVF Centres)
|  |  |  | MNR Electricals |  | Srinidhi Power Solutions
S.No | Description | Qty | UoM | Unit Rate | Amount (Rs.) | Unit Rate | Amount (Rs.)
1 | SITC of IVF Center Main Panel Indoor IP-42 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with /without detachable extension type structure with all type of suitable switching accessories & bus-bar as per load requirement of respective IVF equipment’s. (Which is including Lighting, power DBs & UPS) | 1 | Nos | 337500 | 337500 | 350000 | 350000
| SITC of IVF center AC Panel outdoor IP-54 wall/ free standing floor mounted dust and vermin proof compartmentalized cubical panel made out of CRCA sheet, required hardware, duly treated for de-rusting in 7 tank process with de-phosphate and with powder coating on both side of panel in desired shade. The panel having PU/ Neoprene rubber gasket of not less than 3mm thickness, separate detachable gland plate M.S. base channel, hinged door with locking arrangement for equipment/switchgear. Thickness of sheet shall not be less than 1.6 mm up to 600 mm length / width of any compartment and be of 2.0 mm above 600 mm. Load bearing structure shall be of 2.0 mm thick sheet supported by base M.S. channel if required. Side walls and cable alley compartments having bolted type doors with / without detachable extension type structure with all type of suitable switching accessories & bus-bar as per load requirement of respective AC equipment’s. (Which is including 1nos AHU’s stater with VFD by pass, Heater, ODU & VRF system) | 1 | Nos | 257500 | 257500 | 265000 | 265000
| Total Excl. GST @ 18% |  |  |  | 595000 |  | 615000
| Commercial Rank |  |  |  | L1 |  | L2
We found MNR Electricals quote the lowest price in the market and same has been adopted in price estaimation as the rates are reasonable

## LAN Points
Comparative Statement (LAN POINTS - IVF Centre)
|  |  |  | Velind Virtual Systems |  | Gazelle Technologies |  | Veltronix Industries
SNo | Item | Units | Qty | Unit Rate | Total (INR) | Unit Rate | Total (INR) | Unit Rate | Total (INR)
1 | Data Outlet (RJ45) for LAN Sockets with Anodized GI Box, Front Plate, Labelling. | Nos | 20 | 450 | 9000 | 550 | 11000 | 510 | 10200
2 | CAT-6 UTP | Mtrs | 1600 | 45 | 72000 | 50 | 80000 | 49 | 78400
3 | Certificate, Testing and Documentation of LAN points | Nos | 20 | 500 | 10000 | 750 | 15000 | 600 | 12000
4 | 19” 6U Network Rack. Wall Mount. | Nos | 1 | 11000 | 11000 | 14000 | 14000 | 13000 | 13000
5 | 24 Port manageable Switch. DGS-1210-28 | Nos | 1 | 28500 | 28500 | 32000 | 32000 | 29800 | 29800
6 | 24 Port Patch Panel | Nos | 1 | 8500 | 8500 | 10500 | 10500 | 8500 | 8500
7 | Patch Cords. 1 meter. | Nos | 20 | 225 | 4500 | 275 | 5500 | 250 | 5000
8 | PVC FRLS Conduits | Mtrs | 300 | 90 | 27000 | 90 | 27000 | 95 | 28500
9 | Cable Trays, 100mm | Mtrs | 100 | 1200 | 120000 | 1200 | 120000 | 1500 | 150000
10 | Installation Charges | Lot | 1 | 70830 | 70830 | 85000 | 85000 | 75000 | 75000
Grand Total |  |  |  |  | 361330 |  | 400000 |  | 410400
| Commercial Rank |  |  |  | L1 |  | L2 |  | L3
We found Velind Virtual Systems quote the lowest price in the market and same has been adopted in price estaimation as the rates are reasonable

## UPS
Comparative Statement (20 KVA UPS for IVF Centres)
|  |  |  | APS Tech Systems |  | Srinidhi Power Solutions |  | N K Enterprises
S.No | Description | Qty | UoM | Unit Rate | Total Amount(Rs.) | Unit Rate | Total Amount(Rs.) | Unit Rate | Total Amount(Rs.)
1 | Supply & installation of 20KVA 3ph in & 3ph out on line UPS system IGBT based rectifier with input power factor correction 32 bit microprocessor based with isolation transformers double conversion, SNMP controls, LCD display, Pure sine wave output, with auto static switch three phase input / Three phase output and modular structure for better thermal technology / cooling facility, with warranty up to three years.Makes: APC / Numeric / Emerson / Fuji Electric | 1 | Nos | 275050 | 275050 | 309500 | 309500 | 309750 | 309750
2 | Cables for Interconnection | 1 | Nos | 13000 | 13000 | 14500 | 14500 | 14500 | 14500
| Total Excl. GST @ 18% |  |  |  | 288050 |  | 324000 |  | 324250
| Commercial Rank |  |  |  | L1 |  | L2 |  | L3
We found APS Tech Systems quote the lowest price in the market and same has been adopted in price estaimation as the rates are reasonable

## Clean Room
Comparative Statement (CLEAN ROOM PANELS for IVF Centres)
|  |  |  | Ahlada |  | Airwin |  | Medical Products Service
Sr. No | Description | Unit | Qty |  |  | Supply |  | Supply
|  |  |  | Rate | Amount | Rate | Amount | Rate | Amount
A | CLEAN ROOM MODULAR SYSTEM
1 | Supply & installation of 80mm thick double skin modular wall Panels made of 0.8 mm thick powder coated GI on both the sides, with 40 ± 2 kg/m3 density PUF as infill, GI profiles all along the periphery, flush on both sides with maximum allowable gap of 3- 4mm filled with food grade silicon sealant and placed on cold rolled galvanised bottom tracks with a recess to provide floor to wall coving flush with the wall panel. This includes all required harware for completion Panels to be covered with a protective film to avoid any damages during transportation & installation | Sqm | 145 | 5290 | 767050 | 5450 | 790250 | 5400 | 783000
2 | Supply & installation of 50mm thick double skin ceiling system made of 0.8 mm thick Powder Coated GI sheets on both sides, 40 ± 2 kg/m3 density PUF as infill, GI profiles all along the periphery, panels flush towards room side with maximum allowable gap of 3-4mm at panel to panel joints filled with silicon sealant. Ceiling panels are suspended from the RCC slab by using concealed AL ceiling grid with tie rod and adjustable turn buckle arrangement etc. This includes all required hardware for completion. Panels to be covered with a protective film to avoid any damages during transportation & installation | Sqm | 80 | 4830 | 386400 | 4950 | 396000 | 4875 | 390000
3 | Clean room Doors : 46mm thick flush doors made of 0.8mm thick Powder coated GI sheets on both sides, 90 ± 2 kg/m3 density Honeycomb with stand upto 220 Deg.C Temperature, and compressible strength upto 400 Kg/Sqm, 1.2 mm thick GPSP . door frames, double glazed vision panel with necessary adhesive tapes & silicon sealant, necessary hardware like SS304 ball bearing butt hinges, D- handles, push plates, Dorma make door closure, concealed tower bolt, drop seals for the double leaf door and provision for fixing magnetic type door interlocking system and automatic door bottoms, Both side lock & keys etc. complete. | [7 empty] | 0
a | Double Leaf Door : 1500 X 2100 mm with 300mm X 300mm double glazed view panels | Nos. | 5 | 43068 | 215340 | 41900 | 209500 | 41000 | 205000
b | Single Door : 900 X 2100 mm with 300 mm x 300 mm View panel | Nos. | 2 | 26968 | 53936 | 28000 | 56000 | 27500 | 55000
c | Emergency Fire Door of size 1500 X 2100 mm with 2 hours fire rated and panic push bar and accessories etc. | Nos. | 1 | 51750 | 51750 | 58000 | 58000 | 56000 | 56000
4 | Supply and installation of Extruded Aluminium Coving | Lot | 1 | 552 | 552 | 600 | 600 | 580 | 580
5 | Supply, installation, testing and commissioning of 16 G GI powder coated suitable single person entry air shower as per the manufacture standard ,including SS304 nozzles,grated floor,Pre filter and HEPA ( 99.997 efficiency @ 0.3 micron filters, high efficiency Blower of make : Nicotra or dynamic or EBM mounted on vibration isolators for smmoth operation ,Flourscent lamp,Door closer along with interlocking facility to ensure both doors do not open simultaneously,2 sets of Heavy-duty, durable doors with glass windows to permit visibility. doors suitable to the air shower with necessary hinges and joinery material deemed required for making the unit complete in all aspects. And air shower panels powder coating to matching the clean room partition panel.Electromagnetic interlock system prevents the doors from opening before the air shower cycle is completed, protecting the cleanroom from cross-contamination. Magnehelic gauge across the filters mounted at the entry side of the air shower. Noise level should be lowest possible say less than 65-68 DbA from 1 mtr distance of air shower entry door. | No. | 1 | 337000 | 337000 | 360000 | 360000 | 350000 | 350000
* Door locks automatically release in the event of a power outage or if one of the Emergency Exit buttons are depressed.• Shower time and door interlock duration can be programmed. Status indicator . Air nozzles to be adjusted to redirect streams of air• Energy-efficient LED lighting includes motion-activation. no gaps and crevices where microbes can colonize, rounded corners for easy disinfection. All required documentation and Single Phase , 230 volts . It should meet clean room requirement and standards as per ISO14644. Need to provide all test certificates and to provide qualification documents DQ,IQ ,PQ & OQ, Field test readings relevant to ISO14644 standards . To provide neoprene gasket between the airshower body and the modular panel to reduce the transfer of vibration & finished with coving and sealant. Indicator lights mounted on both sides of the exterior of the air shower to regulate traffic flow, in and out of the cleanroom.
6 | Supply, installation, Testing and Commissioning of Static Pass Boxes of Size 450X450mm with 1.2mm thick SS 304 Mat finish , with interlock doors, UV light On when doors closed condition. As per clean room standard and requirement. | Nos. | 3 | 57250 | 171750 | 57500 | 172500 | 55000 | 165000
SUBTOTAL AMOUNT (RS) FOR SUPPLY AND INSTALLATION |  |  |  |  | 1983778 |  | 2042850 |  | 2004580
Commercial Rank |  |  |  |  | L1 |  | L3 |  | L2
We found AHLADA quote the lowest price in the market and same has been adopted in price estaimation as the rates are reasonable

## MGPS Estimate
Comparative Statement (Gas Piping System for IVF Centres)
|  |  |  | SudhaAnalyticals |  | Vajra Engineering |  | Medical Products Service
ITEM No. | DESCRIPTION OF ITEM | Total Qty | Unit | Rate | Amount | Rate | Amount | Rate | Amount
Sub: MEDICAL GAS PIPING SYSTEM
A | MEDICAL OXYGEN SYSTEM
1 | S/I/T/C of Oxygen Manifold Emergency for 1+1 Cylinders, as per technical specifications. | 1 | set | 20800 | 20800 | 21200 | 21200 | 19500 | 19500
2 | S/I/T/C of Oxygen Outlets with matching probes, as per HTM-2022/02-01 of UK/NFPA99C of USA as per enclosed technical specifications - (Imported) | 4 | each | 8300 | 33200 | 8100 | 32400 | 7500 | 30000
3 | S/I/T/C of Oxygen Flowmeter with Humidifier ,CE Certified with four digit number as per enclosed technical specifications - (Imported) | 4 | each | 7900 | 31600 | 7900 | 31600 | 7200 | 28800
B | MEDICAL NITROUS OXIDE SYSTEM
1 | S/I/T/C of Nitrous Oxide Manifold Emergency for 1 Cylinder, with high pressure Regulator,NRV,tailpipes etc. as per technical specifications | 1 | set | 13100 | 13100 | 12700 | 12700 | 12500 | 12500
2 | S/I/T/C of N20 Outlets with matching probes, as per HTM-2022/02-01 of UK/NFPA99C of USA as per enclosed technical specifications - (Imported) | 4 | each | 8300 | 33200 | 8100 | 32400 | 7500 | 30000
C | Carbon-Dioxide System
1 | S/I/T/C of C02 Manifold for 2 Cylinders, with high pressure Regulator,NRV,tailpipes etc. as per technical specifications | 1 | set | 20800 | 20800 | 21200 | 21200 | 19500 | 19500
2 | S/I/T/C of C02 Outlets with matching probes, as per HTM-2022102-01ofUK/NFPA99C of USA as per enclosed technical specifications - (Imported) | 4 | each | 7900 | 31600 | 8100 | 32400 | 7500 | 30000
D | S/I/T/C of MEDICAL Grade BS EN: 13348 Kite Marked COPPER PIPE
1 | 12mm | 24 | mtr | 610 | 14640 | 650 | 15600 | 625 | 15000
2 | 15mm | 114 | mtr | 895 | 102030 | 850 | 96900 | 845 | 96330
3 | 22mm | 36 | mtr | 1315 | 47340 | 1300 | 46800 | 1265 | 45540
4 | 28mm | 18 | mtr | 1700 | 30600 | 1620 | 29160 | 1595 | 28710
E | S/I/T/C of Touch type LCD AreaAlarm and Zonal Valve box- as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications (imported)
1 | 3 gases | 1 | each | 320000 | 320000 | 300000 | 300000 | 295000 | 295000
2 | Master Main Alarm including all Gases | 1 | each | 415000 | 415000 | 400000 | 400000 | 395000 | 395000
F | S/I/T/C of MEDICAL LINE VALVE, AS PER CE CERTIFIED I UL LISTED AS PER TECHNICAL SPECIFICATIONS- (Indian)
1 | 15mm0D | 3 | each | 2400 | 7200 | 2150 | 6450 | 2200 | 6600
2 | 22mm0D | 3 | each | 2900 | 8700 | 2700 | 8100 | 2750 | 8250
3 | 28mm0D | 4 | each | 3050 | 12200 | 3200 | 12800 | 3250 | 13000
0
G | S/I/T/C of Bed Head Panel - as per HTM 2022/02-01/ NFPA99C as per enclosed technical specifications | 2 | each | 35200 | 70400 | 35000 | 70000 | 34500 | 69000
| Total amount is excluding GST @ 18% extra |  |  |  | 1212410 |  | 1169710 |  | 1142730
| Commercial Ranking |  |  |  | L3 |  | L2 |  | L1
We found Medical Products Service quote the lowest price in the market and same has been adopted in price estaimation as the rates are reasonable

## Vinyl Flooring
Comparative Statement (VINYL FLOORING for IVF Centres)
|  |  |  | Decor Inn |  | A&A Enterprises |  | Medical Products Service
S.No | Description | Qty | UoM | Unit Rate | Amount (Rs.) | Unit Rate | Amount (Rs.) | Unit Rate | Amount (Rs.)
1 | Providing ,laying of scratch proof PVC/Vinyl flooring of 1.5-2mm thickness with proper welded joints air tight, along with levelling compound to match the existing flooring levels as per engineer in charge instructions. Rate inclusive of sifting of material and labour charges. | 145 | Nos | 3830.6897 | 555450 | 3950 | 572750 | 3900 | 565500
2 | sub floor preparation with self levelling compound. After the sub floor preparation, it should be suitable for ESD flooring. | 145 | Nos
| Total Excl. GST @ 18% |  |  |  | 555450 |  | 572750 |  | 565500
| Commercial Rank |  |  |  | L1 |  | L3 |  | L2
We found Décor Inn quote the lowest price in the market and same has been adopted in price estaimation as the rates are reasonable

## HPL Partition Boards
Comparative Statement (HPL Partition Boards for IVF Centres)
|  |  |  | Decor Inn |  | A&A Enterprises
S.No | Description | Qty | UoM | Unit Rate | Amount (Rs.) | Unit Rate | Amount (Rs.)
1 | Providing ,laying of scratch proof PVC/Vinyl flooring of 1.5-2mm thickness with proper welded joints air tight, along with levelling compound to match the existing flooring levels as per engineer in charge instructions. Rate inclusive of sifting of material and labour charges. | 145 | Nos | 3830.6897 | 555450 | 3950 | 572750
2 | sub floor preparation with self levelling compound. After the sub floor preparation, it should be suitable for ESD flooring. | 145 | Nos
| Total Excl. GST @ 18% |  |  |  | 555450 |  | 572750
| Commercial Rank |  |  |  | L1 |  | L2
We found Décor Inn quote the lowest price in the market and same has been adopted in price estaimation as the rates are reasonable

## CCTV
Comparative Statement (CCTV CAMERA - IVF Centre)
|  |  |  | Velind Virtual Systems |  | Gazelle Technologies |  | Veltronix Industries
SNo | Item | Units | Qty | Unit Rate | Total (INR) | Unit Rate | Total (INR) | Unit Rate | Total (INR)
1 | IP Camera DS-2CD2023G0-I | Nos | 5 | 8500 | 42500 | 10200 | 51000 | 9100 | 45500
2 | Back box for camera | Nos | 5 | 280 | 1400 | 0 | 0 | 0 | 0
3 | 8 Channel NVR DS-7608NI-K2/8P | Nos | 1 | 18650 | 18650 | 22000 | 22000 | 20000 | 20000
4 | 4 TB HDD (Skyhawk) | Nos | 1 | 14500 | 14500 | 17000 | 17000 | 16150 | 16150
5 | 8 Port POE Switch | Nos | 1 | 11000 | 11000 | 14000 | 14000 | 13000 | 13000
6 | 6U Network Rack | Nos | 1 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500
7 | CAT6 UTP | Mtrs | 350 | 45 | 15750 | 60 | 21000 | 66 | 23100
8 | PVC FRLS Conduit | Mtrs | 350 | 55 | 19250 | 105 | 36750 |  | 17000
9 | 32 Inch Monitor | Nos | 1 | 25000 | 25000 | 27500 | 27500 | 28000 | 28000
10 | Installation and Configuration |  | 1 | 16000 | 16000 | 35000 | 35000 | 20000 | 20000
[5 empty] | 171550 |  | 231750 |  | 190250
| Commercial Rank |  |  |  | L1 |  | L3 |  | L2
We found Velind Virtual Systems quote the lowest price in the market and same has been adopted in price estaimation as the rates are reasonable

## Fire Alarm System
Comparative Statement (FIRE DETECTION & ALARM SYSTEM - IVF Centre)
|  |  |  | Velind Virtual Systems |  | Gazelle Technologies |  | Veltronix Industries
SNo | Item | Units | Qty | Unit Rate | Total (INR) | Unit Rate | Total (INR) | Unit Rate | Total (INR)
1 | UL Listed 2 loop micro processor based analog addressable fire control panel expandable by minimum 2 additional loops with minimum 160 character LCD display 4 access levels 1000 events, historical logging, flash E- PROM, 240 volts A C Power supply, automatic battery charger, 24V SLA batteries suitable for operating the entire system and the hooters /strobes for a minimum of 4 hours in battery condition. the panel shall have suitable power amplifiers for hooter / strobes. with zonal indications and battery back up. | Nos | 1 | 125280 | 125280 | 150000 | 150000 | 139100 | 139100
2 | UL approved intelligent analogue addressable photo electric smoke and Temperature detector including cost of base plate etc., complete as per specification with required fittings and accessories. Above and Below Ceiling. | Nos | 30 | 6800 | 204000 | 8000 | 240000 | 7200 | 216000
3 | Response indicators for Above False Ceiling Detectors | Nos | 15 | 475 | 7125 | 570 | 8550 | 550 | 8250
4 | Addressable wall mounting strobes cum hooters including the cost of mounting accessories complete as per specifications and as required | Nos | 1 | 4500 | 4500 | 5000 | 5000 | 4500 | 4500
5 | UL approved intelligent analogue addressable fault isolator modules including the cost of mounting accessories complete as per specifications. | Nos | 1 | 6500 | 6500 | 6500 | 6500 | 6800 | 6800
6 | Addressable Analogue Manual Call Point with resettable flexible element to initiate alarm. | Nos | 1 | 8500 | 8500 | 8500 | 8500 | 8500 | 8500
7 | 2 Core x 1.5Sqmm FRLS armoured copper cable as per IS. 7098 / Part-I / 1988 | Mtrs | 400 | 190 | 76000 | 207.5 | 83000 | 200 | 80000
8 | Installation and Configuration | LOT | 1 | 48000 | 48000 | 62000 | 62000 | 50000 | 50000
[5 empty] | 479905 |  | 563550 |  | 513150
| Commercial Rank |  |  |  | L1 |  | L3 |  | L2
We found Velind Virtual Systems quote the lowest price in the market and same has been adopted in price estaimation as the rates are reasonable

## Video Recording
Comparative Statement (Video Recording System - IVF Centre)
|  |  |  | Velind Virtual Systems |  | Gazelle Technologies |  | Veltronix Industries
SNo | Item | Units | Qty | Unit Rate | Total (INR) | Unit Rate | Total (INR) | Unit Rate | Total (INR)
1 | IP Camera DS-2CD2526G2-I(S) | Nos | 1 | 8500 | 8500 | 10200 | 10200 | 9100 | 9100
2 | Back box for camera | Mtrs | 1 | 280 | 280 | 0 | 0 | 0 | 0
3 | 8 Channel NVR DS-7608NI-K2/8P | Nos | 1 | 18650 | 18650 | 22000 | 22000 | 20000 | 20000
4 | 4 TB HDD (Skyhawk) | Nos | 1 | 14500 | 14500 | 17000 | 17000 | 16150 | 16150
5 | 4 Port POE Switch | Nos | 1 | 7500 | 7500 | 14000 | 14000 | 13000 | 13000
6 | 6U Network Rack | Nos | 1 | 7500 | 7500 | 8200 | 8200 | 8000 | 8000
7 | CAT6 UTP | Nos | 150 | 45 | 6750 | 60 | 9000 | 65 | 9750
8 | PVC FRLS Conduit | Mtrs | 150 | 55 | 8250 | 105 | 15750 | 54 | 8100
9 | Wall Mount Audio MIC | Nos | 1 | 5000 | 5000 | 7500 | 7500 | 8000 | 8000
10 | Installation Charges | Lot | 1 | 12000 | 12000 | 17500 | 17500 | 15000 | 15000
Grand Total |  |  |  |  | 88930 |  | 121150 |  | 107100
| Commercial Rank |  |  |  | L1 |  | L2 |  | L3
We found Velind Virtual Systems quote the lowest price in the market and same has been adopted in price estaimation as the rates are reasonable

## Access Control
Comparative Statement (ACCESS CONTROL - IVF Centre)
|  |  |  | Velind Virtual Systems |  | Gazelle Technologies |  | Veltronix Industries
SNo | Item | Units | Qty | Unit Rate | Total (INR) | Unit Rate | Total (INR) | Unit Rate | Total (INR)
1 | Fingerprint and RF Card based Premium Door Controller with LCD and Keypad - COSEC DOOR FOP + COSEC CPM EM PROX | Nos | 1 | 38500 | 38500 | 45200 | 45200 | 42500 | 42500
2 | Cosec centra Dongle & Plat form with 100 user license for Time and Attendance | Nos | 1 | 25000 | 25000 | 32000 | 32000 | 30000 | 30000
3 | Electro Magnetic Lock (Double Door Model) | Nos | 1 | 14500 | 14500 | 17000 | 17000 | 16150 | 16150
4 | Exit Push Button | Nos | 1 | 2800 | 2800 | 3000 | 3000 | 3000 | 3000
5 | CAT-6 UTP in FRLS Conduit. | Nos | 100 | 95 | 9500 | 60 | 6000 | 98 | 9800
6 | 4 Port Gigabyte POE Switch | Nos | 1 | 6500 | 6500 | 7500 | 7500 | 7000 | 7000
7 | Installation Charges for Access Control System | LOT | 1 | 20000 | 20000 | 20000 | 20000 | 20000 | 20000
[5 empty] | 116800 |  | 130700 |  | 128450
| Commercial Rank |  |  |  | L1 |  | L3 |  | L2
We found Velind Virtual Systems quote the lowest price in the market and same has been adopted in price estaimation as the rates are reasonable