## Template
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | Supply and installation of Under-deck Thermocol insulation sheets of 40 mm thick having more than 30 Kg/m3 density to ceiling by brush application of bituminous adhesive to the sheets and secured with screw along with washer at the centre of the sheet supported with GI wire running diagonally to the sheet of 2mm dia. |  |  |  | 262.74 | Sqm | 859.322 | 225778.2712 | 94826.8739
2 | Supply and Laying of Floor leveller compund (self smoothing mortar) to level the surface, having bulk density not less than 2 Kg/l for a fresh mortor, compressive strength not less than 20 N/mm2, initial setting time not more than 40 minutes and offer a 25 minutes working time, The surface should be walkabe after 30 min of laying. (ICUs) |  |  |  | 725.55 | Sqm | 1237.2881 | 897714.4068 | 377040.0508
3 | Providing dadooing to walls with glazed full body ceramic wall tiles of size 800 x 1600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. |  |  |  | 119.385 | Sqm | 3953.3898 | 471975.4449 | 198229.6869
4 | Glass Sliding Door in TIR-2 & TIR-3 *Size 1.8mt x 2.1mt. *The door will be sliding. ”The material of door will be Glass. *The door will be operate by sensor. *The door movement will be easy and smooth. |  |  |  | 2 | Nos | 229047.4576 | 458094.9153 | 192399.8644
5 | V-Board Partitions on top of false ceiling for partitioning of sterile corridor and non-sterile corridor |  |  |  | 16 | Sqm | 3084.7458 | 49355.9322 | 20729.4915
6 | GI Powder Coated Sliding Doors (0.8mm shutter sheet thk & 1.2mm frame sheet thk with Single Rebate and Honeycomb Infill) Double Leaf Door 1200 x 2100mm with Accessories (Sliding Track for Double Door, Sliding Dead Lock Enox, Concealed Handles 100mm Ahlada, Flush Bolt 300mm Ahlada, SS304 Kick Plate upto 350mm ht, DG Clear Float Glass 350x750x6mm with Adhesive Tape & Silicon Sealant) |  |  |  | 1 | Nos | 71299.1525 | 71299.1525 | 29945.6441
| Total Amount | [6 empty] | 2174218.1229 | 913171.6116
| GST @ 18% | [6 empty] | 391359.2621
| Total Amount excluding CAMC | [6 empty] | 3478748.9966
| CAMC Amount as per below table | [6 empty] | 913171.6116
| Total Amount including CAMC | [6 empty] | 4391920.6082
Comprehensive Annual Maintanance Charges post warranty period for 5 years(6th to 10th year) @8, 8,8, 9, 9 % respectively.
| Base Price |  |  | 2174218.1229
| S.No | Year | CAMC % | Amount
| 1 | 6th | 8 | 173937.4498
| 2 | 7th | 8 | 173937.4498
| 3 | 8th | 8 | 173937.4498
| 4 | 9th | 9 | 195679.6311
| 5 | 10th | 9 | 195679.6311
| Total % |  | 42
| Total Amount |  |  | 913171.6116

## MPS-ASTA
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | Supply and installation of Under-deck Thermocol insulation sheets of 40 mm thick having more than 30 Kg/m3 density to ceiling by brush application of bituminous adhesive to the sheets and secured with screw along with washer at the centre of the sheet supported with GI wire running diagonally to the sheet of 2mm dia. |  |  |  | 262.74 | Sqm | 859.322 | 225778.2712 | 0
2 | Supply and Laying of Floor leveller compound (self smoothing mortar) to level the surface, having bulk density not less than 2 Kg/l for a fresh mortar, compressive strength not less than 20 N/mm2, initial setting time not more than 40 minutes and offer a 25 minutes working time, The surface should be walkable after 30 min of laying. (ICUs) |  |  |  | 882.44 | Sqm | 1237.2881 | 1091832.5424 | 0
3 | Providing dadooing to walls with glazed full body ceramic wall tiles of size 800 x 1600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. |  |  |  | 119.385 | Sqm | 3953.3898 | 471975.4449 | 0
4 | Providing (1500 X 2100) single sliding door operated by elbow switches / foot switch as well as touchless sensor of 10mm thick toughened glass (Saint Gobin / Modi Guard) fixed in SS 304 grade 2 Track top channel of 45 mm (one track to hold fixed glass partition in position and second track with top rollers suitably angled to reduce resistance to movement to facilitate smooth sliding movement of the door). Single track bottom channel to be provided for fixed glass partition. Floor guide to be provided for smooth sliding of the door. Concealed door handle of (150 mm) to be provided in cutout on the sliding door for manual operation when required. All fittings provided should be of Titon /Ozone / Enox make in SS 304 - In TIRs |  |  |  | 2 | Nos | 229047.4576 | 458094.9153 | 189200
5 | V-Board Partitions on top of false ceiling for partitioning of sterile corridor and non-sterile corridor |  |  |  | 16 | Sqm | 3084.7458 | 49355.9322 | 20385
6 | GI Powder Coated Sliding Doors (0.8mm shutter sheet thick & 1.2mm frame sheet thick with Single Rebate and Honeycomb Infill) Double Leaf Door 1200 x 2100mm with Accessories (Sliding Track for Double Door, Sliding Dead Lock Enox, Concealed Handles 100mm Ahlada, Flush Bolt 300mm Ahlada, SS304 Kick Plate up to 350mm ht, DG Clear Float Glass 350x750x6mm with Adhesive Tape & Silicon Sealant) |  |  |  | 1 | Nos | 71299.1525 | 71299.1525 | 29450
7 | 4 Gas Digital Alarm Panels : 4 Gas Digital Alarm Panel consisting of all necessary accessories ie Pressure sensors, reguIators, hand valves, pressure gauges (Oxygen, Nitrous oxide, Medical Air, Vacuum) |  |  |  | 2 | Nos | 35720.339 | 71440.678 | 29510
8 | 6 Gas Digital Alarm Panel : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dioxide) consisting of all necessary accessories ie pressure sensors, regulators, hand valves, pressure gauges etc. | 6 Gas Digital Alarm Panele : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. | 6 Gas Digital Alarm Panele : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. | 6 Gas Digital Alarm Panele : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. | 6 | Nos | 50854.2373 | 305125.4237 | 126015
9 | Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a breakable glass for emergency. | Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. | Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. | Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. | 2 | Nos | 18814.4068 | 37628.8136 | 15540
10 | 4 + 4 size of O2 manifold system : 4+4 Oxygen Main manifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frame and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen. | 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen. | 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen. | 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen. | 1 | Job | 40765.2542 | 40765.2542 | 16835
11 | Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yellow indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line distribution pressure. ”Capable to provide a distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporate safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED. | Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED. | Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED. | Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED. | 1 | Job | 188146.6102 | 188146.6102 | 77705
12 | 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 1 | Job | 40765.2542 | 40765.2542 | 16835
13 | 2 cylinder emergency manifold - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 1 | Job | 14746.6102 | 14746.6102 | 6090
14 | Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. "Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS, D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041, C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED | Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. "Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041 C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED | Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. "Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041 C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED | Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. "Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041 C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED | 1 | Job | 188146.6102 | 188146.6102 | 77705
15 | 800 KVA Transformer OLTC for transformers with RTCC: Supply, Transportation, Installation, Testing and Commissioning of 800 KVA TRANSFORMER with all test reports. The Transformer shall be designed and manufactured as per IS:1180 OLTC with level-II with initial filling of oil as per IS 335-1993. 1000 A LT Breaker Kiosk - 01 No.The basic details of the Transformer are as under. Makes: Esennar |  |  |  | 1 | Nos | 4080503 | 4080503 | 1685250
16 | Recording in counselling room |  |  |  | 1 | Job | 131676.2712 | 131676.2712 | 32000
17 | Local Area Network (LAN) System | Local Area Network (LAN) System | Local Area Network (LAN) System | Local Area Network (LAN) System | 1 | Job | 390035.5932 | 390035.5932 | 120000
18 | Supply, Transportation and installation of 20KVA / 312V DC on line UPS system Makes: Vertiv Liberty | Supply, Transportation and installation of 20KVA / 312V DC on line UPS system | Supply, Transportation and installation of 20KVA / 312V DC on line UPS system | Supply, Transportation and installation of 20KVA / 312V DC on line UPS system | 2 | Nos | 533354.2373 | 1066708.4746 | 200000
19 | Monitor Stand beside Bed in ICUs & TIRs |  |  |  | 31 | Nos | 5233.8983 | 162250.8475 | 20000
20 | Double arm Surgical Pendant (supported): The pendant shall be imparted & comply with NFPA99c/HTM 02 - 01/ISO7396 -1/DIN. The support arms shall be extremely robust and revolve on high quality bearings so that pendant head glides smoothly and quickly to any desired position. double moveable arms with total coverage of not less than 1800mm and 330deg, horizontal movement for each arm, which can be easily adjusted to suit desired mode of operation. Vertical movement shall be motorized. Weight carrying capacity of the arm shall not be less than 180 kgs Shall have pneumatic brakes The pendant service heads shall be modular with minimum 1200mm head. the head shall be capable of accepting a range of shavasana infusion poles or other accessories. The pendant heads shall support the range of physiological Monitor Mounting solutions. Shall be dual art of 800mm/8tXfmm.05 no’s platforms of not less than 5tXlmm x5tXbnm x400mm,01 no’s Drawer for place Accessories. Each platform shall have a weight bearing capacity of minimum 30kg each. Sail has iv rod stand with capacity of 30 kg with 4-hooks for each rod. medical gas outlets CO2-02 NOS, Vacuum - 2n0s, Air (7bar)-2nos, Electrical sockets12no, shall provide on the service head (6on each side), DAT port RJ-45/cat6 -2nos. all interface for integration, braking systems, a small spring arm on the side support an additional monitor. |  |  |  | 6 | Nos | 1012712 | 6076272 | 2509500.336
21 | Supply of Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs with borders and design as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM (1:8) prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab , including neat cement slurry of honey like consistancy spread @ 3.3 kgs per Sqm. and jointed neately with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site (excluding cost of C.C. bed) including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in-charge etc.,and overheads & contractors profit complete for finished item of work. (APSS No.701 & 707). |  |  |  | 342 | Sqm | 2161 | 739062 | 0
22 | Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707) |  |  |  | 120 | Rmt | 212 | 25440 | 0
| Total Amount | [6 empty] | 15927049.6992 | 5172020.336
| GST @ 18% | [6 empty] | 2866868.9458
| Total Amount excluding CAMC | [6 empty] | 18793918.645
| CAMC Amount as per below table | [6 empty] | 5172020 |  | 1034404.0672
| Total Amount including CAMC | [6 empty] | 23965938.645
| S.No | Year | CAMC % | Amount
| 1 | 6th |  | 1034404
| 2 | 7th |  | 1034404
| 3 | 8th |  | 1034404
| 4 | 9th |  | 1034404
| 5 | 10th |  | 1034404
| Total % |  | 0
| Total Amount |  |  | 5172020

## Sheet3
750 KVA Generator Set with AMF Control Panel Supply, Transportation, erection and commissioning (Excluding Foundation) of 3 Phase, 415, 50Hz, water cooled multi cylinder diesel generator set with alternator of 750 KVA output continuous rating directly coupled Engine and Alternator 750 KVA, 415 Volts with guard and mounted on a common base plate of Robust construction and complete with AMF panel having IP-52 protection, Acoustic Enclosure as per CPCB norms , sound absorbing material, t to restrict sound level up to 75 dB up to 1 Mtr distance and as per CPCB norms

## KSIPL
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | Supply and installation of Under-deck Thermocol insulation sheets of 40 mm thick having more than 30 Kg/m3 density to ceiling by brush application of bituminous adhesive to the sheets and secured with screw along with washer at the centre of the sheet supported with GI wire running diagonally to the sheet of 2mm dia. |  |  |  | 262.74 | Sqm | 893 | 234626.82 | 89158.1916
2 | Supply and Laying of Floor leveller compund (self smoothing mortar) to level the surface, having bulk density not less than 2 Kg/l for a fresh mortor, compressive strength not less than 20 N/mm2, initial setting time not more than 40 minutes and offer a 25 minutes working time, The surface should be walkabe after 30 min of laying. (ICUs) |  |  |  | 725.55 | Sqm | 1408 | 1021574.4 | 388198.272
3 | Providing dadooing to walls with glazed full body ceramic wall tiles of size 800 x 1600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. |  |  |  | 119.385 | Sqm | 4117 | 491508.045 | 186773.0571
4 | Providing (1500 X 2100) single sliding door operated by elbow switches / foot switch as well as touchless sensor of 10mm thick toughened glass (Saint Gobin / Modi Guard) fixed in SS 304 grade 2 Track top channel of 45 mm (one track to hold fixed glass partition in position and second track with top rollers suitably angled to reduce resistance to movement to facilitate smooth sliding movement of the door). Single track bottom channel to be provided for fixed glass partition. Floor guide to be provided for smooth sliding of the door. Concealed door handle of (150 mm) to be provided in cutout on the sliding door for manual operation when required. All fittings provided should be of Titon /Ozone / Enox make in SS 304 - In TIRs |  |  |  | 2 | Nos | 254270 | 508540 | 193245.2
5 | V-Board Partitions on top of false ceiling for partitioning of sterile corridor and non-sterile corridor |  |  |  | 16 | Sqm | 3272 | 52352 | 19893.76
6 | GI Powder Coated Sliding Doors (0.8mm shutter sheet thk & 1.2mm frame sheet thk with Single Rebate and Honeycomb Infill) Double Leaf Door 1200 x 2100mm with Accessories (Sliding Track for Double Door, Sliding Dead Lock Enox, Concealed Handles 100mm Ahlada, Flush Bolt 300mm Ahlada, SS304 Kick Plate upto 350mm ht, DG Clear Float Glass 350x750x6mm with Adhesive Tape & Silicon Sealant) |  |  |  | 1 | Nos | 77440 | 77440 | 29427.2
| Total Amount | [6 empty] | 2386041.265 | 906695.6807
| GST @ 18% | [6 empty] | 429487.4277
| Total Amount excluding CAMC | [6 empty] | 2815528.6927
| CAMC Amount as per below table | [6 empty] | 906695.6807
| Total Amount including CAMC | [6 empty] | 3722224.3734
Comprehensive Annual Maintanance Charges post warranty period for 5 years(6th to 10th year) @6, 6, 8, 8, 10 % respectively.
| Base Price |  |  | 2386041.265
| S.No | Year | CAMC % | Amount
| 1 | 6th | 6 | 143162.4759
| 2 | 7th | 6 | 143162.4759
| 3 | 8th | 8 | 190883.3012
| 4 | 9th | 8 | 190883.3012
| 5 | 10th | 10 | 238604.1265
| Total % |  | 38
| Total Amount |  |  | 906695.6807

## A&A
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | Supply and installation of Under-deck Thermocol insulation sheets of 40 mm thick having more than 30 Kg/m3 density to ceiling by brush application of bituminous adhesive to the sheets and secured with screw along with washer at the centre of the sheet supported with GI wire running diagonally to the sheet of 2mm dia. |  |  |  | 262.74 | Sqm | 886 | 232787.64 | 93115.056
2 | Supply and Laying of Floor leveller compund (self smoothing mortar) to level the surface, having bulk density not less than 2 Kg/l for a fresh mortor, compressive strength not less than 20 N/mm2, initial setting time not more than 40 minutes and offer a 25 minutes working time, The surface should be walkabe after 30 min of laying. (ICUs) |  |  |  | 882.44 | Sqm | 1296 | 1143642.24 | 457456.896
3 | Providing dadooing to walls with glazed full body ceramic wall tiles of size 800 x 1600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. |  |  |  | 119.385 | Sqm | 4090 | 488284.65 | 195313.86
4 | Providing (1500 X 2100) single sliding door operated by elbow switches / foot switch as well as touchless sensor of 10mm thick toughened glass (Saint Gobin / Modi Guard) fixed in SS 304 grade 2 Track top channel of 45 mm (one track to hold fixed glass partition in position and second track with top rollers suitably angled to reduce resistance to movement to facilitate smooth sliding movement of the door). Single track bottom channel to be provided for fixed glass partition. Floor guide to be provided for smooth sliding of the door. Concealed door handle of (150 mm) to be provided in cutout on the sliding door for manual operation when required. All fittings provided should be of Titon /Ozone / Enox make in SS 304 - In TIRs |  |  |  | 2 | Nos | 252225 | 504450 | 201780
5 | V-Board Partitions on top of false ceiling for partitioning of sterile corridor and non-sterile corridor |  |  |  | 16 | Sqm | 3375 | 54000 | 21600
6 | GI Powder Coated Sliding Doors (0.8mm shutter sheet thk & 1.2mm frame sheet thk with Single Rebate and Honeycomb Infill) Double Leaf Door 1200 x 2100mm with Accessories (Sliding Track for Double Door, Sliding Dead Lock Enox, Concealed Handles 100mm Ahlada, Flush Bolt 300mm Ahlada, SS304 Kick Plate upto 350mm ht, DG Clear Float Glass 350x750x6mm with Adhesive Tape & Silicon Sealant) |  |  |  | 1 | Nos | 74986 | 74986 | 29994.4
| Supply of Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs with borders and design as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM (1:8) prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab , including neat cement slurry of honey like consistancy spread @ 3.3 kgs per Sqm. and jointed neately with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site (excluding cost of C.C. bed) including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in-charge etc.,and overheads & contractors profit complete for finished item of work. (APSS No.701 & 707). |  |  |  | 342 | Sqm | 2250 | 769500 | 307800
| Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707) |  |  |  | 120 | Rmt | 225 | 27000 | 10800
| Total Amount | [6 empty] | 3294650.53 | 1317860.212
| GST @ 18% | [6 empty] | 593037.0954
| Total Amount excluding CAMC | [6 empty] | 3887687.6254
| CAMC Amount as per below table | [6 empty] | 1317860.212
| Total Amount including CAMC | [6 empty] | 5205547.8374
Comprehensive Annual Maintanance Charges post warranty period for 5 years(6th to 10th year) @6, 7, 8, 9, 10 % respectively.
| Base Price |  |  | 3294650.53
| S.No | Year | CAMC % | Amount
| 1 | 6th | 6 | 197679.0318
| 2 | 7th | 7 | 230625.5371
| 3 | 8th | 8 | 263572.0424
| 4 | 9th | 9 | 296518.5477
| 5 | 10th | 10 | 329465.053
| Total % |  | 40
| Total Amount |  |  | 1317860.212

## GASTECH
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | 4 Gas Digital Alarm Panels : 4 Gas Digital Alarm Panel consisting of atl necessary accessories ie Pressure sensors,reguIators,hand valves ,pressure gauges ecL(Oxygen, Nitrous oxide, Medical Air, Vacuum) |  |  |  | 2 | Nos | 43628 | 87256 | 34902.4
2 | 6 Gas Digital Alarm Panele : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. | 6 Gas Digital Alarm Panele : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. | 6 Gas Digital Alarm Panele : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. | 6 Gas Digital Alarm Panele : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. | 6 | Nos | 53172 | 319032 | 127612.8
3 | Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. | Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. | Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. | Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. | 2 | Nos | 20451 | 40902 | 16360.8
4 | 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen. | 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen. | 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen. | 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen. | 1 | Job | 42264 | 42264 | 16905.6
5 | Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED. | Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED. | Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED. | Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED. | 1 | Job | 190873 | 190873 | 76349.2
6 | 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 1 | Job | 42264 | 42264 | 16905.6
7 | 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 1 | Job | 190873 | 190873 | 76349.2
8 | Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. "Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041 C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED | Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. "Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041 C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED | Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. "Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041 C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED | Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. "Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041 C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED | 1 | Job | 152695 | 152695 | 61078
| Total Amount | [6 empty] | 1066159 | 426463.6
| GST @ 18% | [6 empty] | 191908.62
| Total Amount excluding CAMC | [6 empty] | 1258067.62
| CAMC Amount as per below table | [6 empty] | 426463.6
| Total Amount including CAMC | [6 empty] | 1684531.22
Comprehensive Annual Maintanance Charges post warranty period for 5 years(6th to 10th year) @6, 7, 8, 9, 10 % respectively.
| Base Price |  |  | 1066159
| S.No | Year | CAMC % | Amount
| 1 | 6th | 6 | 63969.54
| 2 | 7th | 7 | 74631.13
| 3 | 8th | 8 | 85292.72
| 4 | 9th | 9 | 95954.31
| 5 | 10th | 10 | 106615.9
| Total % |  | 40
| Total Amount |  |  | 426463.6

## LSS
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | 4 Gas Digital Alarm Panels : 4 Gas Digital Alarm Panel consisting of atl necessary accessories ie Pressure sensors,reguIators,hand valves ,pressure gauges ecL(Oxygen, Nitrous oxide, Medical Air, Vacuum) |  |  |  | 2 | Nos | 40902 | 81804 | 29449.44
2 | 6 Gas Digital Alarm Panele : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. | 6 Gas Digital Alarm Panele : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. | 6 Gas Digital Alarm Panele : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. | 6 Gas Digital Alarm Panele : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. | 6 | Nos | 54535 | 327210 | 117795.6
3 | Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. | Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. | Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. | Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. | 2 | Nos | 19769 | 39538 | 14233.68
4 | 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen. | 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen. | 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen. | 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen. | 1 | Job | 44310 | 44310 | 15951.6
5 | Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED. | Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED. | Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED. | Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED. | 1 | Job | 193600 | 193600 | 69696
6 | 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 1 | Job | 44310 | 44310 | 15951.6
7 | 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 1 | Job | 193600 | 193600 | 69696
8 | Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. "Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041 C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED | Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. "Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041 C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED | Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. "Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041 C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED | Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. "Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041 C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED | 1 | Job | 160195 | 160195 | 57670.2
| Total Amount | [6 empty] | 1084567 | 390444.12
| GST @ 18% | [6 empty] | 195222.06
| Total Amount excluding CAMC | [6 empty] | 1279789.06
| CAMC Amount as per below table | [6 empty] | 390444.12
| Total Amount including CAMC | [6 empty] | 1670233.18
Comprehensive Annual Maintanance Charges post warranty period for 5 years(6th to 10th year) @5, 6, 7, 8, 10 % respectively.
| Base Price |  |  | 1084567
| S.No | Year | CAMC % | Amount
| 1 | 6th | 5 | 54228.35
| 2 | 7th | 6 | 65074.02
| 3 | 8th | 7 | 75919.69
| 4 | 9th | 8 | 86765.36
| 5 | 10th | 10 | 108456.7
| Total % |  | 36
| Total Amount |  |  | 390444.12

## SRINIDHI
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | 800 KVA Transformer OLTC for transformers with RTCC: Supply, Transportation, Installation, Testing and Commissioning of 800 KVA TRANSFORMER with all test reports. The Transformer shall be designed and manufactured as per IS:1180 OLTC with level-II with initial filling of oil as per IS 335-1993. 1000 A LT Breaker Kiosk - 01 No.The basic details of the Transformer are as under. Makes: Kirloskar / PETE / Esennar / Voltamp / Crompton / ABB / Schneider. |  |  |  | 1 | Nos | 4563729 | 4563729 | 1962403.47
| Total Amount | [6 empty] | 4563729 | 1962403.47
| GST @ 18% | [6 empty] | 821471.22
| Total Amount excluding CAMC | [6 empty] | 5385200.22
| CAMC Amount as per below table | [6 empty] | 1962403.47
| Total Amount including CAMC | [6 empty] | 7347603.69
Comprehensive Annual Maintanance Charges post warranty period for 5 years(6th to 10th year) @8, 8, 9, 9, 9 % respectively.
| Base Price |  |  | 4563729
| S.No | Year | CAMC % | Amount
| 1 | 6th | 8 | 365098.32
| 2 | 7th | 8 | 365098.32
| 3 | 8th | 9 | 410735.61
| 4 | 9th | 9 | 410735.61
| 5 | 10th | 9 | 410735.61
| Total % |  | 43
| Total Amount |  |  | 1962403.47

## iCARE
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | 800 KVA Transformer OLTC for transformers with RTCC: Supply, Transportation, Installation, Testing and Commissioning of 800 KVA TRANSFORMER with all test reports. The Transformer shall be designed and manufactured as per IS:1180 OLTC with level-II with initial filling of oil as per IS 335-1993. 1000 A LT Breaker Kiosk - 01 No.The basic details of the Transformer are as under. Makes: Kirloskar / PETE / Esennar / Voltamp / Crompton / ABB / Schneider. |  |  |  | 1 | Nos | 4590997 | 4590997 | 2065948.65
| Total Amount | [6 empty] | 4590997 | 2065948.65
| GST @ 18% | [6 empty] | 826379.46
| Total Amount excluding CAMC | [6 empty] | 5417376.46
| CAMC Amount as per below table | [6 empty] | 2065948.65
| Total Amount including CAMC | [6 empty] | 7483325.11
Comprehensive Annual Maintanance Charges post warranty period for 5 years(6th to 10th year) @9, 9, 9, 9, 9 % respectively.
| Base Price |  |  | 4590997
| S.No | Year | CAMC % | Amount
| 1 | 6th | 9 | 413189.73
| 2 | 7th | 9 | 413189.73
| 3 | 8th | 9 | 413189.73
| 4 | 9th | 9 | 413189.73
| 5 | 10th | 9 | 413189.73
| Total % |  | 45
| Total Amount |  |  | 2065948.65

## VELIND
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | Recording in counselling room |  |  |  | 1 | Job | 144246 | 144246 | 56255.94
2 | Local Area Network (LAN) System | Local Area Network (LAN) System | Local Area Network (LAN) System | Local Area Network (LAN) System | 1 | Job | 418531 | 418531 | 163227.09
3 | Supply, Transportation and installation of 20KVA / 312V DC on line UPS system | Supply, Transportation and installation of 20KVA / 312V DC on line UPS system | Supply, Transportation and installation of 20KVA / 312V DC on line UPS system | Supply, Transportation and installation of 20KVA / 312V DC on line UPS system | 2 | Nos | 565803 | 1131606 | 441326.34
| Total Amount | [6 empty] | 1694383 | 660809.37
| GST @ 18% | [6 empty] | 304988.94
| Total Amount excluding CAMC | [6 empty] | 1999371.94
| CAMC Amount as per below table | [6 empty] | 660809.37
| Total Amount including CAMC | [6 empty] | 2660181.31
Comprehensive Annual Maintanance Charges post warranty period for 5 years(6th to 10th year) @6, 7, 8, 9, 9 % respectively.
| Base Price |  |  | 1694383
| S.No | Year | CAMC % | Amount
| 1 | 6th | 6 | 101662.98
| 2 | 7th | 7 | 118606.81
| 3 | 8th | 8 | 135550.64
| 4 | 9th | 9 | 152494.47
| 5 | 10th | 9 | 152494.47
| Total % |  | 39
| Total Amount |  |  | 660809.37

## SURYA TE
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | Recording in counselling room |  |  |  | 1 | Job | 150244 | 150244 | 63102.48
2 | Local Area Network (LAN) System | Local Area Network (LAN) System | Local Area Network (LAN) System | Local Area Network (LAN) System | 1 | Job | 438326 | 438326 | 184096.92
3 | Supply, Transportation and installation of 20KVA / 312V DC on line UPS system | Supply, Transportation and installation of 20KVA / 312V DC on line UPS system | Supply, Transportation and installation of 20KVA / 312V DC on line UPS system | Supply, Transportation and installation of 20KVA / 312V DC on line UPS system | 2 | Nos | 576709 | 1153418 | 484435.56
| Total Amount | [6 empty] | 1741988 | 731634.96
| GST @ 18% | [6 empty] | 313557.84
| Total Amount excluding CAMC | [6 empty] | 2055545.84
| CAMC Amount as per below table | [6 empty] | 731634.96
| Total Amount including CAMC | [6 empty] | 2787180.8
Comprehensive Annual Maintanance Charges post warranty period for 5 years(6th to 10th year) @8, 8,8, 9, 9 % respectively.
| Base Price |  |  | 1741988
| S.No | Year | CAMC % | Amount
| 1 | 6th | 8 | 139359.04
| 2 | 7th | 8 | 139359.04
| 3 | 8th | 8 | 139359.04
| 4 | 9th | 9 | 156778.92
| 5 | 10th | 9 | 156778.92
| Total % |  | 42
| Total Amount |  |  | 731634.96

## BSM
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | Monitor Stand beside Bed in ICUs & TIRs |  |  |  | 31 | Nos | 5589 | 173259 | 69303.6
| Double arm Surgical Pendant (supported): The pendant shall be imparted & comply with NFPA99c/HTM 02-01/ISO7396-1/DIN. The support arms shall be extremely robust and revolve on high quality bearings so that pendant head glides smoothly and quickly to any desired position. double moveable arms with total coverage of not less than 1800mm and 330deg, horizontal movement for each arm, which can be easily adjusted to suit desired mode of operation. Vertical movement shall be motorized. Weight carrying capacity of the arm shall not be less than 180 kgs Shall have pneumatic brakes The pendant service heads shall be modular with minimum 1200mm head. the head shall be capable of accepting a range of shavasana infusion poles or other accessories. The pendant heads shall support the range of physiological Monitor Mounting solutions. Shall be dual art of 800mm/8tXfmm.05 no's platforms of not less than 5tXImm x5tXbnm x400mm,01 no's Drawer for place Accessories. Each platform shall have a weight bearing capacity of minimum 30kg each. Sail has iv rod stand with capacity of 30 kg with 4-hooks for each rod. medical gas outlets CO2-02 NOS, Vacuum - 2n0s, Air (7bar)-2nos, Electrical sockets 12no, shall provide on the service head (6on each side), DATA port RJ-45/cat6 -2nos. all interface for integration, braking systems, a small spring arm on the side support an additional monitor. |  |  |  | 6 | Nos | 1280000 | 7680000 | 3072000
| Total Amount | [6 empty] | 7853259 | 3141303.6
| GST @ 18% | [6 empty] | 1413586.62
| Total Amount excluding CAMC | [6 empty] | 9266845.62
| CAMC Amount as per below table | [6 empty] | 3141303.6
| Total Amount including CAMC | [6 empty] | 12408149.22
Double arm Surgical Pendant (supported): The pendant shall be imparted & comply with NFPA99c/HTM 02-01/ISO7396-1/DIN. The support arms shall be extremely robust and revolve on high quality bearings so that pendant head glides smoothly and quickly to any desired position. double moveable arms with total coverage of not less than 1800mm and 330deg, horizontal movement for each arm, which can be easily adjusted to suit desired mode of operation. Vertical movement shall be motorized. Weight carrying capacity of the arm shall not be less than 180 kgs Shall have pneumatic brakes The pendant service heads shall be modular with minimum 1200mm head. the head shall be capable of accepting a range of shavasana infusion poles or other accessories. The pendant heads shall support the range of physiological Monitor Mounting solutions. Shall be dual art of 800mm/8tXfmm.05 no's platforms of not less than 5tXImm x5tXbnm x400mm,01 no's Drawer for place Accessories. Each platform shall have a weight bearing capacity of minimum 30kg each. Sail has iv rod stand with capacity of 30 kg with 4-hooks for each rod. medical gas outlets CO2-02 NOS, Vacuum - 2n0s, Air (7bar)-2nos, Electrical sockets 12no, shall provide on the service head (6on each side), DAT port RJ-45/cat6 -2nos. all interface for integration, braking systems, a small spring arm on the side support an additional monitor.
Comprehensive Annual Maintanance Charges post warranty period for 5 years(6th to 10th year) @8, 8,8, 8, 8 % respectively.
| Base Price |  |  | 7853259
| S.No | Year | CAMC % | Amount
| 1 | 6th | 8 | 628260.72
| 2 | 7th | 8 | 628260.72
| 3 | 8th | 8 | 628260.72
| 4 | 9th | 8 | 628260.72
| 5 | 10th | 8 | 628260.72
| Total % |  | 40
| Total Amount |  |  | 3141303.6

## MDS
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | Monitor Stand beside Bed in ICUs & TIRs |  |  |  | 31 | Nos | 5692 | 176452 | 79403.4
| Total Amount | [6 empty] | 176452 | 79403.4
| GST @ 18% | [6 empty] | 31761.36
| Total Amount excluding CAMC | [6 empty] | 208213.36
| CAMC Amount as per below table | [6 empty] | 79403.4
| Total Amount including CAMC | [6 empty] | 287616.76
Comprehensive Annual Maintanance Charges post warranty period for 5 years(6th to 10th year) @9, 9, 9, 9, 9 % respectively.
| Base Price |  |  | 176452
| S.No | Year | CAMC % | Amount
| 1 | 6th | 9 | 15880.68
| 2 | 7th | 9 | 15880.68
| 3 | 8th | 9 | 15880.68
| 4 | 9th | 9 | 15880.68
| 5 | 10th | 9 | 15880.68
| Total % |  | 45
| Total Amount |  |  | 79403.4

## DG-1
Srinidhi
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | 750 KVA Generator Set with AMF Control Panel Supply, Transportation, erection and commissioning (Excluding Foundation) of 3 Phase, 415, 50Hz, water cooled multi cylinder diesel generator set with alternator of 750 KVA output continuous rating directly coupled Engine and Alternator 750 KVA, 415 Volts with guard and mounted on a common base plate of Robust construction and complete with AMF panel having IP-52 protection, Acoustic Enclosure as per CPCB norms , sound absorbing material, t to restrict sound level up to 75 dB up to 1 Mtr distance and as per CPCB norms etc. |  |  |  | 1 | Nos | 8275000 | 8275000 | 3310000 | 9764500
| Total Amount | [6 empty] | 8275000 | 3310000 | 8275000
| GST @ 18% | [6 empty] | 1489500
| Total Amount excluding CAMC | [6 empty] | 9764500
| CAMC Amount as per below table | [6 empty] | 3310000
| Total Amount including CAMC | [6 empty] | 13074500
Comprehensive Annual Maintanance Charges post warranty period for 5 years(6th to 10th year) @8, 8, 9, 9, 9 % respectively.
| Base Price |  |  | 8275000
| S.No | Year | CAMC % | Amount
| 1 | 6th | 6 | 496500
| 2 | 7th | 7 | 579250
| 3 | 8th | 8 | 662000
| 4 | 9th | 9 | 744750
| 5 | 10th | 10 | 827500
| Total % |  | 40
| Total Amount |  |  | 3310000

## DG-2
iCARE
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | 750 KVA Generator Set with AMF Control Panel Supply, Transportation, erection and commissioning (Excluding Foundation) of 3 Phase, 415, 50Hz, water cooled multi cylinder diesel generator set with alternator of 750 KVA output continuous rating directly coupled Engine and Alternator 750 KVA, 415 Volts with guard and mounted on a common base plate of Robust construction and complete with AMF panel having IP-52 protection, Acoustic Enclosure as per CPCB norms , sound absorbing material, t to restrict sound level up to 75 dB up to 1 Mtr distance and as per CPCB norms etc. |  |  |  | 1 | Nos | 8360000 | 8360000 | 3511200 | 9864800
| Total Amount | [6 empty] | 8360000 | 3511200 | 8360000
| GST @ 18% | [6 empty] | 1504800
| Total Amount excluding CAMC | [6 empty] | 9864800
| CAMC Amount as per below table | [6 empty] | 3511200
| Total Amount including CAMC | [6 empty] | 13376000
Comprehensive Annual Maintanance Charges post warranty period for 5 years(6th to 10th year) @8, 8, 9, 9, 9 % respectively.
| Base Price |  |  | 8360000
| S.No | Year | CAMC % | Amount
| 1 | 6th | 7 | 585200
| 2 | 7th | 7 | 585200
| 3 | 8th | 9 | 752400
| 4 | 9th | 9 | 752400
| 5 | 10th | 10 | 836000
| Total % |  | 42
| Total Amount |  |  | 3511200

## RO-1
MPS-ASTA
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | Supply and installation of double pass RO system with raw water tank capacity of 5000 ltr plastic tank having 2 nos feed pumps of 1.5 HP with max flow of 9000 ltr/hr including construction of sand filter of dimensions (H=1665 mm, D=325 mm) with filter media as Quartz sand of SS vessel construction and Activated Carbon filter of dimensions (H= 1665mm) with filter media as Activated carbon (IV-600) of SS vessel construction, with 4 nos of spiral wound RO membrane of size 8 inch dia x 1 m length of make G.E OSMONICS (or) HYDRAUNAUTICS, 4 nos UV system with service flow of 1500 ltr/hr (Before Snd filter and after SS tank out-let) with cPVC pipeline recirculation loop to avoid contamination in pipe to supply for 10 beds in Post ICU, 4 beds in Transplant ICU, 1 for each TIR, 2 in Point of Care Lab and one for each scrub station) Drinage outlet to be provided near each RO outlet. |  |  |  | 1 | Nos | 5084746 | 5084746 | 1779661.1 | 9735000
| Total Amount | [6 empty] | 5084746 | 1779661.1 | 8250000
| GST @ 18% | [6 empty] | 915254.28
| Total Amount excluding CAMC | [6 empty] | 6000000.28
| CAMC Amount as per below table | [6 empty] | 2100000.098
| Total Amount including CAMC | [6 empty] | 8100000.378
Comprehensive Annual Maintanance Charges post warranty period for 5 years(6th to 10th year) @7, 7, 7, 7, 7 % respectively.
6000000.28
| S.No | Year | CAMC % | Amount
| 1 | 6th | 7 | 420000.0196
| 2 | 7th | 7 | 420000.0196
| 3 | 8th | 7 | 420000.0196
| 4 | 9th | 7 | 420000.0196
| 5 | 10th | 7 | 420000.0196
| Total % |  | 35
| Total Amount |  |  | 2100000.098

## RO-2
Ananya
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | Supply and installation of double pass RO system having 2 nos feed pumps of 1.5 HP with max flow of 4000 ltr/hr including construction of sand filter of dimensions (H=1650 mm, D=325 mm) with filter media as Quartz sand of SS vessel construction and Activated Carbon filter of dimensions (H= 1650mm) with filter media as Activated carbon (IV-600) of SS vessel construction, with 4 nos of spiral wound RO membrane of size 4 inch dia x 1 m length of make ION EXCHANGE (HYDROMEN) (or) equal, 2 nos UV system with service flow of 1000 ltr/hr (Before 2nd filter and after SS tank out-let) with PEX pipeline recirculation loop to avoid contamination in pipe to supply for 10 beds in Post ICU, 4 beds in Transplant ICU and 1 for each TIR.) Drinage outlet to be provided near each RO outlet. |  |  |  | 1 | Nos | 5425000 | 5425000 | 4502750 | 5425000 | 9735000
| Total Amount | [6 empty] | 5425000 | 4502750 |  | 8250000
| GST @ 18% | [6 empty] | 976500
| Total Amount excluding CAMC | [6 empty] | 6401500
| CAMC Amount as per below table | [6 empty] | 4502750
| Total Amount including CAMC | [6 empty] | 10904250
Comprehensive Annual Maintanance Charges post warranty period for 5 years(6th to 10th year) @7, 7, 7, 7, 7 % respectively.
5425000
| S.No | Year | CAMC % | Amount
| 1 | 6th | 14 | 759500
| 2 | 7th | 15 | 813750
| 3 | 8th | 16 | 868000
| 4 | 9th | 18 | 976500
| 5 | 10th | 20 | 1085000
| Total % |  | 83
| Total Amount |  |  | 4502750

## RO-3
Blue Space Medicals
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | Supply and installation of double pass RO system having 2 nos feed pumps of 1.5 HP with max flow of 4000 ltr/hr including construction of sand filter of dimensions (H=1650 mm, D=325 mm) with filter media as Quartz sand of SS vessel construction and Activated Carbon filter of dimensions (H= 1650mm) with filter media as Activated carbon (IV-600) of SS vessel construction, with 4 nos of spiral wound RO membrane of size 4 inch dia x 1 m length of make ION EXCHANGE (HYDROMEN) (or) equal, 2 nos UV system with service flow of 1000 ltr/hr (Before 2nd filter and after SS tank out-let) with PEX pipeline recirculation loop to avoid contamination in pipe to supply for 10 beds in Post ICU, 4 beds in Transplant ICU and 1 for each TIR.) Drinage outlet to be provided near each RO outlet. |  |  |  | 1 | Nos | 5510000 | 5510000 | 4683500 | 9735000
| Total Amount | [6 empty] | 5510000 | 4683500 | 8250000
| GST @ 18% | [6 empty] | 991800
| Total Amount excluding CAMC | [6 empty] | 6501800
| CAMC Amount as per below table | [6 empty] | 4683500
| Total Amount including CAMC | [6 empty] | 11185300
Comprehensive Annual Maintanance Charges post warranty period for 5 years(6th to 10th year) @7, 7, 7, 7, 7 % respectively.
5510000
| S.No | Year | CAMC % | Amount
| 1 | 6th | 12 | 661200
| 2 | 7th | 15 | 826500
| 3 | 8th | 18 | 991800
| 4 | 9th | 20 | 1102000
| 5 | 10th | 20 | 1102000
| Total % |  | 85
| Total Amount |  |  | 4683500

## MPS-ASTA (2)
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | 750 KVA Generator Set with AMF Control Panel Supply, Transportation, erection and commissioning (Excluding Foundation) of 3 Phase, 415, 50Hz, water cooled multi cylinder diesel generator set with alternator of 750 KVA output continuous rating directly coupled Engine and Alternator 750 KVA, 415 Volts with guard and mounted on a common base plate of Robust construction and complete with AMF panel having IP-52 protection, Acoustic Enclosure as per CPCB norms , sound absorbing material, t to restrict sound level up to 75 dB up to 1 Mtr distance and as per CPCB norms etc. |  |  |  | 1 | Nos | 8084745.76 | 8084745.76 | 3339000
2 | Supply and installation of double pass RO system having 2 nos feed pumps of 1.5 HP with max flow of 4000 ltr/hr including construction of sand filter of dimensions (H=1650 mm, D=325 mm) with filter media as Quartz sand of SS vessel construction and Activated Carbon filter of dimensions (H= 1650mm) with filter media as Activated carbon (IV-600) of SS vessel construction, with 4 nos of spiral wound RO membrane of size 4 inch dia x 1 m length of make ION EXCHANGE (HYDROMEN) (or) equal, 2 nos UV system with service flow of 1000 ltr/hr (Before 2nd filter and after SS tank out-let) with PEX pipeline recirculation loop to avoid contamination in pipe to supply for 10 beds in Post ICU, 4 beds in Transplant ICU and 1 for each TIR.) Drinage outlet to be provided near each RO outlet. |  |  |  | 1 | Job | 5288135.6 | 5288135.6 | 4459625
| Total Amount | [6 empty] | 13372881.36 | 7798625 | 1559725
| GST @ 18% | [6 empty] | 2407118.6448
| Total Amount excluding CAMC | [6 empty] | 15780000.0048
| CAMC Amount as per below table | [6 empty] | 7798625
| Total Amount including CAMC | [6 empty] | 23578625.0048
| S.No | Year | CAMC % | Amount
| 1 | 6th |  | 1559725
| 2 | 7th |  | 1559725
| 3 | 8th |  | 1559725
| 4 | 9th |  | 1559725
| 5 | 10th |  | 1559725
| Total % |  | 0
| Total Amount |  |  | 7798625

## R3
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | 4 Gas Digital Alarm Panels : 4 Gas Digital Alarm Panel consisting of atl necessary accessories ie Pressure sensors,reguIators,hand valves ,pressure gauges ecL(Oxygen, Nitrous oxide, Medical Air, Vacuum) |  |  |  | 2 | Nos | 43628 | 87256 | 34902.4
2 | 6 Gas Digital Alarm Panele : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. | 6 Gas Digital Alarm Panele : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. | 6 Gas Digital Alarm Panele : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. | 6 Gas Digital Alarm Panele : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. | 6 | Nos | 53172 | 319032 | 127612.8
3 | Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. | Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. | Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. | Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. | 2 | Nos | 20451 | 40902 | 16360.8
4 | 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen. | 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen. | 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen. | 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen. | 1 | Job | 42264 | 42264 | 16905.6
5 | Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED. | Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED. | Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED. | Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED. | 1 | Job | 190873 | 190873 | 76349.2
6 | 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 1 | Job | 42264 | 42264 | 16905.6
7 | 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | 1 | Job | 190873 | 190873 | 76349.2
8 | Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. "Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041 C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED | Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. "Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041 C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED | Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. "Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041 C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED | Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. "Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041 C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED | 1 | Job | 152695 | 152695 | 61078
| Total Amount | [6 empty] | 1066159 | 426463.6
| GST @ 18% | [6 empty] | 191908.62
| Total Amount excluding CAMC | [6 empty] | 1258067.62
| CAMC Amount as per below table | [6 empty] | 426463.6
| Total Amount including CAMC | [6 empty] | 1684531.22
Comprehensive Annual Maintanance Charges post warranty period for 5 years(6th to 10th year) @6, 7, 8, 9, 10 % respectively.
| Base Price |  |  | 1066159
| S.No | Year | CAMC % | Amount
| 1 | 6th | 6 | 63969.54
| 2 | 7th | 7 | 74631.13
| 3 | 8th | 8 | 85292.72
| 4 | 9th | 9 | 95954.31
| 5 | 10th | 10 | 106615.9
| Total % |  | 40
| Total Amount |  |  | 426463.6

## A&A (2)
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | Acoustic Wall Panelling with framework consisting of 25mm high GI wall channels with fully knurled surface of 0.55mm thick bottom wedge of 80mm width, having two equal flanges of 26mm is anchored to GI studs of 50mm high. GI studs of 50mm High to be fixed to wall at 600mm centres, 25mm thick channels are then fixed perpendicular to the GI studs and suitable fixing channel is fixed to the cross channel to fix the panel to achieve overall air gap of 75mm from the wall and GI Clips for inside panel and Clips for border panel of 18mm to be fixed to the GI wall channel to achieve required shape. Secured arranging of polyester wool of – thickness/density, Prelam Board to be installed. 15mm thick Prelam perforated Wooden slat of required dia perforation & pitch is to be customised and then fixed to GI frame rigidly by using fixing channel fastened perpendicular to the cross channel with GI brackets. The boards shall be fixed to the GI frame with special cleats. (MOTs Integration Room) |  |  |  | 110 | Sqm | 5600 | 616000 | 246400
2 | Accooustic Ceiling Paneling with Perforated board Fine line Grid false ceiling using 11mm thick Perforated Board sheet tiles of size 595mm x 595mm fixing to steel precoated GI wall angle of size 25mm x 25mm x 0.70mm thick along the perimeter of ceiling screw fixed to brick work / partition at 610mm center to center and suspending the frame work using precoated GI Tee section (24mm x 38mm x 0.7mm) from soffit at 1220mm center to center fixed with GI Soffit Cleat, rawl plugs and steel expansion fasteners & connecting clip to the GI Tee section with 4mm dia GI rod with galvanised spring steel level clip of PVC unversal holding clips system at 1200mm center to center and Secured arranging of polyester wool of 50mm thick 1000 GSM, Prelam Board to be installed. 15mm thick Prelam perforated Wooden slat of required dia perforation & pitch is to be customised and then fixed to GI frame rigidly by using fixing channel fastened perpendicular to the cross channel with GI brackets. The boards shall be fixed to the GI frame with special cleats. (MOTs Integration Room) |  |  |  | 62 | Sqm | 5010 | 310620 | 124248 | 366544
3 | 80% blockout Ruler Blinds for MOTs Integration Room Windows |  |  |  | 3 | Nos | 11000 | 33000 | 13200
4 | Wooden Flooring with Engineered wood planks of 14mm thick (MOTs Integration Room) |  |  |  | 65 | Sqm | 6500 | 422500 | 169000
5 | Skirting for Wooden Flooring with Engineered wood planks of 14mm thick (MOTs Integration Room) |  |  |  | 40 | Rmt | 850 | 34000 | 13600
| Total Amount | [6 empty] | 1416120 | 383848
| GST @ 18% | [6 empty] | 254901.6
| Total Amount excluding CAMC | [6 empty] | 1671021.6
| CAMC Amount as per below table | [6 empty] | 566448
| Total Amount including CAMC | [6 empty] | 2237469.6
Comprehensive Annual Maintanance Charges post warranty period for 5 years(6th to 10th year) @6, 7, 8, 9, 10 % respectively.
| Base Price |  |  | 1416120
| S.No | Year | CAMC % | Amount
| 1 | 6th | 6 | 84967.2
| 2 | 7th | 7 | 99128.4
| 3 | 8th | 8 | 113289.6
| 4 | 9th | 9 | 127450.8
| 5 | 10th | 10 | 141612
| Total % |  | 40
| Total Amount |  |  | 566448

## MPS-ASTA (3)
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | Acoustic Wall Panelling with framework consisting of 25mm high GI wall channels with fully knurled surface of 0.55mm thick bottom wedge of 80mm width, having two equal flanges of 26mm is anchored to GI studs of 50mm high. GI studs of 50mm High to be fixed to wall at 600mm centres, 25mm thick channels are then fixed perpendicular to the GI studs and suitable fixing channel is fixed to the cross channel to fix the panel to achieve overall air gap of 75mm from the wall and GI Clips for inside panel and Clips for border panel of 18mm to be fixed to the GI wall channel to achieve required shape. Secured arranging of polyester wool of – thickness/density, Prelam Board to be installed. 15mm thick Prelam perforated Wooden slat of required dia perforation & pitch is to be customised and then fixed to GI frame rigidly by using fixing channel fastened perpendicular to the cross channel with GI brackets. The boards shall be fixed to the GI frame with special cleats. (MOTs Integration Room) |  |  |  | 110 | Sqm | 5381.36 | 591949.6 | 150000
2 | Accooustic Ceiling Paneling with Perforated board Fine line Grid false ceiling using 11mm thick Perforated Board sheet tiles of size 595mm x 595mm fixing to steel precoated GI wall angle of size 25mm x 25mm x 0.70mm thick along the perimeter of ceiling screw fixed to brick work / partition at 610mm center to center and suspending the frame work using precoated GI Tee section (24mm x 38mm x 0.7mm) from soffit at 1220mm center to center fixed with GI Soffit Cleat, rawl plugs and steel expansion fasteners & connecting clip to the GI Tee section with 4mm dia GI rod with galvanised spring steel level clip of PVC unversal holding clips system at 1200mm center to center and Secured arranging of polyester wool of 50mm thick 1000 GSM, Prelam Board to be installed. 15mm thick Prelam perforated Wooden slat of required dia perforation & pitch is to be customised and then fixed to GI frame rigidly by using fixing channel fastened perpendicular to the cross channel with GI brackets. The boards shall be fixed to the GI frame with special cleats. (MOTs Integration Room) |  |  |  | 62 | Sqm | 4830.51 | 299491.62 | 75875
3 | 80% blockout Ruler Blinds for MOTs Integration Room Windows |  |  |  | 3 | Nos | 10169.49 | 30508.47 | 12600
4 | Wooden Flooring with Engineered wood planks of 14mm thick (MOTs Integration Room) |  |  |  | 65 | Sqm | 6186.44 | 402118.6 | 80000
5 | Skirting for Wooden Flooring with Engineered wood planks of 14mm thick (MOTs Integration Room) |  |  |  | 40 | Rmt | 762.71 | 30508.4 | 12600
| Total Amount | [6 empty] | 1354576.69 | 331075 | 66215
| GST @ 18% | [6 empty] | 243823.8042
| Total Amount excluding CAMC | [6 empty] | 1598400.4942
| CAMC Amount as per below table | [6 empty] | 331075
| Total Amount including CAMC | [6 empty] | 1929475.4942
| S.No | Year | CAMC % | Amount
| 1 | 6th |  | 66215
| 2 | 7th |  | 66215
| 3 | 8th |  | 66215
| 4 | 9th |  | 66215
| 5 | 10th |  | 66215
| Total % |  | 0
| Total Amount |  |  | 331075

## MPS-ASTA (4)
ANNEXURE-01
Sl. No | Item Description |  |  |  | Qty | Unit | Rate | Amount | CAMC Amount for 5 Years
Unit
1 | Supply and installation of 50mm thick double skin modular wall Panels made of 0.8 mm thick powder coated GI on both the sides, with 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, flush on both sides with maximum allowable gap of 3- 4mm filled with food grade silicon sealant and placed on cold rolled galvanised bottom tracks with a recess to provide floor to wall coving flush with the wall panel. This includes all required harware for completion Panels to be covered with a protective film to avoid any damages during transportation and installation |  |  |  | 297.52 | Sqm | 6313.55 | 1878407.396 | 225000
2 | Supply and installation of 50mm thick double skin ceiling system made of 0.8 mm thick Powder Coated GI sheets on both sides, 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, panels flush towards room side with maximum allowable gap of 3-4mm at panel to panel joints filled with silicon sealant. Ceiling panels are suspended from the RCC slab by using concealed AL ceiling grid with tie rod and adjustable turn buckle arrangement etc. This includes all required hardware for completion. Panels to be covered with a protective film to avoid any damages during transportation and installation |  |  |  | 163.08 | Sqm | 6313.55 | 1029613.734 | 175000
| Total Amount | [6 empty] | 2908021.13 | 400000 | 80000
| GST @ 18% | [6 empty] | 523443.8034
| Total Amount excluding CAMC | [6 empty] | 3431464.9334
| CAMC Amount as per below table | [6 empty] | 400000
| Total Amount including CAMC | [6 empty] | 3831464.9334
| S.No | Year | CAMC % | Amount
| 1 |  |  | 80000
| 2 | 7th |  | 80000
| 3 | 8th |  | 80000
| 4 | 9th |  | 80000
| 5 | 10th |  | 80000
| Total % |  | 0
| Total Amount |  |  | 400000