## RE 15.03.2024
REVISED ESTIMATE OF SOTC 8TH FLOOR, SOUTH-WEST BLOCK, GANDHI HOSPITAL (Amount in Rs.)
S.No | Tech. Spec Cl. No in TED | Item Code | Item Name | UOM | Unit Rate (Rs.) | As Per Agreement (with 4 OTs) |  | Additional Sanction for 2 OTs |  | Total (6 OTs) |  | As Per Work Done/To Be Done |  | CAMC Unit Rate (As per Price bid) | Total CAMC
[6 empty] | QTY | Amount | QTY | Amount | QTY | Amount | QTY | Amount
1 | 1 | SOTC001 | Stainless Steel Pre-fabricated Wall panels. (MOTs & MOT Corridor) - Wall panels | Sqm | 15010 | 400 | 6004000 | 350 | 5253500 | 750 | 11257500 | 491.9486 | 7384148 | 5253.5 | 2584452 |  | AE | AUTHORIZED EXTRAS | 59355462 | 61
2 | 1 | SOTC002 | Stainless Steel Pre-fabricated Ceiling panels In MOTs & MOTs Corridor | Sqm | 15010 | 385 | 5778850 | 78 | 1170780 | 463 | 6949630 | 263.165 | 3950107 | 5253.5 | 1382537 |  | SI | SUPPLEMENTAL ITEMS | 250533639.825 | 32
3 | 1.5 | SOTC003 | Dynamic Hatch Box | Nos | 295000 | 2 | 590000 | 1 | 295000 | 3 | 885000 | 0 | 0 | 103250 | 0 |  |  |  | 309889101.825 | 93
4 | 2.1 | SOTC004 | Electro conductive Flooring inside MOTs | Sqm | 4035 | 160 | 645600 | 80 | 322800 | 240 | 968400 | 217.7802 | 878743 | 1412.25 | 307560
5 | 2.2 | SOTC005 | Flooring with Vinyl Sheets In MOT Corridor | Sqm | 3750 | 175 | 656250 | 50 | 187500 | 225 | 843750 | 87.0329 | 326374 | 1312.5 | 114231
6 | 3 | SOTC006 | Uni Directional Ceiling Laminar Airflow Systems | Nos | 465000 | 4 | 1860000 | 2 | 930000 | 6 | 2790000 | 6 | 2790000 | 162750 | 976500 | AE
7 | 3.1 | SOTC007 | Air Handling Units (AHUs) 11 TR | Nos | 1495000 | 4 | 5980000 | 2 | 2990000 | 6 | 8970000 | 6 | 8970000 | 523250 | 3139500
8 | 3.2 | SOTC008 | Condensing Units | Nos | 345000 | 4 | 1380000 | 2 | 690000 | 6 | 2070000 | 6 | 2070000 | 0 | 0
9 |  |  | AE |  | 345000 | [6 empty] | 4 | 1380000 | 0 | 0
10 | 4 | SOTC009 | Pressure Relief Dampers | Nos | 22500 | 4 | 90000 | 2 | 45000 | 6 | 135000 | 6 | 135000 | 7875 | 47250
11 | 5.1 | SOTC010 | Single arm Anesthesia Pendants (Imported) | Nos | 1195000 | 4 | 4780000 | 2 | 2390000 | 6 | 7170000 | 6 | 7170000 | 418250 | 2509500 | AE
12 | 5.2 | SOTC011 | Triple Dome Ceiling OT LED Lights (Imported) | Nos | 4750000 | 2 | 9500000 |  | 0 | 2 | 9500000 | 2 | 9500000 | 1662500 | 3325000
13 |  |  | AE |  | 4750000 | [6 empty] | 2 | 9500000 | 1662500 | 3325000 | AE
14 | 5.3 | SOTC012 | Double Dome Ceiling OT LED Lights (Imported) | Nos | 3550000 | 2 | 7100000 | 2 | 7100000 | 4 | 14200000 | 2 | 7100000 | 1242500 | 2485000
15 | 5.4 | SOTC013 | Detachable Hi Definition Cameras in Triple Dome Ceiling OT Lights | Nos | 995000 | 2 | 1990000 | 1 | 995000 | 3 | 2985000 | 3 | 2985000 | 348250 | 1044750
16 | 91 | SOTC014 | Ceiling/Wall mounted CCTV Room Camera | Nos | 22500 | 4 | 90000 | 2 | 45000 | 6 | 135000 | 6 | 135000 | 7875 | 47250 | AE
17 | 6 | SOTC015 | LED Peripheral Lights cum clean room (OT) luminaries | Nos | 18750 | 62 | 1162500 | 40 | 750000 | 102 | 1912500 | 102 | 1912500 | 6562.5 | 669375
18 |  |  | AE |  | 18750 | [6 empty] | 5 | 93750 | 6562.5 | 32813
19 | 7 | SOTC016 | View Window with Motorised Blinds of 1 Mt Length & 1 Mt Height | Nos | 115000 | 7 | 805000 | 2 | 230000 | 9 | 1035000 | 9 | 1035000 | 40250 | 362250
20 |  |  | AE |  | 115000 | [6 empty] | 5 | 575000 | 40250 | 201250 | AE
21 | 8 | SOTC017 | Hermetically Sealed Doors (1.80mt x 2.10 mt) | Nos | 115000 | 4 | 460000 | 2 | 230000 | 6 | 690000 | 6 | 690000 | 40250 | 241500
22 |  |  | AE |  | 115000 | [6 empty] | 3 | 345000 | 40250 | 120750
23 | 8 | SOTC018 | (1.50mt x 2.10 mt) Sliding Automatic Sliding Doors with View Windoy of 1 Mt x 1 Mt | Nos | 525000 | 2 | 1050000 |  | 0 | 2 | 1050000 | 2 | 1050000 | 183750 | 367500 | AE
24 | 10 | SOTC019 | Storage Units | Nos | 75000 | 4 | 300000 | 2 | 150000 | 6 | 450000 | 6 | 450000 | 26250 | 157500
25 | 11 | SOTC020 | Writing Board (List Board) | Nos | 18750 | 4 | 75000 | 2 | 37500 | 6 | 112500 | 6 | 112500 | 6562.5 | 39375 | AE
26 | 12 | SOTC021 | X-Ray CT Scan LED viewing Screen | Nos | 37500 | 4 | 150000 | 2 | 75000 | 6 | 225000 | 6 | 225000 | 13125 | 78750
27 | 13 | SOTC022 | Touch Screen Surgeon Control Panels | Nos | 385000 | 4 | 1540000 | 2 | 770000 | 6 | 2310000 | 6 | 2310000 | 134750 | 808500 | AE
28 |  |  | AE |  | 385000 | [6 empty] | 3 | 1155000 | 134750 | 404250
29 | 14 | SOTC023 | 3-Bay Scrub Stations/Sinks | Nos | 368750 | 2 | 737500 |  | 0 | 2 | 737500 | 2 | 737500 | 129062.5 | 258125 | AE
30 |  |  | AE |  | 368750 | [6 empty] | 2 | 737500 | 129062.5 | 258125
31 | 16 | SOTC024 | Video and Image Management system | Nos | 8000000 | 1 | 8000000 |  | 0 | 1 | 8000000 | 1 | 8000000 | 2800000 | 2800000 | AE
32 | 16.1 | SOTC025 | Medical Grade Monitors 32 inch 4 K Resolution | Nos | 1295000 | 4 | 5180000 | 2 | 2590000 | 6 | 7770000 | 6 | 7770000 | 453250 | 2719500
33 | 16.2 | SOTC026 | Wall mounted large screen display 55 inch (Commercial Grade) | Nos | 495000 | 2 | 990000 |  | 0 | 2 | 990000 | 2 | 990000 | 173250 | 346500 | AE
34 | 16.3 & 16.4 | SOTC027 | Cable connections for integration within MOTs and with Workshop Projector Hall, Networks with OFC Cable | Job | 997500 | 4 | 3990000 | 2 | 1995000 | 6 | 5985000 | 6 | 5985000 | 349125 | 2094750
35 | 16.5 | SOTC028 | Wireless Microphone | Nos | 255000 | 1 | 255000 |  | 0 | 1 | 255000 | 1 | 255000 | 89250 | 89250
36 | 16.6 | SOTC029 | Digital mixer Amplifier | Nos | 245000 | 1 | 245000 |  | 0 | 1 | 245000 | 1 | 245000 | 85750 | 85750
37 | 16.7 | SOTC030 | Ceiling Mounted Speakers | Nos | 15000 | 4 | 60000 | 2 | 30000 | 6 | 90000 | 6 | 90000 | 5250 | 31500
38 | 16.8 | SOTC031 | Video Conferencing System | Nos | 1195000 | 1 | 1195000 |  | 0 | 1 | 1195000 | 1 | 1195000 | 418250 | 418250
39 | 17.1 | SOTC032 | Home Theatre Power Conditioner, 230 V | Nos | 145000 | 1 | 145000 |  | 0 | 1 | 145000 | 1 | 145000 | 50750 | 50750
40 | 17.2 | SOTC033 | Amplifier (8 Channel) | Nos | 245000 | 1 | 245000 |  | 0 | 1 | 245000 | 1 | 245000 | 85750 | 85750
41 | 17.3 | SOTC034 | HiFi Active Sub Woofer | Nos | 50000 | 1 | 50000 |  | 0 | 1 | 50000 | 1 | 50000 | 17500 | 17500
42 | 17.5 | SOTC035 | 4K Laser Projection TV | Nos | 1495000 | 1 | 1495000 |  | 0 | 1 | 1495000 | 1 | 1495000 | 523250 | 523250
43 | 17.6 & 17.7 | SOTC036 | Equalization & Loud Speaker Control System | Nos | 40000 | 1 | 40000 |  | 0 | 1 | 40000 | 1 | 40000 | 14000 | 14000
44 | 17.8 | SOTC037 | Sound Analog Mixer | Nos | 245000 | 1 | 245000 |  | 0 | 1 | 245000 | 1 | 245000 | 85750 | 85750
45 | 19 | SOTC038 | Electrical Installations in MOTs & TIRs | Job | 195000 | 7 | 1365000 | 2 | 390000 | 9 | 1755000 | 9 | 1755000 | 68250 | 614250
46 | 1 | SOTC039 | Stainless Steel Pre-fabricated Wall panels in TIRs & TIR Corridor | Sqm | 15010 | 202 | 3032020 | 0 | 0 | 202 | 3032020 | 202 | 3032020 | 5253.5 | 1061207
47 |  |  | AE |  | 15010 | [6 empty] | 136.9318 | 2055346 | 5253.5 | 719371 | AE
48 | 1 | SOTC040 | Stainless Steel Pre-fabricated Ceiling panels in TIRs and TIR Corridor | Sqm | 15010 | 146 | 2191460 | 0 | 0 | 146 | 2191460 | 146 | 2191460 | 5253.5 | 767011
49 |  |  | AE |  | 15010 | [6 empty] | 33.22 | 498632 | 5253.5 | 174521 | AE
50 | 2.1 | SOTC041 | Electro conductive Flooring inside TIRs | Sqm | 4035 | 146 | 589110 |  | 0 | 146 | 589110 | 73.6644 | 297236 | 1412.25 | 104033
51 | 2.2 | SOTC042 | Flooring with Vinyl Sheets In TIR Corridor | Sqm | 3750 | 61 | 228750 |  | 0 | 61 | 228750 | 61 | 228750 | 1312.5 | 80063
52 |  |  | AE |  | 3750 | [6 empty] | 70.4074 | 264028 | 1312.5 | 92410
53 | 3 | SOTC043 | Uni Directional Ceiling Laminar Airflow Systems | Nos | 395000 | 3 | 1185000 |  | 0 | 3 | 1185000 | 3 | 1185000 | 138250 | 414750
54 | 3.1 | SOTC044 | Air Handling Units (AHUs) 11 TR | Nos | 1495000 | 2 | 2990000 |  | 0 | 2 | 2990000 | 2 | 2990000 | 523250 | 1046500 | AE
55 | 3.1 | SOTC045 | Air Handling Units (AHUs) 8.5 TR | Nos | 1195000 | 1 | 1195000 |  | 0 | 1 | 1195000 | 1 | 1195000 | 418250 | 418250
56 | 3.2 | SOTC046 | Condensing Units | Nos | 345000 | 3 | 1035000 |  | 0 | 3 | 1035000 | 3 | 1035000 | 120750 | 362250
57 |  |  | AE |  | 345000 | [6 empty] | 3 | 1035000 | 120750 | 362250 | AE
58 | 4 | SOTC047 | Pressure Relief Dampers | Nos | 22500 | 3 | 67500 |  | 0 | 3 | 67500 | 3 | 67500 | 7875 | 23625
59 | 8 | SOTC049 | Hermetically Sealed Doors (1.80mt x 2.10 mt) | Nos | 525000 | 3 | 1575000 |  | 0 | 3 | 1575000 | 3 | 1575000 | 183750 | 551250 | AE
60 | 15 | SOTC050 | 12mm thick glazed Glass partition walls in TIRs | Sqm | 650 | 40 | 26000 |  | 0 | 40 | 26000 | 40 | 26000 | 227.5 | 9100
61 | 15 | SOTC051 | Wall mounted LED TV43 inchesFull HD | Nos | 165000 | 3 | 495000 |  | 0 | 3 | 495000 | 3 | 495000 | 57750 | 173250
62 | 91 | SOTC052 | Ceiling/Wall mounted CCTV Room Camera | Nos | 12000 | 3 | 36000 |  | 0 | 3 | 36000 | 3 | 36000 | 4200 | 12600
63 | 88.6 | SOTC053 | BED HEAD PANEL FOR TIR WITH DOUBLE OUTLETS AND ELECTRICAL OUTLETS | Nos | 49500 | 3 | 148500 |  | 0 | 3 | 148500 | 3 | 148500 | 17325 | 51975
64 | 12 | SOTC054 | X-RAY VIEWERS FOR ALL ICUS AND PRE OPP AREAS AND DOCTORS ROOMS | Nos | 37500 | 5 | 187500 |  | 0 | 5 | 187500 | 5 | 187500 | 13125 | 65625
65 |  |  | AE |  | 37500 | [6 empty] | 1 | 37500 | 13125 | 13125
66 | 11 | SOTC055 | WRITING BOARDS FOR ICUS, PRE OPP | Nos | 18750 | 5 | 93750 |  | 0 | 5 | 93750 | 5 | 93750 | 6562.5 | 32813 | AE
67 |  |  | AE |  | 18750 | [6 empty] | 1 | 18750 | 6562.5 | 6563
68 | 91 | SOTC056 | CCTV CEILING CAMERA | Nos | 9500 | 10 | 95000 |  | 0 | 10 | 95000 | 10 | 95000 | 3325 | 33250
69 | 22 a | SOTC057 | Supply and Fixing of 25mm dia Conduit Pipes surface on wall. | Rmt | 110 | 10000 | 1100000 |  | 0 | 10000 | 1100000 | 10000 | 1100000 | 38.5 | 385000 | AE
70 | 22 b | SOTC058 | Supply and Fixing of 25mm dia Conduit Pipes Concealed on wall. | Rmt | 115 | 4000 | 460000 |  | 0 | 4000 | 460000 | 4000 | 460000 | 40.25 | 161000
71 | 23 a | SOTC059 | Wiring with run of 2 of 1.5 Sqmm Copper cable for points wiring. | Pts | 1525 | 570 | 869250 |  | 0 | 570 | 869250 | 570 | 869250 | 533.75 | 304238
72 | 23 b | SOTC060 | Wiring with run of 2 of 1.5 Sqmm Copper cable for stairecase points wiring. | Pts | 1100 | 10 | 11000 |  | 0 | 10 | 11000 | 10 | 11000 | 385 | 3850 | AE
73 | 23 c | SOTC061 | Supply and fixing of 6A/10A ISI Mark 3/2 pin Modular socket Common switch board | Pts | 900 | 25 | 22500 |  | 0 | 25 | 22500 | 25 | 22500 | 315 | 7875
74 | 23 d | SOTC062 | Wiring with 3 of 1.5 sq.mm with 6A switch and 6A, 3/2 pin socket Modular type with 6A switch control fixing on separate board. | Pts | 2800 | 50 | 140000 |  | 0 | 50 | 140000 | 50 | 140000 | 980 | 49000
75 | 23 e | SOTC063 | Supply and fixing of 6A switchs - 2 Nos and 6A 3/2 pin socket - 3 Nos Modular type with cover plate | Pts | 1400 | 200 | 280000 |  | 0 | 200 | 280000 | 200 | 280000 | 490 | 98000 | AE
76 | 23 f | SOTC064 | Supply & fixing of 16A/6A, 2 in one socket with 16A switch control modular type | Nos | 900 | 200 | 180000 |  | 0 | 200 | 180000 | 200 | 180000 | 315 | 63000
77 | 23 g | SOTC065 | Supply & fixing of 32A, socket with switch control modular | Nos | 1600 | 18 | 28800 |  | 0 | 18 | 28800 | 18 | 28800 | 560 | 10080
78 | 23 h | SOTC066 | Supply & fixing of 64A, socket with 64A switch control modular type | Nos | 18000 | 4 | 72000 |  | 0 | 4 | 72000 | 4 | 72000 | 6300 | 25200
79 | 24 a | SOTC067 | Supply and Run of 1 of 1.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 36 | 2000 | 72000 |  | 0 | 2000 | 72000 | 2000 | 72000 | 12.6 | 25200
80 | 24 b | SOTC068 | Supply and Run of 3 of 1.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable . | Rmt | 100 | 2000 | 200000 |  | 0 | 2000 | 200000 | 2000 | 200000 | 35 | 70000 | AE
81 | 24 c | SOTC069 | Supply and Run of 3 of 2.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 145 | 8000 | 1160000 |  | 0 | 8000 | 1160000 | 8000 | 1160000 | 50.75 | 406000
82 | 24 d | SOTC070 | Supply and Run of 3 runs of 4.0 sq mm (phase neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 230 | 5000 | 1150000 |  | 0 | 5000 | 1150000 | 5000 | 1150000 | 80.5 | 402500
83 | 24 e | SOTC071 | Supply and Run of 3 of 6.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 325 | 300 | 97500 |  | 0 | 300 | 97500 | 300 | 97500 | 113.75 | 34125
84 | 24 f | SOTC072 | Supply and Run of 5 of 6.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 545 | 300 | 163500 |  | 0 | 300 | 163500 | 300 | 163500 | 190.75 | 57225
85 | 24 g | SOTC073 | Supply and Run of 5 of 10.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 850 | 500 | 425000 |  | 0 | 500 | 425000 | 500 | 425000 | 297.5 | 148750
86 | 25 a | SOTC074 | Supply and fixing of DP Metal Enclosure with IP 20 Protection DB Make with 1 No 20A, 10 KA DP MCB | Nos | 1800 | 8 | 14400 |  | 0 | 8 | 14400 | 8 | 14400 | 630 | 5040
87 | 25 b | SOTC075 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 (For Lighting DBs) | Nos | 13000 | 10 | 130000 |  | 0 | 10 | 130000 | 10 | 130000 | 4550 | 45500
88 | 25 c | SOTC076 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 (For Power DB's) | Nos | 13000 | 14 | 182000 |  | 0 | 14 | 182000 | 14 | 182000 | 4550 | 63700
89 | 25 d | SOTC077 | Supply and fixing of 8 Way VTPN DB with IP 43 Protection as per IS:13032 | Nos | 50000 | 5 | 250000 |  | 0 | 5 | 250000 | 5 | 250000 | 17500 | 87500
90 | 25 e | SOTC078 | Supply and fixing of cable adopteres box with cover for DBs including, massanory work etc., complete., | Nos | 6000 | 10 | 60000 |  | 0 | 10 | 60000 | 10 | 60000 | 2100 | 21000
91 | 26 a | SOTC079 | Providing independent earthing for Important equipment with 40mm dia 'B' class 2.5m long G.I pipe (GI Earthing) | Nos | 22500 | 18 | 405000 |  | 0 | 18 | 405000 | 18 | 405000 | 7875 | 141750
92 | 26 b | SOTC080 | Providing independent earthing by exacavating a pit to a depth of 2.25Mtr in all soils as per size specified in the data for Sophisticated Electronic equipment (Copper Earthing) | Nos | 54000 | 18 | 972000 |  | 0 | 18 | 972000 | 18 | 972000 | 18900 | 340200
93 | 26 b 1 | SOTC081 | Providing independent earthing for Important equipment with 100mm dia Heavy gauge C.I Earthing | Nos | 25000 | 6 | 150000 |  | 0 | 6 | 150000 | 6 | 150000 | 8750 | 52500
94 | 26 c | SOTC082 | Supply and Run of 50mm x 6mm G.I Strip | Rmt | 450 | 400 | 180000 |  | 0 | 400 | 180000 | 400 | 180000 | 157.5 | 63000
95 | 26 d | SOTC083 | Supply and Run of 25mm x 3mm copper strip | Rmt | 300 | 400 | 120000 |  | 0 | 400 | 120000 | 400 | 120000 | 105 | 42000
96 | 27 a | SOTC084 | Supply, transportation and fixing of 22W +/ 10% , >/ 2300 lumens, 1200mm length LED light | Nos | 4800 | 20 | 96000 |  | 0 | 20 | 96000 | 20 | 96000 | 1680 | 33600
97 | 27 b | SOTC085 | Supply, transportation and fixing 32-36W (>=3600 Lumens), 2' x2' (600mm x 600mm) slim panel LED luminaire | Nos | 4000 | 60 | 240000 |  | 0 | 60 | 240000 | 60 | 240000 | 1400 | 84000
98 | 27 c | SOTC086 | Supply, transportation and fixing 12 W +/-10% (>= 1200 Lumens) Down lighter back lit LED Down Light Recessed / Surface | Nos | 1400 | 215 | 301000 |  | 0 | 215 | 301000 | 215 | 301000 | 490 | 105350
99 | 27 d | SOTC087 | Supply, transportation and fixing 18 W +/-10% (>= 1800 Lumens) Down lighter back lit LED Down Light | Nos | 1800 | 95 | 171000 |  | 0 | 95 | 171000 | 95 | 171000 | 630 | 59850
100 | 27 e | SOTC088 | Supply, transportation and fixing ISI mark batten holder / slanting holder | Nos | 160 | 8 | 1280 |  | 0 | 8 | 1280 | 8 | 1280 | 56 | 448
101 | 27 f | SOTC089 | Supply, Transportation of energy efficient fan, 1200 mm sweep, aluminium body, consuming 28 W, BEE 5 star rated, ceiling fan | Nos | 3700 | 40 | 148000 |  | 0 | 40 | 148000 | 40 | 148000 | 1295 | 51800
102 | 27 f 1 | SOTC090 | Supply and fixing of Modular type Stepped electronic regulator. | Nos | 1000 | 40 | 40000 |  | 0 | 40 | 40000 | 40 | 40000 | 350 | 14000
103 | 27 f 2 | SOTC091 | Labour charges for fixing of ceiling fan and regulator | Nos | 210 | 40 | 8400 |  | 0 | 40 | 8400 | 40 | 8400 | 73.5 | 2940
104 | 27 f 3 | SOTC092 | Supply and erecting 19/20mm steel tube down rod of one meter length | Nos | 600 | 40 | 24000 |  | 0 | 40 | 24000 | 40 | 24000 | 210 | 8400
105 | 27 g | SOTC093 | Supply of 12" (300mm) Light duty exhaust fan | Nos | 3000 | 5 | 15000 |  | 0 | 5 | 15000 | 5 | 15000 | 1050 | 5250
106 | 27 h | SOTC094 | Supply,Transportation of 12" (300mm) ISI, 900 RPM Heavy duty exhaust fan | Nos | 4900 | 10 | 49000 |  | 0 | 10 | 49000 | 10 | 49000 | 1715 | 17150
107 | 27 i | SOTC095 | Labour charges for fixing the exhaust fan in wall with necessary connections | Nos | 900 | 15 | 13500 |  | 0 | 15 | 13500 | 15 | 13500 | 315 | 4725
108 | 27 j | SOTC096 | Supply and fixing of GI louver shutter including GI mesh | Nos | 3200 | 15 | 48000 |  | 0 | 15 | 48000 | 15 | 48000 | 1120 | 16800
109 | 28 a | SOTC097 | Main Power Panel with 1000A 4 Pole ACB as incomer - 1 No and out goings 800 A 4P MCCB - 1 No., 630 A 4P MCCB - 1 No., 400A 4P MCCB - 4 Nos & 250A 4P MCCB - 3 No's with required Digital Ammeter and Voltmer, LED Indicators | Nos | 1315000 | 1 | 1315000 |  | 0 | 1 | 1315000 | 1 | 1315000 | 460250 | 460250
110 | 28 b | SOTC098 | Floor Power Panel : Incomer: 630A 4 Pole MCCB,- 1 No Outgoings 250 A 4P MCCB - 4 No's 125 A 4P MCCB - 10 No's, 63 A 4P MCCB - 4 No's with required Digital Ammeter and Voltmer, LED Indicators | Nos | 875000 | 1 | 875000 |  | 0 | 1 | 875000 | 1 | 875000 | 306250 | 306250
111 | 28 c | SOTC099 | Electrical Lighting Panels : Incomer: 250 A 4 Pole MCCB - 1 No, Out Goings 125 A 4P MCCB - 4 No's 63 A 4P MCCB - 3 No's with required Digital Ammeter and Voltmer, LED Indicators | Nos | 370000 | 2 | 740000 |  | 0 | 2 | 740000 | 2 | 740000 | 129500 | 259000
112 | 29 d | SOTC100 | 130KVAR Out Door Capacitor panel : Incomer: 250A FP MCCB - 1 No, 63A 10KA TP MCB - 9 Nos. 20 KVAR Capacitor Duty contactors - 5 Nos., 10 KVAR Capacitor Duty contactors - 2 Nos, .5 KVAR Capacitor Duty contactors - 2 Nos. 12 stage APFC Relay - 1 No | Nos | 450000 | 1 | 450000 |  | 0 | 1 | 450000 | 1 | 450000 | 157500 | 157500
113 |  | SOTC101 | 630 KVA Transformer OLTC for transformers with RTCC: Supply, Transportation, Installation, Testing and Commissioning of 630 KVA TRANSFORMER with all test reports. The Transformer shall be designed and manufactured as per IS:1180 OLTC with level-II with initial filling of oil as per IS 335-1993. 1000 A LT Breaker Kiosk - 01 No.The basic details of the Transformer are as under. Makes: Kirloskar / PETE / Esennar / Voltamp / Crompton / ABB / Schneider. | Nos | 4000000 | 1 | 4000000 |  | 0 | 1 | 4000000 | 0 | 0 | 1400000 | 0
114 | 30 a | SOTC102 | Supply of 25 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 300 | 200 | 60000 |  | 0 | 200 | 60000 | 200 | 60000 | 105 | 21000
115 | 30 b | SOTC103 | Supply of 50 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 560 | 200 | 112000 |  | 0 | 200 | 112000 | 200 | 112000 | 196 | 39200
116 | 30 c | SOTC104 | Supply of 70 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 750 | 75 | 56250 |  | 0 | 75 | 56250 | 75 | 56250 | 262.5 | 19688
117 | 30 d | SOTC105 | Supply of 120 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 1050 | 50 | 52500 |  | 0 | 50 | 52500 | 50 | 52500 | 367.5 | 18375
118 | 30 e | SOTC106 | Supply of 185 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 1500 | 50 | 75000 |  | 0 | 50 | 75000 | 50 | 75000 | 525 | 26250
119 | 30 f | SOTC107 | Supply of 240 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 1900 | 100 | 190000 |  | 0 | 100 | 190000 | 100 | 190000 | 665 | 66500
120 | 30 g | SOTC108 | Supply of 300 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 2400 | 500 | 1200000 |  | 0 | 500 | 1200000 | 500 | 1200000 | 840 | 420000
121 | 31 a | SOTC109 | Termination of UG cables of 3.5 core 25 Sq.mm | Nos | 850 | 8 | 6800 |  | 0 | 8 | 6800 | 8 | 6800 | 297.5 | 2380
122 | 31 b | SOTC110 | Termination of UG cables of 3.5 core 50 Sq.mm | Nos | 1200 | 8 | 9600 |  | 0 | 8 | 9600 | 8 | 9600 | 420 | 3360
123 | 31 c | SOTC111 | Termination of UG cables of 3.5 core 70 Sq.mm | Nos | 1500 | 8 | 12000 |  | 0 | 8 | 12000 | 8 | 12000 | 525 | 4200
124 | 31 d | SOTC112 | Termination of UG cables of 3.5 core 120 Sq.mm | Nos | 1900 | 4 | 7600 |  | 0 | 4 | 7600 | 4 | 7600 | 665 | 2660
125 | 31 e | SOTC113 | Termination of UG cables of 3.5 core 185 Sq.mm | Nos | 2500 | 4 | 10000 |  | 0 | 4 | 10000 | 4 | 10000 | 875 | 3500
126 | 31 f | SOTC114 | Termination of UG cables of 3.5 core 240 Sq.mm | Nos | 3500 | 4 | 14000 |  | 0 | 4 | 14000 | 4 | 14000 | 1225 | 4900
127 | 31 g | SOTC115 | Termination of UG cables of 3.5 core 300 Sq.mm | Nos | 4000 | 12 | 48000 |  | 0 | 12 | 48000 | 12 | 48000 | 1400 | 16800
128 | 31 h | SOTC116 | Earth work excavation of Trench laying of U.G cables up to 70 sqmm | Rmt | 1100 | 100 | 110000 |  | 0 | 100 | 110000 | 100 | 110000 | 385 | 38500
129 | 31 i | SOTC117 | Earth work excavation of Trench laying of U.G cables from 95 Sqmm | Rmt | 1150 | 100 | 115000 |  | 0 | 100 | 115000 | 100 | 115000 | 402.5 | 40250
130 | 31 j | SOTC118 | Laying of PVC armoured under ground cable up to 95 Sqmm on wall | Rmt | 125 | 200 | 25000 |  | 0 | 200 | 25000 | 200 | 25000 | 43.75 | 8750
131 | 31 k | SOTC119 | Laying of PVC armoured under ground cable from 120 Sq.mm to 400 Sqmm saddles on wall | Rmt | 270 | 700 | 189000 |  | 0 | 700 | 189000 | 700 | 189000 | 94.5 | 66150
132 | 32 a | SOTC120 | Supply, Transportation and Installation of 150mm x 50mm x 2mm thick hot dip GI perforated cable tray | Rmt | 1295 | 200 | 259000 |  | 0 | 200 | 259000 | 200 | 259000 | 453.25 | 90650
133 | 32 b | SOTC121 | Supply, Transportation and Installation of 300mm x 50mm x 2mm thick thick hot dip GI perforated cable tray | Rmt | 4500 | 100 | 450000 |  | 0 | 100 | 450000 | 100 | 450000 | 1575 | 157500
134 | 33 a | SOTC122 | Supply, Transportation and installation of 10KVA / 312V DC on line UPS system | Nos | 400000 | 7 | 2800000 | 2 | 800000 | 9 | 3600000 | 9 | 3600000 | 140000 | 1260000
135 | 33 b | SOTC123 | Supply and fixing of 12V, 150 AH MF battery | Nos | 25000 | 182 | 4550000 | 52 | 1300000 | 234 | 5850000 | 234 | 5850000 | 8750 | 2047500
136 |  |  | AE |  | 25000 | [6 empty] | 118 | 2950000 | 8750 | 1032500
137 | 33 c | SOTC124 | Supply and providing of UPS cum battery rack 20 batteries | Nos | 30000 | 7 | 210000 | 2 | 60000 | 9 | 270000 | 9 | 270000 | 10500 | 94500
138 |  |  | AE |  | 30000 | [6 empty] | 2 | 60000 | 10500 | 21000
139 | 33 d | SOTC125 | Supply, Transportation, Installation, Testing and commissioning of storage / Pressure type 5 Star rated water heater with ABS plastic body of 15 Ltrs | Nos | 16000 | 7 | 112000 |  | 0 | 7 | 112000 | 7 | 112000 | 5600 | 39200
140 |  |  | AE |  | 16000 | [6 empty] | 4 | 64000 | 5600 | 22400
141 | 34 | SOTC126 | 26 persons ICU bed cum passenger lift (1768 Kgs) G+8 Floors, 9 stops,9 Openings (Cost Includes amount for Construction of Shaft / Cladding from Ground to 8th Floor) | Nos | 10495000 | 1 | 10495000 |  | 0 | 1 | 10495000 | 1 | 10495000 | 3673250 | 3673250
142 | 35.1 | SOTC127 | 1.50 TR with , 18000 BTU/Hr High Wall mount Split Air Conditioners | Nos | 150000 | 6 | 900000 |  | 0 | 6 | 900000 | 6 | 900000 | 52500 | 315000
143 |  |  | AE |  | 150000 | [6 empty] | 1 | 150000 | 52500 | 52500
144 | 35.2 | SOTC128 | 2.0 TR with , 24000 BTU/Hr High Wall mount Split Air Conditioners | Nos | 210000 | 2 | 420000 |  | 0 | 2 | 420000 | 2 | 420000 | 73500 | 147000
145 |  |  | AE |  | 210000 | [6 empty] | 4 | 840000 | 73500 | 294000
146 | 35.3 | SOTC129 | Voltage stabilizer for 4 KVA maximum load | Nos | 7000 | 6 | 42000 |  | 0 | 6 | 42000 | 6 | 42000 | 2450 | 14700
147 |  |  | AE |  | 7000 | [6 empty] | 1 | 7000 | 2450 | 2450
148 | 35.4 | SOTC130 | Voltage stabilizer for 5 KVA maximum load | Nos | 8500 | 2 | 17000 |  | 0 | 2 | 17000 | 2 | 17000 | 2975 | 5950
149 |  |  | AE |  | 8500 | [6 empty] | 4 | 34000 | 2975 | 11900
150 | 35.5 | SOTC131 | Ductable Air Conditioners 11.0 TR with ISEER ≥ 4 | Nos | 1200000 | 1 | 1200000 |  | 0 | 1 | 1200000 | 1 | 1200000 | 420000 | 420000
151 | 35.6 | SOTC132 | Ductable Air Conditioners 8.5 TR with ISEER ≥ 4 | Nos | 1000000 | 2 | 2000000 |  | 0 | 2 | 2000000 | 2 | 2000000 | 350000 | 700000 | AE
152 |  |  | AE |  | 1000000 | [6 empty] | 2 | 2000000 | 350000 | 700000
153 | 35.7 | SOTC133 | Ductable Air Conditioners 5.5 TR with ISEER ≥ 4 | Nos | 900000 | 1 | 900000 |  | 0 | 1 | 900000 | 1 | 900000 | 315000 | 315000 | AE
154 |  |  | AE |  | 900000 | [6 empty] | 2 | 1800000 | 315000 | 630000
155 | 36.2 | SOTC134 | Automatic Smoke Detection System | Job | 1425000 | 1 | 1425000 |  | 0 | 1 | 1425000 | 1 | 1425000 | 498750 | 498750 | AE
156 | 36.3 | SOTC135 | Automatic Fire Alarm System | Job | 1400000 | 1 | 1400000 |  | 0 | 1 | 1400000 | 1 | 1400000 | 490000 | 490000
157 | 36.4 | SOTC136 | Supply & Fixing of 4.5Kg, CO2 Type Fire Extinguisher. | Nos | 27000 | 6 | 162000 |  | 0 | 6 | 162000 | 6 | 162000 | 9450 | 56700
158 | 36.5 | SOTC137 | Supply and fixing of ABC stored pressure squeeze grip type fire extinguishers, 9 kg capacity. | Nos | 16000 | 6 | 96000 |  | 0 | 6 | 96000 | 6 | 96000 | 5600 | 33600
159 | 36.6 | SOTC138 | Supply and fixing of ABC Powder MAP 4 Kg Fire extinguisher | Nos | 11000 | 10 | 110000 |  | 0 | 10 | 110000 | 10 | 110000 | 3850 | 38500
160 | 36.7 | SOTC139 | Supply and fixing of 2 Kg Fire extinguisher Clean Agent | Nos | 22500 | 10 | 225000 |  | 0 | 10 | 225000 | 10 | 225000 | 7875 | 78750
161 | 36.8 | SOTC140 | Supply and fixing of Escape signage boards in Rigid Photo luminescent based glow | Nos | 2000 | 150 | 300000 |  | 0 | 150 | 300000 | 150 | 300000 | 700 | 105000 | AE
162 | 36.9 | SOTC141 | Supply & Fixing of Powder Coated Fire Rated doors. | Sqm | 29000 | 6 | 174000 |  | 0 | 6 | 174000 | 6 | 174000 | 10150 | 60900
163 |  |  | AE |  | 29000 | [6 empty] | 7.8 | 226200 | 10150 | 79170
164 | 37 | SOTC142 | Telephone & EPABX System | Job | 1000000 | 1 | 1000000 |  | 0 | 1 | 1000000 | 1 | 1000000 | 350000 | 350000
165 | 38 | SOTC143 | Local Area Network (LAN) System | Job | 1250000 | 1 | 1250000 |  | 0 | 1 | 1250000 | 1 | 1250000 | 437500 | 437500
166 | 39 | SOTC144 | Biometric Access Control System | Nos | 300000 | 2 | 600000 |  | 0 | 2 | 600000 | 2 | 600000 | 105000 | 210000
167 |  |  | AE |  | 300000 | [6 empty] | 1 | 300000 | 105000 | 105000
168 |  | SOTC145 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Reinforced cement concrete) | Cum | 5400 | 10 | 54000 |  | 0 | 10 | 54000 | 10 | 54000 | 1890 | 18900
169 |  | SOTC146 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Unreinforced cement concrete) | Cum | 4500 | 1.5 | 6750 |  | 0 | 1.5 | 6750 | 1.5 | 6750 | 1575 | 2363
170 |  |  | AE |  | 4500 | [6 empty] | 50.4015 | 226807 | 1575 | 79382 | AE
171 |  | SOTC147 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Brick Masonary) | Cum | 900 | 118 | 106200 |  | 0 | 118 | 106200 | 118 | 106200 | 315 | 37170
172 |  |  | AE |  | 900 | [6 empty] | 34.691 | 31222 | 315 | 10928
173 |  | SOTC148 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Kadapa slabs or shahabad stone slabs on sand bed) | Sqm | 630 | 25 | 15750 |  | 0 | 25 | 15750 | 25 | 15750 | 220.5 | 5513
174 |  |  | AE |  | 630 | [6 empty] | 667.9265 | 420794 | 220.5 | 147278
175 |  | SOTC149 | Dismantling doors, windows and clear storey windows, Ventilators etc., (wood or steel) shutters including Chowkhats, architraves,hold fasts and other attachments etc., and stacking them within 100m lead including charge etc., complete for finished item of work. (Not exceeding 3 sqm in area) | Nos | 1800 | 57 | 102600 |  | 0 | 57 | 102600 | 57 | 102600 | 630 | 35910 | AE
176 |  |  | AE |  | 1800 | [6 empty] | 146 | 262800 | 630 | 91980
177 |  | SOTC150 | Conveyance of un-useful excavated earth to a distance of 16 KM for disposal including hire charges of T and P, labour charges etc., complete for finished item of work. | Cum | 900 | 250 | 225000 |  | 0 | 250 | 225000 | 250 | 225000 | 315 | 78750
178 |  |  | AE |  | 900 | [6 empty] | 64.769 | 58292 | 315 | 20402
179 | 40 | SOTC151 | RCC M 25 grade design mix (For lintels) | Cum | 18900 | 3 | 56700 |  | 0 | 3 | 56700 | 3 | 56700 | 6615 | 19845 | AE
180 |  |  | AE |  | 18900 | [6 empty] | 0.17 | 3213 | 6615 | 1125
181 | 41 | SOTC152 | RCC M 20 grade design mix (50mm thick platforms) | Sqm | 1170 | 12 | 14040 |  | 0 | 12 | 14040 | 0 | 0 | 0 | 0
182 | 41 | SOTC153 | RCC M 20 grade design mix (25 mm thick Shelves) | Sqm | 900 | 12 | 10800 |  | 0 | 12 | 10800 | 0 | 0 | 0 | 0 | AE
183 | 42 | SOTC154 | Brick Masonry work in CM (1:6) prop in superstructure | Cum | 15300 | 3 | 45900 |  | 0 | 3 | 45900 | 3 | 45900 | 5355 | 16065
184 |  |  | AE |  | 15300 | [6 empty] | 108.951 | 1666950 | 5355 | 583433 | AE
185 | 43 | SOTC155 | Reinforced Masonry for partition walls (100 mm thick) in CM (1:4) | Sqm | 2700 | 500 | 1350000 |  | 0 | 500 | 1350000 | 404.9325 | 1093318 | 945 | 382661
186 | 44 | SOTC156 | PCC (1:3:6) nominal mix using 20mm size graded m/c (For bed blocks and hold fasts) (OTs screed) | Cum | 9000 | 1.5 | 13500 |  | 0 | 1.5 | 13500 | 0 | 0 | 0 | 0
187 | 45 | SOTC157 | Filling with light weight concrete in Cement Concrete (1:5:10) proportion using brick jelly for low roofs | Cum | 7200 | 23 | 165600 |  | 0 | 23 | 165600 | 16.8651 | 121429 | 2520 | 42500
188 | 46 | SOTC158 | Thermo Mechanically Treated (Fe -500/500D/550D) for RCC works | MT | 126000 | 1.25 | 157500 |  | 0 | 1.25 | 157500 | 0.7686 | 96844 | 44100 | 33895
189 | 49 | SOTC159 | Plastering 12mm thick in two coats with base coat of 8mm thick in CM (1:6) and top coat of 4mm thick in CM (1:4). for Internal walls. | Sqm | 1224 | 1600 | 1958400 |  | 0 | 1600 | 1958400 | 1600 | 1958400 | 428.4 | 685440
190 |  |  | AE |  | 1224 | [6 empty] | 548.804 | 671736 | 428.4 | 235108
191 | 51 | SOTC160 | Impervious coat to exposed RCC roof slab surfaces (APSS No. 901 and 903) For Toilets | Sqm | 360 | 77.78 | 28000.8 |  | 0 | 77.78 | 28000.8 | 43.05 | 15498 | 126 | 5424
192 | 92 | SOTC161 | Providing and applying Wall putty of White Cement or Polymer or Cement based of average 1 to 2 mm thickness over plastered surface to prepare the surface even and smooth after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, applying emery paper, Sand the surface, clean & wipe off loose dust, applying knifing paste filler by putty knife / muslin pad, air dry for 2 - 3 | Sqm | 270 | 4447 | 1200690 |  | 0 | 4447 | 1200690 | 1811.5335 | 489114 | 94.5 | 171190
193 | 53 | SOTC162 | Flooring with non-skid full body ceramic floor tiles | Sqm | 1710 | 85 | 145350 |  | 0 | 85 | 145350 | 85 | 145350 | 598.5 | 50873
194 |  |  | AE |  | 1710 | [6 empty] | 13.0805 | 22368 | 598.5 | 7829
195 | 55 | SOTC163 | Dadooing to walls with glazed full body Porcelain wall tiles | Sqm | 1440 | 225 | 324000 |  | 0 | 225 | 324000 | 225 | 324000 | 504 | 113400
196 |  |  | AE |  | 1440 | [6 empty] | 115 | 165600 | 504 | 57960
197 | 56 | SOTC164 | Dadooing to walls with glazed full body Ceramic tiles | Sqm | 1440 | 350 | 504000 |  | 0 | 350 | 504000 | 270.2175 | 389113 | 504 | 136190
198 | 57 | SOTC165 | Painting one coat water based cement primer of interior grade I and two coats of acrylic emulsion paint for ceiling and Walls | Sqm | 360 | 4447 | 1600920 |  | 0 | 4447 | 1600920 | 1372.014 | 493925 | 126 | 172874
199 | 59 | SOTC166 | Painting to new wood work | Sqm | 360 | 313 | 112680 |  | 0 | 313 | 112680 | 75 | 27000 | 126 | 9450
| 60 | SOTC167 | Painting to new iron work | Sqm | 270 | 88 | 23760 |  | 0 | 88 | 23760 | 88 | 23760 | 94.5 | 8316
201 |  |  | AE |  | 270 | [6 empty] | 38.42 | 10373 | 94.5 | 3631 | AE
202 | 61 | SOTC168 | Two shutter cupboards | Sqm | 9000 | 100 | 900000 |  | 0 | 100 | 900000 | 0 | 0 | 0 | 0
203 | 64 | SOTC169 | UPVC Fixed Louvered Ventilator | Sqm | 12000 | 7 | 84000 |  | 0 | 7 | 84000 | 7 | 84000 | 4200 | 29400
204 |  |  | AE |  | 12000 | [6 empty] | 9.5165 | 114198 | 4200 | 39969
205 |  | SOTC170 | UPVC 3 track Sliding Windows | Sqm | 9000 | 15 | 135000 |  | 0 | 15 | 135000 | 15 | 135000 | 3150 | 47250
206 |  |  | AE |  | 9000 | [6 empty] | 30.276 | 272484 | 3150 | 95369 | AE
207 |  | SOTC171 | MS Grills to Windows | Sqm | 1800 | 150 | 270000 |  | 0 | 150 | 270000 | 126.42 | 227556 | 630 | 79645
208 | 66 | SOTC172 | Flooring with 16 to 18 mm thick high polished granite stone slabs black colour for platforms (S.S.701 and special) | Sqm | 6300 | 50 | 315000 |  | 0 | 50 | 315000 | 50 | 315000 | 2205 | 110250
209 | 67 | SOTC173 | Doors as per approved drawings with medium teak wood frame (1500mm x 2600mm) | Sqm | 6300 | 50 | 315000 |  | 0 | 50 | 315000 | 15.4 | 97020 | 2205 | 33957
210 | 68 | SOTC174 | Doors as per approved drawings with medium teak wood frame (1000mm x 2100mm) | Sqm | 7400 | 45 | 333000 |  | 0 | 45 | 333000 | 17.2 | 127280 | 2590 | 44548
211 | 69 | SOTC175 | Doors Shutters WPC(800mm x 2100mm) | Sqm | 5400 | 40 | 216000 |  | 0 | 40 | 216000 | 33.3795 | 180249 | 1890 | 63087 | AE
212 | 70 | SOTC176 | Scientific Doors with metal door frames and door shutters made of galvanize steel | Sqm | 18000 | 45 | 810000 |  | 0 | 45 | 810000 | 45 | 810000 | 6300 | 283500
213 |  |  | AE |  | 18000 | [6 empty] | 24.3 | 437400 | 6300 | 153090 | AE
214 | 71 | SOTC177 | False ceiling as per Technical specification | Sqm | 1800 | 1400 | 2520000 |  | 0 | 1400 | 2520000 | 750 | 1350000 | 630 | 472500
215 | 72 | SOTC178 | Vinyl flooring | Sqm | 3000 | 500 | 1500000 |  | 0 | 500 | 1500000 | 500 | 1500000 | 1050 | 525000 | AE
216 |  |  | AE |  | 3000 | [6 empty] | 164 | 492000 | 1050 | 172200
217 | 74 | SOTC179 | Impervious coat to exposed RCC roof slab surfacesof 20mm thick (APSS No. 901 and 903) | Sqm | 1260 | 350 | 441000 |  | 0 | 350 | 441000 | 0 | 0 | 0 | 0 | AE
218 | 63 | SOTC180 | Fixed Glass Window – 1200 x 1200 | Sqm | 5400 | 53.55 | 289170 |  | 0 | 53.55 | 289170 | 53.55 | 289170 | 1890 | 101210
219 |  |  | AE |  | 5400 | [6 empty] | 7.46 | 40284 | 1890 | 14099 | AE
220 | 95 | SOTC181 | Grouting the holes with neat cement slurry of 20mm dia with all required accessories of all materials etc., including cost & Conveyance of all labour Charges etc., complete finished item of work (*As per SSR2021-22 of S.NO:-8) | Nos | 180 | 500 | 90000 |  | 0 | 500 | 90000 | 0 | 0 | 0 | 0
221 | 96 | SOTC182 | Pressure grouting the drilled holes with neat cement slurry or with approved grout admixture using pump - excluding cost of drilling holes after fixing nozzles as technical specification approved by the department etc., including cost & Conveyance of all labour charges etc., complete finished item of work | Nos | 630 | 500 | 315000 |  | 0 | 500 | 315000 | 500 | 315000 | 220.5 | 110250
222 |  | SOTC182 | AE |  | 630 | [6 empty] | 632 | 398160 | 220.5 | 139356 | AE
223 | 87 A | SOTC183 | Supply and fabricating,erecting and fixing inposition trusses of approved design with structural steel other than MS. | Kgs | 180 | 6500 | 1170000 |  | 0 | 6500 | 1170000 | 6500 | 1170000 | 63 | 409500
224 | 87 B | SOTC184 | Supply and fixing of pre painted Galvalume Trapezoidal Profile Roofing with 0.50mm Thickness. | Sqm | 1080 | 65 | 70200 |  | 0 | 65 | 70200 | 65 | 70200 | 378 | 24570 | AE
225 | 75 | SOTC185 | 4" (101.6mm) multi floor trap with jali - UPVC/SWR | Nos | 270 | 25 | 6750 |  | 0 | 25 | 6750 | 25 | 6750 | 94.5 | 2363
226 |  |  | AE |  | 270 | [6 empty] | 19 | 5130 | 94.5 | 1796 | AE
227 | 76 | SOTC186 | 580mm x 440mm long Orissa pan white glazed Water Closet | Nos | 5400 | 4 | 21600 |  | 0 | 4 | 21600 | 4 | 21600 | 1890 | 7560
228 | 77 | SOTC187 | European Water Closet of 1st quality | Nos | 6300 | 9 | 56700 |  | 0 | 9 | 56700 | 9 | 56700 | 2205 | 19845
229 | 78 | SOTC188 | Indian make Flat Back Wash Hand Basin 1st quality | Nos | 3600 | 16 | 57600 |  | 0 | 16 | 57600 | 15 | 54000 | 1260 | 18900
230 | 79 | SOTC189 | CP finish brass soap dish | Nos | 1100 | 21 | 23100 |  | 0 | 21 | 23100 | 21 | 23100 | 385 | 8085
231 | 80 | SOTC190 | TV shape mirror with plastic frame of size 609.6mm x 457.2mm | Nos | 630 | 25 | 15750 |  | 0 | 25 | 15750 | 15 | 9450 | 220.5 | 3308
232 | 81 | SOTC191 | 25.4mm dia , 609.6mm long aluminium anodized towel rods | Nos | 540 | 36 | 19440 |  | 0 | 36 | 19440 | 21 | 11340 | 189 | 3969
233 | 82 | SOTC192 | 15 mm brass body CP finish bib tap of not less than 300 grams weight | Nos | 540 | 25 | 13500 |  | 0 | 25 | 13500 | 14 | 7560 | 189 | 2646
234 | 87 C | SOTC193 | Self Closing Tap - Push Type | Nos | 720 | 25 | 18000 |  | 0 | 25 | 18000 | 15 | 10800 | 252 | 3780
235 | 84 | SOTC194 | Chromium plated finish brass body quarter turn Bibcock cum Health Faucet | Nos | 3600 | 12 | 43200 |  | 0 | 12 | 43200 | 9 | 32400 | 1260 | 11340
236 | 85 | SOTC195 | Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings - 15.90mm OD pipe | Rmt | 270 | 55 | 14850 |  | 0 | 55 | 14850 | 55 | 14850 | 94.5 | 5198
237 |  |  | AE |  | 270 | [6 empty] | 53.234 | 14373 | 94.5 | 5031 | AE
238 | 85 | SOTC196 | Ashirvad/Ajay/Astral Flowguard or equivalent CPVC Pipes and Fittings - 22.20mm OD pipe | Rmt | 360 | 115 | 41400 |  | 0 | 115 | 41400 | 115 | 41400 | 126 | 14490
239 |  |  | AE |  | 360 | [6 empty] | 14.7065 | 5294 | 126 | 1853 | AE
240 | 85 | SOTC197 | Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings -28.60mm OD pipe | Rmt | 450 | 143 | 64350 |  | 0 | 143 | 64350 | 115.5 | 51975 | 157.5 | 18191
241 | 86 | SOTC198 | Bronze Gate/ Globe valve - 25mm Nominal bore | Nos | 1440 | 15 | 21600 |  | 0 | 15 | 21600 | 15 | 21600 | 504 | 7560
242 |  |  | AE |  | 1440 | [6 empty] | 5 | 7200 | 504 | 2520 | AE
243 | 87 | SOTC199 | SWR PVC pipes (Prince/ Sudhakar/ Kisan/ Supreme or any ISI brand) 4 Kg/Sq.cm. - 75mmdia | Rmt | 450 | 145 | 65250 |  | 0 | 145 | 65250 | 84 | 37800 | 157.5 | 13230
244 | 87 | SOTC200 | SWR PVC pipes (Prince/ Sudhakar/ Kisan/ Supreme or any ISI brand) 4 Kg/Sq.cm. -110mmdia | Rmt | 540 | 145 | 78300 |  | 0 | 145 | 78300 | 68.25 | 36855 | 189 | 12899
245 | 90 | SOTC201 | Supplying and fixing15 mm nominal size 152.0 mm CP finish iron body shower rose 1st quality including cost and conveyance of all materials, labour charges , overheads & contractors profit for finished item of work in all floors. | Nos | 630 | 5 | 3150 |  | 0 | 5 | 3150 | 5 | 3150 | 220.5 | 1103
246 |  |  | AE |  | 630 | [6 empty] | 1 | 630 | 220.5 | 221 | AE
247 | 87 D | SOTC202 | Supply and Fixing of white glazed flat back bowl urinals | Nos | 2700 | 4 | 10800 |  | 0 | 4 | 10800 | 0 | 0 | 945 | 0
248 | 87 E | SOTC203 | Supply and fixing of 16mm to 20 mm thick ploished marbles slab partitions of size 4'0"*2'0" | Nos | 3600 | 10 | 36000 |  | 0 | 10 | 36000 | 0 | 0 | 1260 | 0
249 | 88.1 | SOTC204 | 28 mm dia. and 0.90 mm thick Copper Pipe Lines for Main lines | Rmt | 1750 | 700 | 1225000 |  | 0 | 700 | 1225000 | 700 | 1225000 | 612.5 | 428750
250 |  |  | AE |  | 1750 | [6 empty] | 133 | 232750 | 612.5 | 81463
251 | 88.1 | SOTC205 | 42 mm dia. and 1.20 mm thick Copper Pipe Lines for Main lines | Rmt | 2250 | 200 | 450000 |  | 0 | 200 | 450000 | 200 | 450000 | 787.5 | 157500 | AE
252 |  |  | AE |  | 2250 | [6 empty] | 27 | 60750 | 787.5 | 21263
253 | 88.1 | SOTC206 | 54 mm dia. and 1.20 mm thick Copper Pipe Lines for Main lines | Rmt | 2950 | 550 | 1622500 |  | 0 | 550 | 1622500 | 550 | 1622500 | 1032.5 | 567875 | AE
254 |  |  | AE |  | 2950 | [6 empty] | 14 | 41300 | 1032.5 | 14455
255 | 88.1 | SOTC207 | 12 mm dia. and 0.70 mm thick Copper Pipe Lines for distribution lines | Rmt | 650 | 320 | 208000 |  | 0 | 320 | 208000 | 320 | 208000 | 227.5 | 72800 | AE
256 |  |  | AE |  | 650 | [6 empty] | 224 | 145600 | 227.5 | 50960
257 | 88.1 | SOTC208 | 15 mm dia. and 0.90 mm thick Copper Pipe Lines for distribution lines | Rmt | 950 | 525 | 498750 |  | 0 | 525 | 498750 | 525 | 498750 | 332.5 | 174563 | AE
258 |  |  | AE |  | 950 | [6 empty] | 232 | 220400 | 332.5 | 77140
259 | 88.1 | SOTC209 | 22 mm dia. and 0.90 mm thick Copper Pipe Lines for distribution lines | Rmt | 1450 | 530 | 768500 |  | 0 | 530 | 768500 | 530 | 768500 | 507.5 | 268975 | AE
260 |  |  | AE |  | 1450 | [6 empty] | 65 | 94250 | 507.5 | 32988
261 | 88.2 | SOTC210 | 15 mm (1/2") Isolation Valves | Nos | 1500 | 40 | 60000 |  | 0 | 40 | 60000 | 31 | 46500 | 525 | 16275 | AE
262 | 88.2 | SOTC211 | 22 mm (3/4") Isolation Valves | Nos | 2500 | 15 | 37500 |  | 0 | 15 | 37500 | 14 | 35000 | 875 | 12250
263 | 88.2 | SOTC212 | 28 mm Isolation Valves | Nos | 3500 | 3 | 10500 | 2 | 7000 | 5 | 17500 | 5 | 17500 | 1225 | 6125
264 |  |  | AE |  | 3500 | [6 empty] | 4 | 14000 | 1225 | 4900
265 | 88.2 | SOTC213 | 42 mm Isolation Valves | Nos | 4500 | 2 | 9000 | 3 | 13500 | 5 | 22500 | 4 | 18000 | 1575 | 6300 | AE
266 | 88.2 | SOTC214 | 54 mm Isolation Valves | Nos | 5500 | 2 | 11000 | 1 | 5500 | 3 | 16500 | 3 | 16500 | 1925 | 5775
267 |  |  | AE |  | 5500 | [6 empty] | 7 | 38500 | 1925 | 13475
268 | 88.3 | SOTC215 | Gas Outlet Points with probes for Oxygen with S Brackets | Nos | 2850 | 189 | 538650 |  | 0 | 189 | 538650 | 189 | 538650 | 997.5 | 188528 | AE
269 |  |  | AE |  | 2850 | [6 empty] | 17 | 48450 | 997.5 | 16958
270 | 88.4 | SOTC216 | 2 Gas Digital Area Alarm Panels | Nos | 25000 | 2 | 50000 |  | 0 | 2 | 50000 | 0 | 0 | 8750 | 0 | AE
271 | 88.4 | SOTC217 | 3 Gas Digital Area Alarm Panels | Nos | 30000 | 4 | 120000 |  | 0 | 4 | 120000 | 4 | 120000 | 10500 | 42000
272 |  |  | AE |  | 30000 | [6 empty] | 1 | 30000 | 10500 | 10500
273 | 88.4 | SOTC218 | 5 Gas Digital Area Alarm Panels | Nos | 40000 | 5 | 200000 | 1 | 40000 | 6 | 240000 | 0 | 0 | 14000 | 0 | AE
274 | 88.4 | SOTC219 | Master Digital Alarm Panels | Nos | 50000 | 1 | 50000 |  | 0 | 1 | 50000 | 1 | 50000 | 17500 | 17500
275 | 88.5 | SOTC220 | BPC Flow meter with Humidifier bottle and L adapter | Nos | 2250 | 27 | 60750 |  | 0 | 27 | 60750 | 27 | 60750 | 787.5 | 21263
276 |  |  | AE |  | 2250 | [6 empty] | 16 | 36000 | 787.5 | 12600
277 | 88.5 | SOTC221 | L Type Adapter for Oxygen Flow meters | Nos | 1250 | 27 | 33750 |  | 0 | 27 | 33750 | 27 | 33750 | 437.5 | 11813 | AE
278 | 88.5 | SOTC222 | Kit for conversion of Oxygen | Nos | 1650 | 27 | 44550 |  | 0 | 27 | 44550 | 18 | 29700 | 577.5 | 10395
279 | 88.5 | SOTC223 | Suction Jars of 600 ml capacity | Nos | 3450 | 27 | 93150 |  | 0 | 27 | 93150 | 27 | 93150 | 1207.5 | 32603
280 |  |  | AE |  | 3450 | [6 empty] | 19 | 65550 | 1207.5 | 22943
281 | 88.5 | SOTC224 | Adapters for Vacuum | Nos | 750 | 27 | 20250 |  | 0 | 27 | 20250 | 27 | 20250 | 262.5 | 7088 | AE
282 | 88.5 | SOTC225 | Adapters for Air | Nos | 750 | 27 | 20250 |  | 0 | 27 | 20250 | 27 | 20250 | 262.5 | 7088
283 | 88.5 | SOTC226 | Adapters for Nitrous Oxide | Nos | 750 | 15 | 11250 |  | 0 | 15 | 11250 | 15 | 11250 | 262.5 | 3938
284 | 88.5 | SOTC227 | Vacuum Tube | Nos | 550 | 27 | 14850 | 58 | 31900 | 85 | 46750 | 85 | 46750 | 192.5 | 16363
285 |  |  | AE |  | 550 | [6 empty] | 30 | 16500 | 192.5 | 5775
286 | 88.6 | SOTC228 | Bed Head wall panel horizontal 1500 mm long single railing | Nos | 35000 | 27 | 945000 |  | 0 | 27 | 945000 | 27 | 945000 | 12250 | 330750 | AE
287 |  |  | AE |  | 35000 | [6 empty] | 4 | 140000 | 12250 | 49000
288 | 88.7 b | SOTC229 | Valve box -2 services | Nos | 9500 | 1 | 9500 |  | 0 | 1 | 9500 | 0 | 0 | 3325 | 0 | AE
289 | 88.7 b | SOTC230 | Valve box -3 services | Nos | 14500 | 3 | 43500 |  | 0 | 3 | 43500 | 3 | 43500 | 5075 | 15225
290 |  |  | AE |  | 14500 | [6 empty] | 2 | 29000 | 5075 | 10150
291 | 88.7 b | SOTC231 | Valve box -6 services | Nos | 22500 | 1 | 22500 | 5 | 112500 | 6 | 135000 | 6 | 135000 | 7875 | 47250 | AE
292 | 88.8 a | SOTC232 | 4 + 4 size of CO2 manifold System | Job | 40000 | 1 | 40000 | 1 | 40000 | 2 | 80000 | 2 | 80000 | 14000 | 28000
293 |  |  | AE |  | 40000 | [6 empty] | 1 | 40000 | 14000 | 14000
294 | 88.8 b | SOTC233 | 2 cylinder emergency manifold CO2 | Job | 14500 | 1 | 14500 | 1 | 14500 | 2 | 29000 | 2 | 29000 | 5075 | 10150 | AE
295 | 88.8 c | SOTC234 | Fully Automatic CO2 Control System | Job | 185000 | 1 | 185000 | 1 | 185000 | 2 | 370000 | 2 | 370000 | 64750 | 129500
296 | 88.9 | SOTC235 | Aneste Iwata Make TFS 150 C9 Model, Compresso Two stage, Motor 15 HP & 57.18 CFM, 60 CFM Air Dryer with 2000 Ltrs Receiver Twin System (For Air4, Air7) | Job | 1895000 | 1 | 1895000 |  | 0 | 1 | 1895000 | 1 | 1895000 | 663250 | 663250
297 | 88.1 | SOTC236 | Supporting structure for MGPS lines with Ismb Columns, beams, MS angles, Flats and square rods | Job | 795000 | 1 | 795000 |  | 0 | 1 | 795000 | 1 | 795000 | 278250 | 278250
298 | 88.11 | SOTC237 | 2x20 Oxygen Main manifold System | Job | 95000 | 1 | 95000 |  | 0 | 1 | 95000 | 1 | 95000 | 33250 | 33250
299 | 88.12 | SOTC238 | Electrical Control Panel for MGPS | Job | 145000 | 1 | 145000 |  | 0 | 1 | 145000 | 1 | 145000 | 50750 | 50750
300 | 88.13 | SOTC239 | Vaccum system Ingersoll Rand Make Model 15V x 10 Model with 5 HP Motor with 1000 Liters Reciever, Filters, Electricals, Etc Secretion Trap and Bacteria Filter | Job | 1495000 | 2 | 2990000 |  | 0 | 2 | 2990000 | 2 | 2990000 | 523250 | 1046500
301 |  | SOTC240 | Validation By Third Party Agency Charges per Each MOT | Each | 100000 | 4 | 400000 |  | 0 | 4 | 400000 | 4 | 400000 | 35000 | 140000
302 |  |  | AE |  | 100000 | [6 empty] | 5 | 500000 | 35000 | 175000
303 |  | SOTC241 | Anesthetic Gas Scavenging System (AGSS) | Job | 1213000 | 1 | 1213000 |  | 0 | 1 | 1213000 | 1 | 1213000 | 424550 | 424550 | AE
304 |  | SOTC242 | Double Arm Surgical Pendant | Nos | 1195000 | 0 | 0 | 6 | 7170000 | 6 | 7170000 | 6 | 7170000 | 418250 | 2509500
305 |  | SOTC243 | Electrical connections for 2 UPS | Job | 100000 |  |  | 1 | 100000 | 1 | 100000 | 0 |  |  | 0
[5 empty] | TOTAL |  | 175773220.8 |  | 39541980 |  | 215315200.8 |  | 222626238 |  | 76711699 | SI
Sd/- (16.03.2024)
CHIEF ENGINEER
//T.C.B.F.O//
EXECUTIVE ENGINEER
Spl. Projects, TSMSIDC
SI
SUPPLEMENTAL ITEMS | [15 empty] | SI
306 |  |  | Supply and installation of Under-deck Thermocol insulation sheets of 40 mm thick having more than 30 Kg/m3 density to ceiling by brush application of bituminous adhesive to the sheets and secured with screw along with washer at the centre of the sheet supported with GI wire running diagonally to the sheet of 2mm dia. (in ICUs & MOTs Integration Room) | Sqm | 1014 | [6 empty] | 262.74 | 266418 | 0 | 0 | SI
307 |  |  | Supply and placing of the Design Mix Plain Cement Concrete of M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Concrete Batching Plant with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials. (in 6 OTs) | Cum | 11740 | [6 empty] | 28.01 | 328837.4 | 0 | 0 | SI
308 |  |  | Supply and Laying of Floor leveller compund (self smoothing mortar) to level the surface, having bulk density not less than 2 Kg/l for a fresh mortor, compressive strength not less than 20 N/mm2, initial setting time not more than 40 minutes and offer a 25 minutes working time, The surface should be walkabe after 30 min of laying. (all rooms & corridors except OTs, TIRs and Sterile corridor) | Sqm | 1460 | [6 empty] | 882.44 | 1288362.4 | 0 | 0 | SI
309 |  |  | Providing dadooing to walls with glazed full body ceramic wall tiles of size 800 x 1600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. (at Entrance) | Sqm | 4665 | [6 empty] | 119.385 | 556931.025 | 0 | 0 | SI
310 |  |  | Providing (1500 X 2100) single sliding door operated by elbow switches / foot switch as well as touchless sensor of 10mm thick toughened glass (Saint Gobin / Modi Guard) fixed in SS 304 grade 2 Track top channel of 45 mm (one track to hold fixed glass partition in position and second track with top rollers suitably angled to reduce resistance to movement to facilitate smooth sliding movement of the door). Single track bottom channel to be provided for fixed glass partition. Floor guide to be provided for smooth sliding of the door. Concealed door handle of (150 mm) to be provided in cutout on the sliding door for manual operation when required. All fittings provided should be of Titon /Ozone / Enox make in SS 304 - In TIRs | Nos | 270276 | [6 empty] | 2 | 540552 | 94600 | 189200 | SI
311 |  |  | V-Board Partitions on top of false ceiling for partitioning of sterile corridor and non-sterile corridor (for dividing corridors into zones above ceiling) | Sqm | 3640 | [6 empty] | 16 | 58240 | 1274.0625 | 20385 | SI
312 |  |  | GI Powder Coated Sliding Doors (0.8mm shutter sheet thk & 1.2mm frame sheet thk with Single Rebate and Honeycomb Infill) Double Leaf Door 1200 x 2100mm with Accessories (Sliding Track for Double Door, Sliding Dead Lock Enox, Concealed Handles 100mm Ahlada, Flush Bolt 300mm Ahlada, SS304 Kick Plate upto 350mm ht, DG Clear Float Glass 350x750x6mm with Adhesive Tape & Silicon Sealant) (for change rooms to corridor entrance) | Nos | 84133 | [6 empty] | 1 | 84133 | 29450 | 29450 | SI
313 |  |  | Supply and installation of 50mm thick double skin modular wall Panels made of 0.8 mm thick powder coated GI on both the sides, with 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, flush on both sides with maximum allowable gap of 3- 4mm filled with food grade silicon sealant and placed on cold rolled galvanised bottom tracks with a recess to provide floor to wall coving flush with the wall panel. This includes all required harware for completion Panels to be covered with a protective film to avoid any damages during transportation and installation | Sqm | 7450 | [6 empty] | 297.52 | 2216524 | 756.252 | 225000 | SI
314 |  |  | Supply and installation of 50mm thick double skin ceiling system made of 0.8 mm thick Powder Coated GI sheets on both sides, 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, panels flush towards room side with maximum allowable gap of 3-4mm at panel to panel joints filled with silicon sealant. Ceiling panels are suspended from the RCC slab by using concealed AL ceiling grid with tie rod and adjustable turn buckle arrangement etc. This includes all required hardware for completion. Panels to be covered with a protective film to avoid any damages during transportation and installation | Sqm | 7450 | [6 empty] | 163.08 | 1214946 | 1073.0929 | 175000 | SI
315 |  |  | Acoustic Wall Panelling with framework consisting of 25mm high GI wall channels with fully knurled surface of 0.55mm thick bottom wedge of 80mm width, having two equal flanges of 26mm is anchored to GI studs of 50mm high. GI studs of 50mm High to be fixed to wall at 600mm centres, 25mm thick channels are then fixed perpendicular to the GI studs and suitable fixing channel is fixed to the cross channel to fix the panel to achieve overall air gap of 75mm from the wall and GI Clips for inside panel and Clips for border panel of 18mm to be fixed to the GI wall channel to achieve required shape. Secured arranging of polyester wool of – thickness/density, Prelam Board to be installed. 15mm thick Prelam perforated Wooden slat of required dia perforation & pitch is to be customised and then fixed to GI frame rigidly by using fixing channel fastened perpendicular to the cross channel with GI brackets. The boards shall be fixed to the GI frame with special cleats. (MOTs Integration Room) | Sqm | 6350 | [6 empty] | 110 | 698500 | 1363.636 | 150000 | SI
316 |  |  | Accooustic Ceiling Paneling with Perforated board Fine line Grid false ceiling using 11mm thick Perforated Board sheet tiles of size 595mm x 595mm fixing to steel precoated GI wall angle of size 25mm x 25mm x 0.70mm thick along the perimeter of ceiling screw fixed to brick work / partition at 610mm center to center and suspending the frame work using precoated GI Tee section (24mm x 38mm x 0.7mm) from soffit at 1220mm center to center fixed with GI Soffit Cleat, rawl plugs and steel expansion fasteners & connecting clip to the GI Tee section with 4mm dia GI rod with galvanised spring steel level clip of PVC unversal holding clips system at 1200mm center to center and Secured arranging of polyester wool of 50mm thick 1000 GSM, Prelam Board to be installed. 15mm thick Prelam perforated Wooden slat of required dia perforation & pitch is to be customised and then fixed to GI frame rigidly by using fixing channel fastened perpendicular to the cross channel with GI brackets. The boards shall be fixed to the GI frame with special cleats. (MOTs Integration Room) | Sqm | 5700 | [6 empty] | 62 | 353400 | 1223.79 | 75875 | SI
317 |  |  | Wooden Flooring with Engineered wood planks of 14mm thick (MOTs Integration Room) | Sqm | 7300 | [6 empty] | 65 | 474500 | 1230.7692 | 80000 | SI
318 |  |  | Skirting for Wooden Flooring with Engineered wood planks of 14mm thick (MOTs Integration Room) | Rmt | 900 | [6 empty] | 40 | 36000 | 315 | 12600 | SI
319 |  |  | 80% blockout Ruler Blinds for MOTs Integration Room Windows | Nos | 12000 | [6 empty] | 3 | 36000 | 4200 | 12600 | SI
320 |  |  | Supply and installation of double pass RO system having 2 nos feed pumps of 1.5 HP with max flow of 4000 ltr/hr including construction of sand filter of dimensions (H=1650 mm, D=325 mm) with filter media as Quartz sand of SS vessel construction and Activated Carbon filter of dimensions (H= 1650mm) with filter media as Activated carbon (IV-600) of SS vessel construction, with 4 nos of spiral wound RO membrane of size 4 inch dia x 1 m length of make ION EXCHANGE (HYDROMEN) (or) equal, 2 nos UV system with service flow of 1000 ltr/hr (Before 2nd filter and after SS tank out-let) with PEX pipeline recirculation loop to avoid contamination in pipe to supply for 10 beds in Post ICU, 4 beds in Transplant ICU and 1 for each TIR.) Drinage outlet to be provided near each RO outlet. | Job | 6240000 | [6 empty] | 1 | 6240000 | 4459625 | 4459625 | SI
321 |  |  | Terrace Water Proofing: Dismantling and shifting of debris to Ground Floor: Dismantling the existed Concrete Screed flooring completely by using mechanical chipping machine, and shifting debris from terrace to ground floor. | sqm | 306.8 | [6 empty] | 1700 | 521560 | 4414185 | 4414185 | SI
322 |  |  | Terrace Water Proofing: Surface Preparation & Cracks Treatment: Prepare the surface thoroughly by cleaning and wash, removing dust, dirt, oil, grease and loose particle with high 160 bar pressure water Jet pumps. Find the cracks on rcc slab, Shrinkage and non-moving cracks should be pre-treated by cutting the crack @10mmx10mm, prepare the cracks dust free by using of wire brush& air blower, mix the two components of low viscosity epoxy epoxy resin Fosroc Conbextra EP10/Dr. Fixit Pidiprime A/ SIKA Davco FLORPRIMW WB- Water based epoxy primer, two components epoxy injection grout and treat the cracks. Seal the cracks with Fosroc Nitoseal PU 50/ Dr. Fixit Crack X Paste/ Sikalastic(R) -562 IN (DAVCO K10 Polyurethane Plus) single-component moisture-cure, polyurethane hybrid joint sealant. | Sqm | 206.5 | [6 empty] | 1700 | 351050 |  |  | SI
323 |  |  | Terrace Water Proofing: Angle fillet / taper: Providing angle fillet of 75mmx75mm with polymer modified mortar in the ratio of cement: sand: aggregate in the ratio of (1:1.5:1.5) admixed with Fosroc Nitobond SBR/M-Crete PC Bond SBR/ Dr. Fixit Pidicrete URP @10% by the weight of cement to avoid cracking at 90º angle of RCC slab & Masonry wall joints. | Sqm | 507.4 | [6 empty] | 650 | 329810 |  |  | SI
324 |  |  | Terrace Water Proofing: Primer Coat: Applying 1 coat of Fosroc Nitoproof WB Primer/ Dr. Fixit Primeseal Primer/ SikaFloor(R)-133 W Primer (Floorprime WB) is a two component product and must be mixed & applied in order to perform as specified. Transfer base and the hardener to a suitable fresh container and mix thoroughly with a slow speed mixer for 2 -3 minutes which makes the mix as a milky white paste . Add double the quantity of clean water by volume to the mix gradually under mixing which makes the mix as low viscous milky white liquid. The diluted primer should be applied at a coverage of 8-10 m2/litre, preferably using roller. The applied primer should be allowed to reach tack free condition before applying liquid applied coatings and membranes. The tack free condition of Nitoproof WB primer happens after 4-5 hours of application @ 27 deg. | Sqm | 159.3 | [6 empty] | 1700 | 270810 |  |  | SI
325 |  |  | Terrace Water Proofing: Application of 2 Coats of Pitch Free PU based Liquid applied single component elastomeric waterproofing membrane (Fosroc Nitoproof 600PF/ BASF HLM5000/ Dr. Fixit Roofseal Ultra). Application of Fosroc Nitoproof 600PF/ BASF HLM5000/ Dr. Fixit Roofseal Ultra can be applied by brush, squeegee, roller/ suitable spray applied machine. It is applied at a minimum wet film thickness of 1.5mm in 2 coats. The second coat should be applied in perpendicular direction to the first coat. | Sqm | 1569.4 | [6 empty] | 1700 | 2667980 |  |  | SI
326 |  |  | Terrace Water Proofing: Laying 200 GSM Geotextile Fabric: Laying of 200GSM geotextile cloth over the waterproof coating with overlap of 30mm at cloth joints. | Sqm | 177 | [6 empty] | 1700 | 300900 |  |  | SI
327 |  |  | Terrace Water Proofing: Laying of 125mm Fiber Reinforced M20 Grade Protective Concrete Screed on Terrace. Marking the levels over the waterproofing system as per the slab level towards rain outlet. Laying of M20 grade fiber reinforced concrete screed, leveling the surface as per the marked levels, providing the proper slope to rain water outlets providing the neat kalai finish polymer modified slurry. Cut the 5mmx5mm groove for every 4mtx4mt between 24hrs - 48hrs of concrete laying. Provide water stoppers for curing with water. | Sqm | 1770 | [6 empty] | 1700 | 3009000 |  |  | SI
328 |  |  | Terrace Water Proofing: Control Joints Treatment: Provide the masking tape of both edges of joint, prepare the joints dust free by wire brush and air blower, seal the joints of 5mmx5mm with Fosroc Nitoseal PU50/ Dr. Fixit Crack X Paste/ Sikalastic(R)- 562 IN (DAVCO K10 Polyurethane Plus) single component polyurethane sealant by using PU Gun. Remove the masking tapes. | Sqm | 265.5 | [6 empty] | 1060 | 281430 |  |  | SI
329 |  |  | External Walls Repair & Waterproofing Treatment: RCC Sunshades Repairs : a. Check the damaged Rcc sunshades/ projections/ any plastered area damages by visual inspection & fiber hammer test. b. Mark those damaged area, cut the marked area with electronic cutting machine and remove the loose concrete/ plaster and expose the reinforcement. c. Apply Fosroc Reebaklens RR Rust remover/ Dr. Fixit Repairpro rust remover/ SikaRustoff-100 IN with brush for complete wetting of rusted reinforcement and allowed to react it for 16-24 hours. After 24 hours, clean the rust with wire brush & air blower. | Sqm | 5192 | [6 empty] | 645 | 3348840 |  |  | SI
External Walls Repair & Waterproofing Treatment: d. Wash the reinforcement thoroughly with clean water. Wire brush again to remove remaining loose material and finish by thoroughly washing down with clean water and allow to complete dry. e. Applying of FOSROC Nitozinc primer/ Dr. Fixit Epoxy zincrich primer/ Sika Ferrogard-950 IN to exposed existed reinforcement after cleaning the Rust, an unbroken 40 microns coating capable of provided 'active' galvanic protection for exposed reinforcement. f. Enhancing the bonding between Old RCC Ceiling to New Polymer Mortar with applying of SBR Based Polymer Modified Cementitious Bond coat admixed FOSROC Nitobond SBR/ M- Crete PC bond SBR/ Dr. Fixit Pidicrete URP.
|  |  | External Walls Repair & Waterproofing Treatment: g. Providing 20mm of structural grade polymer modified mortar by Fosroc Renderoc S2/M- Crete PC Mortar Ultra with then 2nd layer of finishing will be done by polymer modified mortar with cement mortar 1:3 (cement:sand) admixed Fosroc Nitobond SBR/M-Crete PC bond SBR/ Dr. Fixit Pidicrete URP @10% by the weight of cement weight and water, make the proper finish to existed wall level. h. Any holes will be packed with polymer modified mortar (M-Crete PC mortar Ultra) prior that holes should be prepared dust free by wire-brush and Air Blower, wash the holes with clean water and maintain SSD condition. | [12 empty] | SI
330 |  |  | External Walls Waterproofing: a. Surface Preparation: Surface must be thoroughly cleaned by using 160 bar Jet pump to clean dust, fungus, algae, grease etc. Treat any areas affected by Algae, moss or fungal growth. b. Crack Filling: The surface to be checked for cracks, cut the cracks 5mmx5mm by electronic cutting machine, clean the cracks with wire brush and air blower, seal the cracks with Fosroc Nitoseal PU50/ Dr. Fixit Crack X paste/ Sikalastic(R) -562 IN (DAVCO K10 polyurethane Plus) Polyurethane Sealant . c. External Wall Waterproof Coating & Priming: After the proper surface preparation and curing of repaired areas wash the surface well and maintaining it in saturated surface dry condition proceed for priming using Dr. Fixit Primeseal diluted in 2:1 ratio with water (2 parts Primeseal diluted with 1 part water). Maintain the spreading rate of 8-10 sq mtr per litre for a single coat application to achieve about 20 – 25 microns DFT. Allow it to dry for 6-8 hrs. | Sqm | 826 | [6 empty] | 1700 | 1404200 |  |  | SI
External Walls Waterproofing: d. COATING(2-Coats): Brush apply 1st coat of Dr. Fixit Raincoat waterproof coating without any dilution. Maintain the spreading rate of 3.5 - 4.0 sqm per litre / coat application to achieve about 120-130 microns DFT. The 2nd coat of Dr. Fixit Raincoat Classic Topcoat to be apply ith the interval of 6-8 hrs without any dilution. Maintain the spreading rate of 7-8 sqm per litre/ coat application to achieve about 50-60 microns DFT.
331 |  |  | Window Frame-Wall Joints/Gaps Treatment: Cut the joint and make a groove of 5mmx5mm by electronic cutting machine, clean the cracks with wire brush and air blower, seal the cracks with Fosroc Nitoseal PU50/ Dr. Fixit Crack X Paste/ Sikalastic(R) -562 IN (DAVCO K10 Polyurethane Plus) olyurethane Sealant. | Sqm | 421.26 | [6 empty] | 300 | 126378 |  |  | SI
332 |  |  | Supply of Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs with borders and design as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM (1:8) prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab , including neat cement slurry of honey like consistancy spread @ 3.3 kgs per Sqm. and jointed neately with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site (excluding cost of C.C. bed) including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in-charge etc.,and overheads & contractors profit complete for finished item of work. (APSS No.701 & 707). | Sqm | 2550 | [6 empty] | 342 | 872100 | 0 | 0 | SI
333 |  |  | Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707) | Rmt | 250 | [6 empty] | 120 | 30000 | 0 | 0 | SI
334 |  |  | Supply, Transportation and installation of 20KVA / 312V DC on line UPS system (for emergency lighting in all rooms & Corridor except OTs & TIRs) | Nos | 629358 | [6 empty] | 2 | 1258716 | 100000 | 200000
335 |  |  | 800 KVA Transformer OLTC for transformers with RTCC: Supply, Transportation, Installation, Testing and Commissioning of 800 KVA TRANSFORMER with all test reports. The Transformer shall be designed and manufactured as per IS:1180 OLTC with level-II with initial filling of oil as per IS 335-1993. 1000 A LT Breaker Kiosk - 01 No.The basic details of the Transformer are as under. Makes: Kirloskar / PETE / Esennar / Voltamp / Crompton / ABB / Schneider. | Nos | 4814994 | [6 empty] | 1 | 4814994 | 1685250 | 1685250
336 |  |  | 750 KVA Generator Set with AMF Control Panel Supply, Transportation, erection and commissioning (Excluding Foundation) of 3 Phase, 415, 50Hz, water cooled multi cylinder diesel generator set with alternator of 750 KVA output continuous rating directly coupled Engine and Alternator 750 KVA, 415 Volts with guard and mounted on a common base plate of Robust construction and complete with AMF panel having IP-52 protection, Acoustic Enclosure as per CPCB norms , sound absorbing material, t to restrict sound level up to 75 dB up to 1 Mtr distance and as per CPCB norms etc. | Nos | 9540000 | [6 empty] | 1 | 9540000 | 3339000 | 3339000
337 |  |  | Recording in counselling room | Job | 155378 | [6 empty] | 1 | 155378 | 32000 | 32000
338 |  |  | Local Area Network (LAN) System | Job | 460242 | [6 empty] | 1 | 460242 | 120000 | 120000
339 |  |  | Monitor Stand beside Bed in ICUs & TIRs | Nos | 6176 | [6 empty] | 31 | 191456 | 645.1612 | 20000
340 |  |  | 4 Gas Digital Alarm Panels : 4 Gas Digital Alarm Panel consisting of atl necessary accessories ie Pressure sensors,reguIators,hand valves ,pressure gauges ecL(Oxygen, Nitrous oxide, Medical Air, Vacuum) (for TIRs) | Nos | 42150 | [6 empty] | 2 | 84300 | 14755 | 29510
341 |  |  | 6 Gas Digital Alarm Panels : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. (for OTs) | Nos | 60008 | [6 empty] | 6 | 360048 | 21002.5 | 126015
342 |  |  | Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. (for TIRs) | Nos | 22201 | [6 empty] | 2 | 44402 | 7770 | 15540
343 |  |  | 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen. | Job | 48103 | [6 empty] | 1 | 48103 | 16835 | 16835
344 |  |  | 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | Job | 48103 | [6 empty] | 1 | 48103 | 16835 | 16835
345 |  |  | 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | Job | 17401 | [6 empty] | 1 | 17401 | 6090 | 6090
346 |  |  | Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED. | Job | 222013 | [6 empty] | 1 | 222013 | 77705 | 77705
347 |  |  | Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise & PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041. C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED | Job | 222013 | [6 empty] | 1 | 222013 | 77705 | 77705
[12 empty] | TOTAL | 45374570.825 |  | 15606405
[12 empty] | GRAND TOTAL | 268000808.825 |  | 92318104
Sd/- (16.03.2024)
CHIEF ENGINEER
//T.C.B.F.O//
EXECUTIVE ENGINEER
Spl. Projects, TSMSIDC

## CS 15.03.2024
Name of Work: Design, Fabrication, Installation and Commissioning on Turnkey basis for the work of Establishment of State Organ Transplant Centre in the 8th Floor, South West Block of Gandhi Hospital, Secunderabad.
COMPARATIVE STATEMENT FOR REVISED ESTIMATE (Amount in Rs.)
S.No | Description | As per Original Agmt. | As per Suppl. Agmt. | Total As per Agreements (Col. 3+ Col. 4) | As per Workdone/ To be done | Excess | Less | Remarks
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | Agreement items | 175773220.8 | 39541980 | 215315200.8 | 222626238 | 7311037.2 | 0
2 | Supplemental items |  |  |  | 45374570.825 | 45374570.825 | 0
| Sub-Total | 175773220.8 | 39541980 | 215315200.8 | 268000808.825 | 52685608.025 | 0 |  | 228458828.825 | 52685608.025
3 | Basic Price (Excluding GST) | 148960356.6102 | 33510152.5424 | 182470509.1525 | 227119329.5127 | 44648820.3602 | 0
4 | GST @ 18% | 26812864.1898 | 6031827.4576 | 32844691.6475 | 40881479.3123 | 8036787.6648 | 0
5 | Labour Cess @ 1% on Basic Price of RE | 0 | 0 | 0 | 2271193.2951 | 2271193.2951 | 0
6 | NAC @ 0.1% on Basic Price of RE | 0 | 0 | 0 | 227119.3295 | 227119.3295 | 0
7 | Provision towards Seniorage Charges on Civil Component | 0 | 0 | 0 | 2549 | 2549 | 0 | As proposed by SE
8 | Provision towards DMF Charges @ 30% on Seniorage Charges | 0 | 0 | 0 | 764.7 | 764.7 | 0
9 | Provision towards SMFT Charges @ 2% on seniorage Charges | 0 | 0 | 0 | 50.98 | 50.98 | 0
10 | Provision towards Haritha Nidhi @ 0.01% on Basic Price of Revised Estimate | 0 | 0 | 0 | 22711.933 | 22711.933 | 0
| Sub total of S.No 5 to 10 | 0 | 0 | 0 | 2524389.2376 | 2524389.2376
11 | Provision towards GST @ 18% on sub-total | 0 | 0 | 0 | 454390.0628 | 454390.0628 | 0
12 | Provision towards Engineering Supervision Charges @ 4% on RE Value |  |  |  | 10720032.353 | 10720032.353 | 0 |  |  | 195947053
13 | Provision towards Unforseen items |  |  |  | 1340004.0441 | 1340004.0441 | 0
| Grand Total | 175773220.8 | 39541980 | 215315200.8 | 283039624.5225 | 67724423.7225
|  | As per Agreements |  |  | 215315200.8 | Excess | 67724423.7225
|  | As per Revised Estimate |  |  | 283039624.5225 | Less | 0
|  | Difference |  |  | 67724423.7225 | Difference | 67724423.7225
S.No | Description | As per Original Agmt. | As per Suppl. Agmt. | Total As per Agreements | As per Workdone/ To be done | Excess | Less | Remarks
14 | 5-yrs Comprehensive Annual Maintenance Charges (CAMC) {excl. GST} | 61520427 | 13804693 | 75325120 | 92318104 | 16992984 | 0
Sd/-
CHIEF ENGINEER
//T.C.F.B.O//
EXECUTIVE ENGINEER
Spl. Projects, TSMSIDC

## GA 15.03.2024
Name of Work: Design, Fabrication, Installation and Commissioning on Turnkey basis for the work of Establishment of State Organ Transplant Centre in the 8th Floor, South West Block of Gandhi Hospital, Secunderabad.
GENERAL ABSTRACT FOR REVISED ESTIMATE
S.No |  | Amount (Rs.)
1 | Agreement Items | 222626238
2 | Supplemental Items | 45374570.825
| Sub-Total | 268000808.825
3 | Basic Price (Excluding GST) | 227119329.5127
4 | GST @ 18% | 40881479.3123
5
5 | Labour Cess @ 1% on Basic Price of Revised Estimate | 2271193.2951
6 | NAC @ 0.1% on Basic Price of Revised estimate | 227119.3295
7 | Provision towards Seniorage Charges on Civil Component | 2549
8 | Provision towards DMF Charges @ 30% on Seniorage Charges | 764.7
9 | Provision towards SMFT Charges @ 2% on seniorage Charges | 50.98
10 | Provision towards Haritha Nidhi @ 0.01% on Basic Price of Revised Estimate | 22711.933
| Sub- Total of S.No 5 to 10 | 2524389.2376
11 | Provision towards GST @ 18% on sub-total | 454390.0628
12 | Provision towards Engineering Supervision Charges @ 4% on RE Value | 10720032.353
13 | Provision towards Unforseen items and rounding off (LS) | 1340004.0441
| Total | 283039624.5225
14 | 5-yrs Comprehensive Annual Maintenance Charges (CAMC) {excl. GST} | 92318104
Sd/- (16.03.2024)
CHIEF ENGINEER
//T.C.F.B.O//
EXECUTIVE ENGINEER
Spl. Projects, TSMSIDC

## NA (hidden)
Name of Work: Design, Fabrication, Installation and Commissioning on Turnkey basis for the work of Establishment of State Organ Transplant Centre in the 8th Floor, South West Block of Gandhi Hospital, Secunderabad.
GENERAL ABSTRACT FOR REVISED ESTIMATE
S.No | Description |  |  | As per Agreement | As per Sanction Estimate for 2 Ots | As per Workdone/To be done Estimate | Excess | Less | Remarks
|  |  |  | (in Rs.) | (in Rs.) | (in Rs.) | (in Rs.) | (in Rs.)
1 | Civil Works |  |  | 40701300.8 | 7352080 | 43223650.441 | 0 | 4829730.359
2 | Electrical Works |  |  | 45337380 | 5440000 | 49845130 | 0 | 932250
3 | ELV Work |  |  | 2850000 | 0 | 3150000 | 300000 | 0
4 | Fire Fighting Work |  |  | 3892000 | 0 | 4118200 | 226200 | 0
5 | Equipment |  |  | 46177500 | 21690000 | 71887500 | 4020000 | 0
6 | Air Conditioning Work |  |  | 21104000 | 4610000 | 32960000 | 7246000 | 0
7 | Plumbing Work |  |  | 611340 | 0 | 473957.52 | 0 | 137382.48
8 | MGPS Work |  |  | 15099700 | 449900 | 16967800 | 1418200 | 0
| Sub Total-Agreement (A) |  |  | 175773220.8 | 39541980 | 222626237.961 | 13210400 | 5899362.839 | Excess is 56,87,787
9 | Civil Supplimental Works |  |  |  |  | 27907402.185 | 27907402.185 | 0
10 | Electrical Supplimental Works |  |  |  |  | 15613710 | 15613710 | 0
11 | ELV Supplimental Work |  |  |  |  | 615620 | 615620 | 0
12 | Equipment Supplimental |  |  |  |  | 191456 | 191456 | 0
13 | MGPS Supplimental Work |  |  |  |  | 1046383 | 1046383 | 0
| Sub Total-Supplimental (B) |  |  | 0 | 0 | 45374571.185 | 45374571.185 | 0
| Total (A+B) |  |  | 175773220.8 | 39541980 | 268000809.146 | 58584971.185 | 5899362.839 |  | 228458829.146 | 52685608.346
| Basic Price |  |  | 148960356.6102 | 33510152.5424 | 227119329.7847 | 49648280.6653 | 4999460.0331
| GST @ 18% | 18% |  | 26812864.1898 | 6031827.4576 | 40881479.3613 | 8936690.5197 | 899902.8059
| Total |  |  | 175773220.8 | 39541980 | 268000809.146 | 58584971.185 | 5899362.839
14 | Labour Cess @ 1% on Basic Value of Revised Estimate | 1% | 227119329.7847 |  |  | 2271193.2978 | 2271193.2978 | 0 | 1% of 22,58,11,237
15 | NAC @ 0.1% on Basic Value of Revised estimate | 0.1% | 227119329.7847 |  |  | 227119.3298 | 227119.3298 | 0 | 0.1% of 22,58,11,237
16 | Provision towards Seniorage Charges on Civil Component |  | 17572.3543 |  |  | 17572.3543 | 17572.3543 | 0
17 | Provision towards DMF Charges 30% on Seniorage Charges | 30% | 17572.3543 |  |  | 5271.7063 | 5271.7063 | 0 | 30% of 17,572
18 | Provision towards SMFT Charges 2% on seniorage Charges | 2% | 17572.3543 |  |  | 351.4471 | 351.4471 | 0 | 2% of 17,572
| Provision towards Haritha Nidhi | 0.01% |  |  |  | 22711.933 | 22711.933 | 0
| Total of S.No 14 to 18 |  |  |  |  | 2544220.0683
19 | Provision towards GST 18% on Seniorage Charges | 18% | 2544220.0683 |  |  | 457959.6123 | 457959.6123 | 0 | 18% of 25,29,700
20 | Provision towards Engineering Supervision Charges @ 2% on Equipment | 2% | 72078956 |  |  | 1441579.12 | 1441579.12 | 0 | 2% of 7,05,10,206 (7,03,18,750+1,91,456)
21 | Provision towards Engineering Supervision Charges @ 4% on RE Value (except equipment & AC) | 4% | 195921853.146 |  |  | 7836874.1258 | 7836874.1258 | 0 | 4% of 19,59,47,053 (26,64,57,259-7,05,10,206) |  | 195947053
22 | Provision towards Unforseen items and rounding off (LS) |  |  |  | 0 | 0 | 0 | 0
| Sub Total (Other than RE ECV ) |  |  |  | 0 | 12280632.9264 | 12280632.9264 | 0
| Grand Total |  |  |  | 39541980 | 280281442.0724 | 70865604.1114 | 5899362.839
[5 empty] | As Per Agreement | 215315200.8 | Excess | 70865604.1114
[5 empty] | As Per RE | 280281442.0724 | Less | 5899362.839
[5 empty] | Difference | 64966241.2724 | Difference | 64966241.2724

## NA2 (hidden)
Name of Work: Design, Fabrication, Installation and Commissioning on Turnkey basis for the work of Establishment of State Organ Transplant Centre in the 8th Floor, South West Block of Gandhi Hospital, Secunderabad.
GENERAL ABSTRACT FOR REVISED ESTIMATE
S.No |  | Amount (Rs.)
1 | GO Rt No. 519, HM&FW (A1) Dept. 06.09.2018 (Original sanction) | 350000000
2 | GO Rt No. 358, HM&FW (C2) Dept. 24.06.2023 (Additional sanction) | 50000000
3 | Total Sanctioned Amount | 400000000
4 |  | 203000000
5 | Tender Discount | 27226779.2
6 | Tender Value | 175773220.8
7 | Secondary Agreement | 48059536.4
8 | Agreement Value | 223832757.2
9 | Savings | 27226779.2
10 | Agreement + Savings | 251059536.4
11 | Contract value as per revised estimate | 268000809.146
12 |  | 16941272.746
13 | Amount of Workdone/to be done as per the Revised Estimate including Supplimental items Less: | 280281442.0724
14 | Removal & Relocation of Roof Top Solar Panels Less: | 1400000
| Balance Available from Sanctioned Amount | 118318557.9276

## RE-CS (hidden)
COMPARITIVE STATEMENT FOR ORIGINAL AGREEMENT AND REVISED ESTIMATE OF SOTC 8TH FLOOR, SOUTH-WEST BLOCK, GANDHI HOSPITAL
S.No | Tech. Spec Cl. No in TED | Item S.No | Item Code | Item Name | UOM | Unit Rate (Rs.) | As Per Agreement (with 4 Ots) |  | Additional Sanction fot 2 Ots |  | Total (6 Ots) |  | As Per Work Done/To Be Done |  | Variation
[7 empty] | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | Excess | Less
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  | 4: Modular Operation Theatres |  |  |  |  | Workdone Amount | Sanction Amount | Excess Amount | Less Amount | as per agreement | as per additional 2 Ots
1 | 1 | 1 | SOTC001 | Stainless Steel Pre-fabricated Wall panels. (MOTs & MOT Corridor) - Wall panels | Sqm | 15010 | 400 | 6004000 | 350 | 5253500 | 750 | 11257500 | 491.9486 | 7384148.486 | 0 | 3873351.514 | C | C | CIVIL | 1 | 43223650.441 | 48053380.8 | 8476437.164 | 13306167.523 | 40701300.8 | 7352080
|  | 15: 0; 16: 0 |  | E | ELECTRICAL | 3 | 49845130 | 50777380 | 3167750 | 4100000 | 45337380 | 5440000
2 | 1 | 199 | SOTC002 | Stainless Steel Pre-fabricated Ceiling panels In MOTs & MOTs Corridor | Sqm | 15010 | 385 | 5778850 | 78 | 1170780 | 463 | 6949630 | 263.165 | 3950106.65 | 0 | 2999523.35 | C | ELV |  | 5 | 3150000 | 2850000 | 300000 | 0 | 2850000 | 0
|  | 15: 0; 16: 0 |  | FF | FIRE FIGHTING | 7 | 4118200 | 3892000 | 226200 | 0 | 3892000 | 0
3 | 1.5 | 2 | SOTC003 | Dynamic Hatch Box | Nos | 295000 | 2 | 590000 | 1 | 295000 | 3 | 885000 | 0 | 0 | 0 | 885000 | EQP | EQP | EQUIPMENT | 8 | 71887500 | 67867500 | 12005000 | 7985000 | 46177500 | 21690000
|  | 15: 0; 16: 0 |  | AC | AIR CONDITIONING | 10 | 32960000 | 25714000 | 7246000 | 0 | 21104000 | 4610000
4 | 2.1 | 3 | SOTC004 | Electro conductive Flooring inside MOTs | Sqm | 4035 | 160 | 645600 | 80 | 322800 | 240 | 968400 | 217.7802 | 878743.107 | 0 | 89656.893 | C | P | PLUMBING | 11 | 473957.52 | 611340 | 32627.52 | 170010 | 611340 | 0
|  | 15: 0; 16: 0 |  | G | MGPS | 12 | 16967800 | 15549600 | 1753050 | 334850 | 15099700 | 449900
5 | 2.2 | 4 | SOTC005 | Flooring with Vinyl Sheets In MOT Corridor | Sqm | 3750 | 175 | 656250 | 50 | 187500 | 225 | 843750 | 87.0329 | 326373.525 | 0 | 517376.475 | C | CS | CIVIL SUPPLIMENTAL | 2 | 27907402.185 | 0 | 27907402.185 | 0 | 0 | 0
|  | 15: 0; 16: 0 |  | ES | ELECTRICAL SUPPLIMENTAL | 4 | 15613710 | 0 | 15613710 | 0 | 0 | 0
6 | 3 | 5 | SOTC006 | Uni Directional Ceiling Laminar Airflow Systems | Nos | 465000 | 4 | 1860000 | 2 | 930000 | 6 | 2790000 | 6 | 2790000 | 0 | 0 | AC | ELVS | ELV SUPPLIMENTAL | 6 | 615620 | 0 | 615620 | 0 | 0 | 0
|  | 15: 0; 16: 0 |  | EQPS | EQUIPMENT SUPPLIMENTAL | 9 | 191456 | 0 | 191456 | 0 | 0 | 0
7 | 3.1 | 6 | SOTC007 | Air Handling Units (AHUs) 11 TR | Nos | 1495000 | 4 | 5980000 | 2 | 2990000 | 6 | 8970000 | 6 | 8970000 | 0 | 0 | AC | GS | MGPS SUPPLIMENTAL | 13 | 1046383 | 0 | 1046383 | 0 | 0 | 0
[15 empty] | 0 | 0
8 | 3.2 | 7 | SOTC008 | Condensing Units | Nos | 345000 | 4 | 1380000 | 2 | 690000 | 6 | 2070000 | 6 | 2070000 | 0 | 0 | AC
|  | 4: AE; 6: 345000; 13: 4; 14: 1380000; 15: 1380000; 16: 0 | AC
9 | 4 | 8 | SOTC009 | Pressure Relief Dampers | Nos | 22500 | 4 | 90000 | 2 | 45000 | 6 | 135000 | 6 | 135000 | 0 | 0 | EQP
[15 empty] | 0 | 0
10 | 5.1 | 9 | SOTC010 | Single arm Anesthesia Pendants (Imported) | Nos | 1195000 | 4 | 4780000 | 2 | 2390000 | 6 | 7170000 | 6 | 7170000 | 0 | 0 | EQP
[15 empty] | 0 | 0
11 | 5.2 | 10 | SOTC011 | Triple Dome Ceiling OT LED Lights (Imported) | Nos | 4750000 | 2 | 9500000 |  | 0 | 2 | 9500000 | 2 | 9500000 | 0 | 0 | EQP
|  | 4: AE; 6: 4750000; 13: 2; 14: 9500000; 15: 9500000; 16: 0 | EQP
12 | 5.3 | 11 | SOTC012 | Double Dome Ceiling OT LED Lights (Imported) | Nos | 3550000 | 2 | 7100000 | 2 | 7100000 | 4 | 14200000 | 2 | 7100000 | 0 | 7100000 | EQP
[15 empty] | 0 | 0
13 | 5.4 | 12 | SOTC013 | Detachable Hi Definition Cameras in Triple Dome Ceiling OT Lights | Nos | 995000 | 2 | 1990000 | 1 | 995000 | 3 | 2985000 | 3 | 2985000 | 0 | 0 | EQP
|  | 14: 0; 15: 0; 16: 0 | EQP
14 | 91 | 13 | SOTC014 | Ceiling/Wall mounted CCTV Room Camera | Nos | 22500 | 4 | 90000 | 2 | 45000 | 6 | 135000 | 6 | 135000 | 0 | 0 | E
[15 empty] | 0 | 0
15 | 6 | 14 | SOTC015 | LED Peripheral Lights cum clean room (OT) luminaries | Nos | 18750 | 62 | 1162500 | 40 | 750000 | 102 | 1912500 | 102 | 1912500 | 0 | 0 | E
|  | 4: AE; 6: 18750; 13: 5; 14: 93750; 15: 93750; 16: 0 | E
16 | 7 | 239 | SOTC016 | View Window with Motorised Blinds of 1 Mt Length & 1 Mt Height | Nos | 115000 | 7 | 805000 | 2 | 230000 | 9 | 1035000 | 9 | 1035000 | 0 | 0 | EQP
|  | 4: AE; 6: 115000; 13: 5; 14: 575000; 15: 575000; 16: 0 | EQP
17 | 8 | 15 | SOTC017 | Hermetically Sealed Doors (1.80mt x 2.10 mt) | Nos | 115000 | 4 | 460000 | 2 | 230000 | 6 | 690000 | 6 | 690000 | 0 | 0 | C
|  | 4: AE; 6: 115000; 13: 3; 14: 345000; 15: 345000; 16: 0 | C
18 | 8 | 240 | SOTC018 | (1.50mt x 2.10 mt) Sliding Automatic Sliding Doors with View Windoy of 1 Mt x 1 Mt | Nos | 525000 | 2 | 1050000 |  | 0 | 2 | 1050000 | 2 | 1050000 | 0 | 0 | C
[15 empty] | 0 | 0
19 | 10 | 16 | SOTC019 | Storage Units | Nos | 75000 | 4 | 300000 | 2 | 150000 | 6 | 450000 | 6 | 450000 | 0 | 0 | C
[15 empty] | 0 | 0
20 | 11 | 17 | SOTC020 | Writing Board (List Board) | Nos | 18750 | 4 | 75000 | 2 | 37500 | 6 | 112500 | 6 | 112500 | 0 | 0 | C
[15 empty] | 0 | 0
21 | 12 | 18 | SOTC021 | X-Ray CT Scan LED viewing Screen | Nos | 37500 | 4 | 150000 | 2 | 75000 | 6 | 225000 | 6 | 225000 | 0 | 0 | EQP
[15 empty] | 0 | 0
22 | 13 | 19 | SOTC022 | Touch Screen Surgeon Control Panels | Nos | 385000 | 4 | 1540000 | 2 | 770000 | 6 | 2310000 | 6 | 2310000 | 0 | 0 | EQP
|  | 4: AE; 6: 385000; 13: 3; 14: 1155000; 15: 1155000; 16: 0 | EQP
23 | 14 | 20 | SOTC023 | 3-Bay Scrub Stations/Sinks | Nos | 368750 | 2 | 737500 |  | 0 | 2 | 737500 | 2 | 737500 | 0 | 0 | EQP
|  | 4: AE; 6: 368750; 13: 2; 14: 737500; 15: 737500; 16: 0 | EQP
24 | 16 | 21 | SOTC024 | Video and Image Management system | Nos | 8000000 | 1 | 8000000 |  | 0 | 1 | 8000000 | 1 | 8000000 | 0 | 0 | EQP
[15 empty] | 0 | 0
25 | 16.1 | 22 | SOTC025 | Medical Grade Monitors 32 inch 4 K Resolution | Nos | 1295000 | 4 | 5180000 | 2 | 2590000 | 6 | 7770000 | 6 | 7770000 | 0 | 0 | EQP
[15 empty] | 0 | 0
26 | 16.2 | 23 | SOTC026 | Wall mounted large screen display 55 inch (Commercial Grade) | Nos | 495000 | 2 | 990000 |  | 0 | 2 | 990000 | 2 | 990000 | 0 | 0 | EQP
[15 empty] | 0 | 0
27 | 16.3 & 16.4 | 24 | SOTC027 | Cable connections for integration within MOTs and with Workshop Projector Hall, Networks with OFC Cable | Job | 997500 | 4 | 3990000 | 2 | 1995000 | 6 | 5985000 | 6 | 5985000 | 0 | 0 | E
[15 empty] | 0 | 0
28 | 16.5 | 25 | SOTC028 | Wireless Microphone | Nos | 255000 | 1 | 255000 |  | 0 | 1 | 255000 | 1 | 255000 | 0 | 0 | EQP
[15 empty] | 0 | 0
29 | 16.6 | 26 | SOTC029 | Digital mixer Amplifier | Nos | 245000 | 1 | 245000 |  | 0 | 1 | 245000 | 1 | 245000 | 0 | 0 | EQP
[15 empty] | 0 | 0
30 | 16.7 | 27 | SOTC030 | Ceiling Mounted Speakers | Nos | 15000 | 4 | 60000 | 2 | 30000 | 6 | 90000 | 6 | 90000 | 0 | 0 | EQP
[15 empty] | 0 | 0
31 | 16.8 | 28 | SOTC031 | Video Conferencing System | Nos | 1195000 | 1 | 1195000 |  | 0 | 1 | 1195000 | 1 | 1195000 | 0 | 0 | EQP
[15 empty] | 0 | 0
32 | 17.1 | 29 | SOTC032 | Home Theatre Power Conditioner, 230 V | Nos | 145000 | 1 | 145000 |  | 0 | 1 | 145000 | 1 | 145000 | 0 | 0 | EQP
[15 empty] | 0 | 0
33 | 17.2 | 30 | SOTC033 | Amplifier (8 Channel) | Nos | 245000 | 1 | 245000 |  | 0 | 1 | 245000 | 1 | 245000 | 0 | 0 | EQP
[15 empty] | 0 | 0
34 | 17.3 | 31 | SOTC034 | HiFi Active Sub Woofer | Nos | 50000 | 1 | 50000 |  | 0 | 1 | 50000 | 1 | 50000 | 0 | 0 | EQP
[15 empty] | 0 | 0
35 | 17.5 | 32 | SOTC035 | 4K Laser Projection TV | Nos | 1495000 | 1 | 1495000 |  | 0 | 1 | 1495000 | 1 | 1495000 | 0 | 0 | EQP
[15 empty] | 0 | 0
36 | 17.6 & 17.7 | 200 | SOTC036 | Equalization & Loud Speaker Control System | Nos | 40000 | 1 | 40000 |  | 0 | 1 | 40000 | 1 | 40000 | 0 | 0 | EQP
[15 empty] | 0 | 0
37 | 17.8 | 33 | SOTC037 | Sound Analog Mixer | Nos | 245000 | 1 | 245000 |  | 0 | 1 | 245000 | 1 | 245000 | 0 | 0 | EQP
[15 empty] | 0 | 0
38 | 19 | 201 | SOTC038 | Electrical Installations in MOTs & TIRs | Job | 195000 | 7 | 1365000 | 2 | 390000 | 9 | 1755000 | 9 | 1755000 | 0 | 0 | E
[15 empty] | 0 | 0
[10 empty] | PART - A |  | SUB TOTAL |  | 111378121.768 | 0
|  |  |  | Transplant Isolation Rooms | [10 empty] | 0 | 0
39 | 1 | 34 | SOTC039 | Stainless Steel Pre-fabricated Wall panels in TIRs & TIR Corridor | Sqm | 15010 | 202 | 3032020 | 0 | 0 | 202 | 3032020 | 202 | 3032020 | 0 | 0 | C
|  | 4: AE; 6: 15010; 13: 136.9318; 14: 2055346.318; 15: 2055346.318; 16: 0 | C
40 | 1 | 35 | SOTC040 | Stainless Steel Pre-fabricated Ceiling panels in TIRs and TIR Corridor | Sqm | 15010 | 146 | 2191460 | 0 | 0 | 146 | 2191460 | 146 | 2191460 | 0 | 0 | C
|  | 4: AE; 6: 15010; 13: 33.22; 14: 498632.2; 15: 498632.2; 16: 0 | C
41 | 2.1 | 202 | SOTC041 | Electro conductive Flooring inside TIRs | Sqm | 4035 | 146 | 589110 |  | 0 | 146 | 589110 | 73.6644 | 297235.854 | 0 | 291874.146 | C
[15 empty] | 0 | 0
42 | 2.2 | 36 | SOTC042 | Flooring with Vinyl Sheets In TIR Corridor | Sqm | 3750 | 61 | 228750 |  | 0 | 61 | 228750 | 61 | 228750 | 0 | 0 | C
|  | 4: AE; 6: 3750; 13: 70.4074; 14: 264027.75; 15: 264027.75; 16: 0 | C
43 | 3 | 37 | SOTC043 | Uni Directional Ceiling Laminar Airflow Systems | Nos | 395000 | 3 | 1185000 |  | 0 | 3 | 1185000 | 3 | 1185000 | 0 | 0 | AC
[15 empty] | 0 | 0
44 | 3.1 | 38 | SOTC044 | Air Handling Units (AHUs) 11 TR | Nos | 1495000 | 2 | 2990000 |  | 0 | 2 | 2990000 | 2 | 2990000 | 0 | 0 | AC
[15 empty] | 0 | 0
45 | 3.1 | 39 | SOTC045 | Air Handling Units (AHUs) 8.5 TR | Nos | 1195000 | 1 | 1195000 |  | 0 | 1 | 1195000 | 1 | 1195000 | 0 | 0 | AC
[15 empty] | 0 | 0
46 | 3.2 | 40 | SOTC046 | Condensing Units | Nos | 345000 | 3 | 1035000 |  | 0 | 3 | 1035000 | 3 | 1035000 | 0 | 0 | AC
|  | 4: AE; 6: 345000; 13: 3; 14: 1035000; 15: 1035000; 16: 0 | AC
47 | 4 | 41 | SOTC047 | Pressure Relief Dampers | Nos | 22500 | 3 | 67500 |  | 0 | 3 | 67500 | 3 | 67500 | 0 | 0 | EQP
[15 empty] | 0 | 0
48 | 8 | 42 | SOTC049 | Hermetically Sealed Doors (1.80mt x 2.10 mt) | Nos | 525000 | 3 | 1575000 |  | 0 | 3 | 1575000 | 3 | 1575000 | 0 | 0 | C
[15 empty] | 0 | 0
49 | 15 | 43 | SOTC050 | 12mm thick glazed Glass partition walls in TIRs | Sqm | 650 | 40 | 26000 |  | 0 | 40 | 26000 | 40 | 26000 | 0 | 0 | C
[15 empty] | 0 | 0
50 | 15 | 44 | SOTC051 | Wall mounted LED TV43 inchesFull HD | Nos | 165000 | 3 | 495000 |  | 0 | 3 | 495000 | 3 | 495000 | 0 | 0 | EQP
[15 empty] | 0 | 0
51 | 91 | 45 | SOTC052 | Ceiling/Wall mounted CCTV Room Camera | Nos | 12000 | 3 | 36000 |  | 0 | 3 | 36000 | 3 | 36000 | 0 | 0 | E
[15 empty] | 0 | 0
52 | 88.6 | 46 | SOTC053 | BED HEAD PANEL FOR TIR WITH DOUBLE OUTLETS AND ELECTRICAL OUTLETS | Nos | 49500 | 3 | 148500 |  | 0 | 3 | 148500 | 3 | 148500 | 0 | 0 | G
[15 empty] | 0 | 0
53 | 12 | 47 | SOTC054 | X-RAY VIEWERS FOR ALL ICUS AND PRE OPP AREAS AND DOCTORS ROOMS | Nos | 37500 | 5 | 187500 |  | 0 | 5 | 187500 | 5 | 187500 | 0 | 0 | EQP
|  | 4: AE; 13: 1; 14: 37500; 15: 37500 | EQP
54 | 11 | 48 | SOTC055 | WRITING BOARDS FOR ICUS, PRE OPP | Nos | 18750 | 5 | 93750 |  | 0 | 5 | 93750 | 5 | 93750 | 0 | 0 | C
|  | 4: AE; 6: 18750; 13: 1; 14: 18750; 15: 18750; 16: 0 | C
[10 empty] | PART-A |  | SUB TOTAL |  | 18692972.122 | 0
|  |  |  | Electrical Works | [10 empty] | 0 | 0
55 | 91 | 49 | SOTC056 | CCTV CEILING CAMERA | Nos | 9500 | 10 | 95000 |  | 0 | 10 | 95000 | 10 | 95000 | 0 | 0 | E
[15 empty] | 0 | 0
56 | 22 a | 50 | SOTC057 | Supply and Fixing of 25mm dia Conduit Pipes surface on wall. | Rmt | 110 | 10000 | 1100000 |  | 0 | 10000 | 1100000 | 10000 | 1100000 | 0 | 0 | E
[15 empty] | 0 | 0
57 | 22 b | 51 | SOTC058 | Supply and Fixing of 25mm dia Conduit Pipes Concealed on wall. | Rmt | 115 | 4000 | 460000 |  | 0 | 4000 | 460000 | 4000 | 460000 | 0 | 0 | E
[15 empty] | 0 | 0
58 | 23 a | 52 | SOTC059 | Wiring with run of 2 of 1.5 Sqmm Copper cable for points wiring. | Pts | 1525 | 570 | 869250 |  | 0 | 570 | 869250 | 570 | 869250 | 0 | 0 | E
[15 empty] | 0 | 0
59 | 23 b | 53 | SOTC060 | Wiring with run of 2 of 1.5 Sqmm Copper cable for stairecase points wiring. | Pts | 1100 | 10 | 11000 |  | 0 | 10 | 11000 | 10 | 11000 | 0 | 0 | E
[15 empty] | 0 | 0
60 | 23 c | 54 | SOTC061 | Supply and fixing of 6A/10A ISI Mark 3/2 pin Modular socket Common switch board | Pts | 900 | 25 | 22500 |  | 0 | 25 | 22500 | 25 | 22500 | 0 | 0 | E
[15 empty] | 0 | 0
61 | 23 d | 55 | SOTC062 | Wiring with 3 of 1.5 sq.mm with 6A switch and 6A, 3/2 pin socket Modular type with 6A switch control fixing on separate board. | Pts | 2800 | 50 | 140000 |  | 0 | 50 | 140000 | 50 | 140000 | 0 | 0 | E
[15 empty] | 0 | 0
62 | 23 e | 56 | SOTC063 | Supply and fixing of 6A switchs - 2 Nos and 6A 3/2 pin socket - 3 Nos Modular type with cover plate | Pts | 1400 | 200 | 280000 |  | 0 | 200 | 280000 | 200 | 280000 | 0 | 0 | E
[15 empty] | 0 | 0
63 | 23 f | 203 | SOTC064 | Supply & fixing of 16A/6A, 2 in one socket with 16A switch control modular type | Nos | 900 | 200 | 180000 |  | 0 | 200 | 180000 | 200 | 180000 | 0 | 0 | E
[15 empty] | 0 | 0
64 | 23 g | 204 | SOTC065 | Supply & fixing of 32A, socket with switch control modular | Nos | 1600 | 18 | 28800 |  | 0 | 18 | 28800 | 18 | 28800 | 0 | 0 | E
[15 empty] | 0 | 0
65 | 23 h | 205 | SOTC066 | Supply & fixing of 64A, socket with 64A switch control modular type | Nos | 18000 | 4 | 72000 |  | 0 | 4 | 72000 | 4 | 72000 | 0 | 0 | E
[15 empty] | 0 | 0
66 | 24 a | 57 | SOTC067 | Supply and Run of 1 of 1.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 36 | 2000 | 72000 |  | 0 | 2000 | 72000 | 2000 | 72000 | 0 | 0 | E
[15 empty] | 0 | 0
67 | 24 b | 58 | SOTC068 | Supply and Run of 3 of 1.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable . | Rmt | 100 | 2000 | 200000 |  | 0 | 2000 | 200000 | 2000 | 200000 | 0 | 0 | E
[15 empty] | 0 | 0
68 | 24 c | 59 | SOTC069 | Supply and Run of 3 of 2.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 145 | 8000 | 1160000 |  | 0 | 8000 | 1160000 | 8000 | 1160000 | 0 | 0 | E
[15 empty] | 0 | 0
69 | 24 d | 60 | SOTC070 | Supply and Run of 3 runs of 4.0 sq mm (phase neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 230 | 5000 | 1150000 |  | 0 | 5000 | 1150000 | 5000 | 1150000 | 0 | 0 | E
[15 empty] | 0 | 0
70 | 24 e | 61 | SOTC071 | Supply and Run of 3 of 6.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 325 | 300 | 97500 |  | 0 | 300 | 97500 | 300 | 97500 | 0 | 0 | E
[15 empty] | 0 | 0
71 | 24 f | 62 | SOTC072 | Supply and Run of 5 of 6.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 545 | 300 | 163500 |  | 0 | 300 | 163500 | 300 | 163500 | 0 | 0 | E
[15 empty] | 0 | 0
72 | 24 g | 63 | SOTC073 | Supply and Run of 5 of 10.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 850 | 500 | 425000 |  | 0 | 500 | 425000 | 500 | 425000 | 0 | 0 | E
[15 empty] | 0 | 0
73 | 25 a | 64 | SOTC074 | Supply and fixing of DP Metal Enclosure with IP 20 Protection DB Make with 1 No 20A, 10 KA DP MCB | Nos | 1800 | 8 | 14400 |  | 0 | 8 | 14400 | 8 | 14400 | 0 | 0 | E
[15 empty] | 0 | 0
74 | 25 b | 65 | SOTC075 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 (For Lighting DBs) | Nos | 13000 | 10 | 130000 |  | 0 | 10 | 130000 | 10 | 130000 | 0 | 0 | E
[15 empty] | 0 | 0
75 | 25 c | 230 | SOTC076 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 (For Power DB's) | Nos | 13000 | 14 | 182000 |  | 0 | 14 | 182000 | 14 | 182000 | 0 | 0 | E
[15 empty] | 0 | 0
76 | 25 d | 66 | SOTC077 | Supply and fixing of 8 Way VTPN DB with IP 43 Protection as per IS:13032 | Nos | 50000 | 5 | 250000 |  | 0 | 5 | 250000 | 5 | 250000 | 0 | 0 | E
[15 empty] | 0 | 0
77 | 25 e | 67 | SOTC078 | Supply and fixing of cable adopteres box with cover for DBs including, massanory work etc., complete., | Nos | 6000 | 10 | 60000 |  | 0 | 10 | 60000 | 10 | 60000 | 0 | 0 | E
[15 empty] | 0 | 0
78 | 26 a | 206 | SOTC079 | Providing independent earthing for Important equipment with 40mm dia 'B' class 2.5m long G.I pipe (GI Earthing) | Nos | 22500 | 18 | 405000 |  | 0 | 18 | 405000 | 18 | 405000 | 0 | 0 | E
[15 empty] | 0 | 0
79 | 26 b | 68 | SOTC080 | Providing independent earthing by exacavating a pit to a depth of 2.25Mtr in all soils as per size specified in the data for Sophisticated Electronic equipment (Copper Earthing) | Nos | 54000 | 18 | 972000 |  | 0 | 18 | 972000 | 18 | 972000 | 0 | 0 | E
[15 empty] | 0 | 0
80 | 26 b 1 | 69 | SOTC081 | Providing independent earthing for Important equipment with 100mm dia Heavy gauge C.I Earthing | Nos | 25000 | 6 | 150000 |  | 0 | 6 | 150000 | 6 | 150000 | 0 | 0 | E
[15 empty] | 0 | 0
81 | 26 c | 70 | SOTC082 | Supply and Run of 50mm x 6mm G.I Strip | Rmt | 450 | 400 | 180000 |  | 0 | 400 | 180000 | 400 | 180000 | 0 | 0 | E
[15 empty] | 0 | 0
82 | 26 d | 71 | SOTC083 | Supply and Run of 25mm x 3mm copper strip | Rmt | 300 | 400 | 120000 |  | 0 | 400 | 120000 | 400 | 120000 | 0 | 0 | E
[15 empty] | 0 | 0
83 | 27 a | 207 | SOTC084 | Supply, transportation and fixing of 22W +/ 10% , >/ 2300 lumens, 1200mm length LED light | Nos | 4800 | 20 | 96000 |  | 0 | 20 | 96000 | 20 | 96000 | 0 | 0 | E
[15 empty] | 0 | 0
84 | 27 b | 208 | SOTC085 | Supply, transportation and fixing 32-36W (>=3600 Lumens), 2' x2' (600mm x 600mm) slim panel LED luminaire | Nos | 4000 | 60 | 240000 |  | 0 | 60 | 240000 | 60 | 240000 | 0 | 0 | E
[15 empty] | 0 | 0
85 | 27 c | 209 | SOTC086 | Supply, transportation and fixing 12 W +/-10% (>= 1200 Lumens) Down lighter back lit LED Down Light Recessed / Surface | Nos | 1400 | 215 | 301000 |  | 0 | 215 | 301000 | 215 | 301000 | 0 | 0 | E
[15 empty] | 0 | 0
86 | 27 d | 210 | SOTC087 | Supply, transportation and fixing 18 W +/-10% (>= 1800 Lumens) Down lighter back lit LED Down Light | Nos | 1800 | 95 | 171000 |  | 0 | 95 | 171000 | 95 | 171000 | 0 | 0 | E
[15 empty] | 0 | 0
87 | 27 e | 72 | SOTC088 | Supply, transportation and fixing ISI mark batten holder / slanting holder | Nos | 160 | 8 | 1280 |  | 0 | 8 | 1280 | 8 | 1280 | 0 | 0 | E
[15 empty] | 0 | 0
88 | 27 f | 231 | SOTC089 | Supply, Transportation of energy efficient fan, 1200 mm sweep, aluminium body, consuming 28 W, BEE 5 star rated, ceiling fan | Nos | 3700 | 40 | 148000 |  | 0 | 40 | 148000 | 40 | 148000 | 0 | 0 | E
[15 empty] | 0 | 0
89 | 27 f 1 | 73 | SOTC090 | Supply and fixing of Modular type Stepped electronic regulator. | Nos | 1000 | 40 | 40000 |  | 0 | 40 | 40000 | 40 | 40000 | 0 | 0 | E
[15 empty] | 0 | 0
90 | 27 f 2 | 74 | SOTC091 | Labour charges for fixing of ceiling fan and regulator | Nos | 210 | 40 | 8400 |  | 0 | 40 | 8400 | 40 | 8400 | 0 | 0 | E
[15 empty] | 0 | 0
91 | 27 f 3 | 75 | SOTC092 | Supply and erecting 19/20mm steel tube down rod of one meter length | Nos | 600 | 40 | 24000 |  | 0 | 40 | 24000 | 40 | 24000 | 0 | 0 | E
[15 empty] | 0 | 0
92 | 27 g | 211 | SOTC093 | Supply of 12" (300mm) Light duty exhaust fan | Nos | 3000 | 5 | 15000 |  | 0 | 5 | 15000 | 5 | 15000 | 0 | 0 | E
[15 empty] | 0 | 0
93 | 27 h | 212 | SOTC094 | Supply,Transportation of 12" (300mm) ISI, 900 RPM Heavy duty exhaust fan | Nos | 4900 | 10 | 49000 |  | 0 | 10 | 49000 | 10 | 49000 | 0 | 0 | E
[15 empty] | 0 | 0
94 | 27 i | 76 | SOTC095 | Labour charges for fixing the exhaust fan in wall with necessary connections | Nos | 900 | 15 | 13500 |  | 0 | 15 | 13500 | 15 | 13500 | 0 | 0 | E
[15 empty] | 0 | 0
95 | 27 j | 77 | SOTC096 | Supply and fixing of GI louver shutter including GI mesh | Nos | 3200 | 15 | 48000 |  | 0 | 15 | 48000 | 15 | 48000 | 0 | 0 | E
[15 empty] | 0 | 0
96 | 28 a | 213 | SOTC097 | Main Power Panel with 1000A 4 Pole ACB as incomer - 1 No and out goings 800 A 4P MCCB - 1 No., 630 A 4P MCCB - 1 No., 400A 4P MCCB - 4 Nos & 250A 4P MCCB - 3 No's with required Digital Ammeter and Voltmer, LED Indicators | Nos | 1315000 | 1 | 1315000 |  | 0 | 1 | 1315000 | 1 | 1315000 | 0 | 0 | E
[15 empty] | 0 | 0
97 | 28 b | 214 | SOTC098 | Floor Power Panel : Incomer: 630A 4 Pole MCCB,- 1 No Outgoings 250 A 4P MCCB - 4 No's 125 A 4P MCCB - 10 No's, 63 A 4P MCCB - 4 No's with required Digital Ammeter and Voltmer, LED Indicators | Nos | 875000 | 1 | 875000 |  | 0 | 1 | 875000 | 1 | 875000 | 0 | 0 | E
[15 empty] | 0 | 0
98 | 28 c | 215 | SOTC099 | Electrical Lighting Panels : Incomer: 250 A 4 Pole MCCB - 1 No, Out Goings 125 A 4P MCCB - 4 No's 63 A 4P MCCB - 3 No's with required Digital Ammeter and Voltmer, LED Indicators | Nos | 370000 | 2 | 740000 |  | 0 | 2 | 740000 | 2 | 740000 | 0 | 0 | E
[15 empty] | 0 | 0
99 | 29 d | 78 | SOTC100 | 130KVAR Out Door Capacitor panel : Incomer: 250A FP MCCB - 1 No, 63A 10KA TP MCB - 9 Nos. 20 KVAR Capacitor Duty contactors - 5 Nos., 10 KVAR Capacitor Duty contactors - 2 Nos, .5 KVAR Capacitor Duty contactors - 2 Nos. 12 stage APFC Relay - 1 No | Nos | 450000 | 1 | 450000 |  | 0 | 1 | 450000 | 1 | 450000 | 0 | 0 | E
[15 empty] | 0 | 0
100 | 29 a | 232 | SOTC101 | 630 KVA Transformer OLTC for transformers with RTCC: Supply, Transportation, Installation, Testing and Commissioning of 630 KVA TRANSFORMER with all test reports. The Transformer shall be designed and manufactured as per IS:1180 OLTC with level-II with initial filling of oil as per IS 335-1993. 1000 A LT Breaker Kiosk - 01 No.The basic details of the Transformer are as under. Makes: Kirloskar / PETE / Esennar / Voltamp / Crompton / ABB / Schneider. | Nos | 4000000 | 1 | 4000000 |  | 0 | 1 | 4000000 | 0 | 0 | 0 | 4000000 | E
[15 empty] | 0 | 0
101 | 30 a | 79 | SOTC102 | Supply of 25 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 300 | 200 | 60000 |  | 0 | 200 | 60000 | 200 | 60000 | 0 | 0 | E
[15 empty] | 0 | 0
102 | 30 b | 80 | SOTC103 | Supply of 50 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 560 | 200 | 112000 |  | 0 | 200 | 112000 | 200 | 112000 | 0 | 0 | E
[15 empty] | 0 | 0
103 | 30 c | 81 | SOTC104 | Supply of 70 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 750 | 75 | 56250 |  | 0 | 75 | 56250 | 75 | 56250 | 0 | 0 | E
[15 empty] | 0 | 0
104 | 30 d | 82 | SOTC105 | Supply of 120 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 1050 | 50 | 52500 |  | 0 | 50 | 52500 | 50 | 52500 | 0 | 0 | E
[15 empty] | 0 | 0
105 | 30 e | 83 | SOTC106 | Supply of 185 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 1500 | 50 | 75000 |  | 0 | 50 | 75000 | 50 | 75000 | 0 | 0 | E
[15 empty] | 0 | 0
106 | 30 f | 84 | SOTC107 | Supply of 240 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 1900 | 100 | 190000 |  | 0 | 100 | 190000 | 100 | 190000 | 0 | 0 | E
[15 empty] | 0 | 0
107 | 30 g | 85 | SOTC108 | Supply of 300 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 2400 | 500 | 1200000 |  | 0 | 500 | 1200000 | 500 | 1200000 | 0 | 0 | E
[15 empty] | 0 | 0
108 | 31 a | 86 | SOTC109 | Termination of UG cables of 3.5 core 25 Sq.mm | Nos | 850 | 8 | 6800 |  | 0 | 8 | 6800 | 8 | 6800 | 0 | 0 | E
[15 empty] | 0 | 0
109 | 31 b | 87 | SOTC110 | Termination of UG cables of 3.5 core 50 Sq.mm | Nos | 1200 | 8 | 9600 |  | 0 | 8 | 9600 | 8 | 9600 | 0 | 0 | E
[15 empty] | 0 | 0
110 | 31 c | 88 | SOTC111 | Termination of UG cables of 3.5 core 70 Sq.mm | Nos | 1500 | 8 | 12000 |  | 0 | 8 | 12000 | 8 | 12000 | 0 | 0 | E
[15 empty] | 0 | 0
111 | 31 d | 89 | SOTC112 | Termination of UG cables of 3.5 core 120 Sq.mm | Nos | 1900 | 4 | 7600 |  | 0 | 4 | 7600 | 4 | 7600 | 0 | 0 | E
[15 empty] | 0 | 0
112 | 31 e | 90 | SOTC113 | Termination of UG cables of 3.5 core 185 Sq.mm | Nos | 2500 | 4 | 10000 |  | 0 | 4 | 10000 | 4 | 10000 | 0 | 0 | E
[15 empty] | 0 | 0
113 | 31 f | 91 | SOTC114 | Termination of UG cables of 3.5 core 240 Sq.mm | Nos | 3500 | 4 | 14000 |  | 0 | 4 | 14000 | 4 | 14000 | 0 | 0 | E
[15 empty] | 0 | 0
114 | 31 g | 92 | SOTC115 | Termination of UG cables of 3.5 core 300 Sq.mm | Nos | 4000 | 12 | 48000 |  | 0 | 12 | 48000 | 12 | 48000 | 0 | 0 | E
[15 empty] | 0 | 0
115 | 31 h | 93 | SOTC116 | Earth work excavation of Trench laying of U.G cables up to 70 sqmm | Rmt | 1100 | 100 | 110000 |  | 0 | 100 | 110000 | 100 | 110000 | 0 | 0 | E
[15 empty] | 0 | 0
116 | 31 i | 94 | SOTC117 | Earth work excavation of Trench laying of U.G cables from 95 Sqmm | Rmt | 1150 | 100 | 115000 |  | 0 | 100 | 115000 | 100 | 115000 | 0 | 0 | E
[15 empty] | 0 | 0
117 | 31 j | 95 | SOTC118 | Laying of PVC armoured under ground cable up to 95 Sqmm on wall | Rmt | 125 | 200 | 25000 |  | 0 | 200 | 25000 | 200 | 25000 | 0 | 0 | E
[15 empty] | 0 | 0
118 | 31 k | 96 | SOTC119 | Laying of PVC armoured under ground cable from 120 Sq.mm to 400 Sqmm saddles on wall | Rmt | 270 | 700 | 189000 |  | 0 | 700 | 189000 | 700 | 189000 | 0 | 0 | E
[15 empty] | 0 | 0
119 | 32 a | 97 | SOTC120 | Supply, Transportation and Installation of 150mm x 50mm x 2mm thick hot dip GI perforated cable tray | Rmt | 1295 | 200 | 259000 |  | 0 | 200 | 259000 | 200 | 259000 | 0 | 0 | E
[15 empty] | 0 | 0
120 | 32 b | 98 | SOTC121 | Supply, Transportation and Installation of 300mm x 50mm x 2mm thick thick hot dip GI perforated cable tray | Rmt | 4500 | 100 | 450000 |  | 0 | 100 | 450000 | 100 | 450000 | 0 | 0 | E
[15 empty] | 0 | 0
121 | 33 a | 99 | SOTC122 | Supply, Transportation and installation of 10KVA / 312V DC on line UPS system | Nos | 400000 | 7 | 2800000 | 2 | 800000 | 9 | 3600000 | 9 | 3600000 | 0 | 0 | E
[15 empty] | 0 | 0
122 | 33 b | 100 | SOTC123 | Supply and fixing of 12V, 150 AH MF battery | Nos | 25000 | 182 | 4550000 | 52 | 1300000 | 234 | 5850000 | 234 | 5850000 | 0 | 0 | E
|  | 4: AE; 6: 25000; 13: 118; 14: 2950000; 15: 2950000; 16: 0 | E
123 | 33 c | 101 | SOTC124 | Supply and providing of UPS cum battery rack 20 batteries | Nos | 30000 | 7 | 210000 | 2 | 60000 | 9 | 270000 | 9 | 270000 | 0 | 0 | E
|  | 4: AE; 6: 30000; 13: 2; 14: 60000; 15: 60000; 16: 0 | E
124 | 33 d | 102 | SOTC125 | Supply, Transportation, Installation, Testing and commissioning of storage / Pressure type 5 Star rated water heater with ABS plastic body of 15 Ltrs | Nos | 16000 | 7 | 112000 |  | 0 | 7 | 112000 | 7 | 112000 | 0 | 0 | E
|  | 4: AE; 6: 16000; 13: 4; 14: 64000; 15: 64000; 16: 0 | E
125 | 34 | 103 | SOTC126 | 26 persons ICU bed cum passenger lift (1768 Kgs) G+8 Floors, 9 stops,9 Openings (Cost Includes amount for Construction of Shaft / Cladding from Ground to 8th Floor) | Nos | 10495000 | 1 | 10495000 |  | 0 | 1 | 10495000 | 1 | 10495000 | 0 | 0 | E
|  | 15: 0; 16: 0 | E
[10 empty] | PART-A |  | SUB TOTAL |  | 39927880 | 0
|  |  |  | Air Conditioning | [10 empty] | 0 | 0
126 | 35.1 | 104 | SOTC127 | 1.50 TR with , 18000 BTU/Hr High Wall mount Split Air Conditioners | Nos | 150000 | 6 | 900000 |  | 0 | 6 | 900000 | 6 | 900000 | 0 | 0 | AC
|  | 4: AE; 6: 150000; 13: 1; 14: 150000; 15: 150000; 16: 0 | AC
127 | 35.2 | 105 | SOTC128 | 2.0 TR with , 24000 BTU/Hr High Wall mount Split Air Conditioners | Nos | 210000 | 2 | 420000 |  | 0 | 2 | 420000 | 2 | 420000 | 0 | 0 | AC
|  | 4: AE; 6: 210000; 13: 4; 14: 840000; 15: 840000; 16: 0 | AC
128 | 35.3 | 106 | SOTC129 | Voltage stabilizer for 4 KVA maximum load | Nos | 7000 | 6 | 42000 |  | 0 | 6 | 42000 | 6 | 42000 | 0 | 0 | AC
|  | 4: AE; 6: 7000; 13: 1; 14: 7000; 15: 7000; 16: 0 | AC
129 | 35.4 | 107 | SOTC130 | Voltage stabilizer for 5 KVA maximum load | Nos | 8500 | 2 | 17000 |  | 0 | 2 | 17000 | 2 | 17000 | 0 | 0 | AC
|  | 4: AE; 6: 8500; 13: 4; 14: 34000; 15: 34000; 16: 0 | AC
130 | 35.5 | 216 | SOTC131 | Ductable Air Conditioners 11.0 TR with ISEER ≥ 4 | Nos | 1200000 | 1 | 1200000 |  | 0 | 1 | 1200000 | 1 | 1200000 | 0 | 0 | AC
[15 empty] | 0 | 0
131 | 35.6 | 217 | SOTC132 | Ductable Air Conditioners 8.5 TR with ISEER ≥ 4 | Nos | 1000000 | 2 | 2000000 |  | 0 | 2 | 2000000 | 2 | 2000000 | 0 | 0 | AC
|  | 4: AE; 6: 1000000; 13: 2; 14: 2000000; 15: 2000000; 16: 0 | AC
132 | 35.7 | 218 | SOTC133 | Ductable Air Conditioners 5.5 TR with ISEER ≥ 4 | Nos | 900000 | 1 | 900000 |  | 0 | 1 | 900000 | 1 | 900000 | 0 | 0 | AC
|  | 4: AE; 6: 900000; 13: 2; 14: 1800000; 15: 1800000; 16: 0 | AC
[10 empty] | PART-A |  | SUB TOTAL |  | 10310000 | 0
|  |  |  | Fire Fighting | [10 empty] | 0 | 0
133 | 36.2 | 108 | SOTC134 | Automatic Smoke Detection System | Job | 1425000 | 1 | 1425000 |  | 0 | 1 | 1425000 | 1 | 1425000 | 0 | 0 | FF
[15 empty] | 0 | 0
134 | 36.3 | 109 | SOTC135 | Automatic Fire Alarm System | Job | 1400000 | 1 | 1400000 |  | 0 | 1 | 1400000 | 1 | 1400000 | 0 | 0 | FF
[15 empty] | 0 | 0
135 | 36.4 | 219 | SOTC136 | Supply & Fixing of 4.5Kg, CO2 Type Fire Extinguisher. | Nos | 27000 | 6 | 162000 |  | 0 | 6 | 162000 | 6 | 162000 | 0 | 0 | FF
[15 empty] | 0 | 0
136 | 36.5 | 110 | SOTC137 | Supply and fixing of ABC stored pressure squeeze grip type fire extinguishers, 9 kg capacity. | Nos | 16000 | 6 | 96000 |  | 0 | 6 | 96000 | 6 | 96000 | 0 | 0 | FF
[15 empty] | 0 | 0
137 | 36.6 | 111 | SOTC138 | Supply and fixing of ABC Powder MAP 4 Kg Fire extinguisher | Nos | 11000 | 10 | 110000 |  | 0 | 10 | 110000 | 10 | 110000 | 0 | 0 | FF
[15 empty] | 0 | 0
138 | 36.7 | 112 | SOTC139 | Supply and fixing of 2 Kg Fire extinguisher Clean Agent | Nos | 22500 | 10 | 225000 |  | 0 | 10 | 225000 | 10 | 225000 | 0 | 0 | FF
[15 empty] | 0 | 0
139 | 36.8 | 113 | SOTC140 | Supply and fixing of Escape signage boards in Rigid Photo luminescent based glow | Nos | 2000 | 150 | 300000 |  | 0 | 150 | 300000 | 150 | 300000 | 0 | 0 | FF
[15 empty] | 0 | 0
140 | 36.9 | 220 | SOTC141 | Supply & Fixing of Powder Coated Fire Rated doors. | Sqm | 29000 | 6 | 174000 |  | 0 | 6 | 174000 | 6 | 174000 | 0 | 0 | FF
|  | 4: AE; 6: 29000; 13: 7.8; 14: 226200; 15: 226200; 16: 0 | FF
[10 empty] | PART-A |  | SUB TOTAL |  | 4118200 | 0
|  |  |  | ELV | [10 empty] | 0 | 0
141 | 37 | 221 | SOTC142 | Telephone & EPABX System | Job | 1000000 | 1 | 1000000 |  | 0 | 1 | 1000000 | 1 | 1000000 | 0 | 0 | ELV
[15 empty] | 0 | 0
142 | 38 | 114 | SOTC143 | Local Area Network (LAN) System | Job | 1250000 | 1 | 1250000 |  | 0 | 1 | 1250000 | 1 | 1250000 | 0 | 0 | ELV
[15 empty] | 0 | 0
143 | 39 | 115 | SOTC144 | Biometric Access Control System | Nos | 300000 | 2 | 600000 |  | 0 | 2 | 600000 | 2 | 600000 | 0 | 0 | ELV
|  | 4: AE; 6: 300000; 13: 1; 14: 300000; 15: 300000; 16: 0 | ELV
[10 empty] | PART-A |  | SUB TOTAL |  | 3150000 | 0
|  |  |  | Civil Works | [10 empty] | 0 | 0
144 |  | 116 | SOTC145 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Reinforced cement concrete) | Cum | 5400 | 10 | 54000 |  | 0 | 10 | 54000 | 10 | 54000 | 0 | 0 | C
[15 empty] | 0 | 0
145 |  | 117 | SOTC146 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Unreinforced cement concrete) | Cum | 4500 | 1.5 | 6750 |  | 0 | 1.5 | 6750 | 1.5 | 6750 | 0 | 0 | C
|  | 4: AE; 6: 4500; 13: 50.4015; 14: 226806.75; 15: 226806.75; 16: 0 | C
146 |  | 118 | SOTC147 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Brick Masonary) | Cum | 900 | 118 | 106200 |  | 0 | 118 | 106200 | 118 | 106200 | 0 | 0 | C
|  | 4: AE; 6: 900; 13: 34.691; 14: 31221.9; 15: 31221.9; 16: 0 | C
147 |  | 119 | SOTC148 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Kadapa slabs or shahabad stone slabs on sand bed) | Sqm | 630 | 25 | 15750 |  | 0 | 25 | 15750 | 25 | 15750 | 0 | 0 | C
|  | 4: AE; 6: 630; 13: 667.9265; 14: 420793.695; 15: 420793.695; 16: 0 | C
148 |  | 120 | SOTC149 | Dismantling doors, windows and clear storey windows, Ventilators etc., (wood or steel) shutters including Chowkhats, architraves,hold fasts and other attachments etc., and stacking them within 100m lead including charge etc., complete for finished item of work. (Not exceeding 3 sqm in area) | Nos | 1800 | 57 | 102600 |  | 0 | 57 | 102600 | 57 | 102600 | 0 | 0 | C
|  | 4: AE; 6: 1800; 13: 146; 14: 262800; 15: 262800; 16: 0 | C
149 |  | 121 | SOTC150 | Conveyance of un-useful excavated earth to a distance of 16 KM for disposal including hire charges of T and P, labour charges etc., complete for finished item of work. | Cum | 900 | 250 | 225000 |  | 0 | 250 | 225000 | 250 | 225000 | 0 | 0 | C
|  | 4: AE; 6: 900; 13: 64.769; 14: 58292.1; 15: 58292.1; 16: 0 | C
150 | 40 | 122 | SOTC151 | RCC M 25 grade design mix (For lintels) | Cum | 18900 | 3 | 56700 |  | 0 | 3 | 56700 | 3 | 56700 | 0 | 0 | C
|  | 4: AE; 6: 18900; 13: 0.17; 14: 3213; 15: 3213; 16: 0 | C
151 | 41 | 123 | SOTC152 | RCC M 20 grade design mix (50mm thick platforms) | Sqm | 1170 | 12 | 14040 |  | 0 | 12 | 14040 | 0 | 0 | 0 | 14040 | C
|  | 15: 0; 16: 0 | C
152 | 41 | 124 | SOTC153 | RCC M 20 grade design mix (25 mm thick Shelves) | Sqm | 900 | 12 | 10800 |  | 0 | 12 | 10800 | 0 | 0 | 0 | 10800 | C
|  | 15: 0; 16: 0 | C
153 | 42 | 125 | SOTC154 | Brick Masonry work in CM (1:6) prop in superstructure | Cum | 15300 | 3 | 45900 |  | 0 | 3 | 45900 | 3 | 45900 | 0 | 0 | C
|  | 4: AE; 6: 15300; 13: 108.951; 14: 1666950.3; 15: 1666950.3; 16: 0 | C
154 | 43 | 126 | SOTC155 | Reinforced Masonry for partition walls (100 mm thick) in CM (1:4) | Sqm | 2700 | 500 | 1350000 |  | 0 | 500 | 1350000 | 404.9325 | 1093317.75 | 0 | 256682.25 | C
|  | 15: 0; 16: 0 | C
155 | 44 | 127 | SOTC156 | PCC (1:3:6) nominal mix using 20mm size graded m/c (For bed blocks and hold fasts) | Cum | 9000 | 1.5 | 13500 |  | 0 | 1.5 | 13500 | 0 | 0 | 0 | 13500 | C
|  | 15: 0; 16: 0 | C
156 | 45 | 128 | SOTC157 | Filling with light weight concrete in Cement Concrete (1:5:10) proportion using brick jelly for low roofs | Cum | 7200 | 23 | 165600 |  | 0 | 23 | 165600 | 16.8651 | 121428.72 | 0 | 44171.28 | C
|  | 15: 0; 16: 0 | C
157 | 46 | 129 | SOTC158 | Thermo Mechanically Treated (Fe -500/500D/550D) for RCC works | MT | 126000 | 1.25 | 157500 |  | 0 | 1.25 | 157500 | 0.7686 | 96843.6 | 0 | 60656.4 | C
|  | 15: 0; 16: 0 | C
158 | 49 | 130 | SOTC159 | Plastering 12mm thick in two coats with base coat of 8mm thick in CM (1:6) and top coat of 4mm thick in CM (1:4). for Internal walls. | Sqm | 1224 | 1600 | 1958400 |  | 0 | 1600 | 1958400 | 1600 | 1958400 | 0 | 0 | C
|  | 4: AE; 6: 1224; 13: 548.804; 14: 671736.096; 15: 671736.096; 16: 0 | C
159 | 51 | 131 | SOTC160 | Impervious coat to exposed RCC roof slab surfaces (APSS No. 901 and 903) For Toilets | Sqm | 360 | 77.78 | 28000.8 |  | 0 | 77.78 | 28000.8 | 43.05 | 15498 | 0 | 12502.8 | C
|  | 15: 0; 16: 0 | C
160 | 92 | 222 | SOTC161 | Providing and applying Wall putty of White Cement or Polymer or Cement based of average 1 to 2 mm thickness over plastered surface to prepare the surface even and smooth after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, applying emery paper, Sand the surface, clean & wipe off loose dust, applying knifing paste filler by putty knife / muslin pad, air dry for 2 - 3 | Sqm | 270 | 4447 | 1200690 |  | 0 | 4447 | 1200690 | 1811.5335 | 489114.045 | 0 | 711575.955 | C
|  | 15: 0; 16: 0 | C
161 | 53 | 132 | SOTC162 | Flooring with non-skid full body ceramic floor tiles | Sqm | 1710 | 85 | 145350 |  | 0 | 85 | 145350 | 85 | 145350 | 0 | 0 | C
|  | 4: AE; 6: 1710; 13: 13.0805; 14: 22367.655; 15: 22367.655; 16: 0 | C
162 | 55 | 133 | SOTC163 | Dadooing to walls with glazed full body Porcelain wall tiles | Sqm | 1440 | 225 | 324000 |  | 0 | 225 | 324000 | 225 | 324000 | 0 | 0 | C
|  | 4: AE; 6: 1440; 13: 115; 14: 165600; 15: 165600; 16: 0 | C
163 | 56 | 134 | SOTC164 | Dadooing to walls with glazed full body Ceramic tiles | Sqm | 1440 | 350 | 504000 |  | 0 | 350 | 504000 | 270.2175 | 389113.2 | 0 | 114886.8 | C
|  | 15: 0; 16: 0 | C
164 | 57 | 135 | SOTC165 | Painting one coat water based cement primer of interior grade I and two coats of acrylic emulsion paint for ceiling and Walls | Sqm | 360 | 4447 | 1600920 |  | 0 | 4447 | 1600920 | 1372.014 | 493925.04 | 0 | 1106994.96 | C
|  | 15: 0; 16: 0 | C
165 | 59 | 136 | SOTC166 | Painting to new wood work | Sqm | 360 | 313 | 112680 |  | 0 | 313 | 112680 | 75 | 27000 | 0 | 85680 | C
|  | 15: 0; 16: 0 | C
166 | 60 | 137 | SOTC167 | Painting to new iron work | Sqm | 270 | 88 | 23760 |  | 0 | 88 | 23760 | 88 | 23760 | 0 | 0 | C
|  | 4: AE; 6: 270; 13: 38.42; 14: 10373.4; 15: 10373.4; 16: 0 | C
167 | 61 | 138 | SOTC168 | Two shutter cupboards | Sqm | 9000 | 100 | 900000 |  | 0 | 100 | 900000 | 0 | 0 | 0 | 900000 | C
|  | 15: 0; 16: 0 | C
168 | 64 | 139 | SOTC169 | UPVC Fixed Louvered Ventilator | Sqm | 12000 | 7 | 84000 |  | 0 | 7 | 84000 | 7 | 84000 | 0 | 0 | C
|  | 4: AE; 6: 12000; 13: 9.5165; 14: 114198; 15: 114198; 16: 0 | C
169 |  | 140 | SOTC170 | UPVC 3 track Sliding Windows | Sqm | 9000 | 15 | 135000 |  | 0 | 15 | 135000 | 15 | 135000 | 0 | 0 | C
|  | 4: AE; 6: 9000; 13: 30.276; 14: 272484; 15: 272484; 16: 0 | C
170 |  | 141 | SOTC171 | MS Grills to Windows | Sqm | 1800 | 150 | 270000 |  | 0 | 150 | 270000 | 126.42 | 227556 | 0 | 42444 | C
|  | 15: 0; 16: 0 | C
171 | 66 | 142 | SOTC172 | Flooring with 16 to 18 mm thick high polished granite stone slabs black colour for platforms (S.S.701 and special) | Sqm | 6300 | 50 | 315000 |  | 0 | 50 | 315000 | 50 | 315000 | 0 | 0 | C
|  | 14: 0; 15: 0; 16: 0 | C
172 | 67 | 143 | SOTC173 | Doors as per approved drawings with medium teak wood frame (1500mm x 2600mm) | Sqm | 6300 | 50 | 315000 |  | 0 | 50 | 315000 | 15.4 | 97020 | 0 | 217980 | C
|  | 15: 0; 16: 0 | C
173 | 68 | 144 | SOTC174 | Doors as per approved drawings with medium teak wood frame (1000mm x 2100mm) | Sqm | 7400 | 45 | 333000 |  | 0 | 45 | 333000 | 17.2 | 127280 | 0 | 205720 | C
|  | 15: 0; 16: 0 | C
174 | 69 | 145 | SOTC175 | Doors Shutters WPC(800mm x 2100mm) | Sqm | 5400 | 40 | 216000 |  | 0 | 40 | 216000 | 33.3795 | 180249.3 | 0 | 35750.7 | C
|  | 15: 0; 16: 0 | C
175 | 70 | 146 | SOTC176 | Scientific Doors with metal door frames and door shutters made of galvanize steel | Sqm | 18000 | 45 | 810000 |  | 0 | 45 | 810000 | 45 | 810000 | 0 | 0 | C
|  | 4: AE; 6: 18000; 13: 24.3; 14: 437400; 15: 437400; 16: 0 | C
176 | 71 | 147 | SOTC177 | False ceiling as per Technical specification | Sqm | 1800 | 1400 | 2520000 |  | 0 | 1400 | 2520000 | 750 | 1350000 | 0 | 1170000 | C
|  | 15: 0; 16: 0 | C
177 | 72 | 148 | SOTC178 | Vinyl flooring | Sqm | 3000 | 500 | 1500000 |  | 0 | 500 | 1500000 | 500 | 1500000 | 0 | 0 | C
|  | 4: AE; 6: 3000; 13: 164; 14: 492000; 15: 492000; 16: 0 | C
178 | 74 | 149 | SOTC179 | Impervious coat to exposed RCC roof slab surfacesof 20mm thick (APSS No. 901 and 903) | Sqm | 1260 | 350 | 441000 |  | 0 | 350 | 441000 | 0 | 0 | 0 | 441000 | C
|  | 15: 0; 16: 0 | C
179 | 63 | 233 | SOTC180 | Fixed Glass Window – 1200 x 1200 | Sqm | 5400 | 53.55 | 289170 |  | 0 | 53.55 | 289170 | 53.55 | 289170 | 0 | 0 | C
|  | 4: AE; 6: 5400; 13: 7.46; 14: 40284; 15: 40284; 16: 0 | C
180 | 95 | 223 | SOTC181 | Grouting the holes with neat cement slurry of 20mm dia with all required accessories of all materials etc., including cost & Conveyance of all labour Charges etc., complete finished item of work (*As per SSR2021-22 of S.NO:-8) | Nos | 180 | 500 | 90000 |  | 0 | 500 | 90000 | 0 | 0 | 0 | 90000 | C
|  | 15: 0; 16: 0 | C
181 | 96 | 224 | SOTC182 | Pressure grouting the drilled holes with neat cement slurry or with approved grout admixture using pump - excluding cost of drilling holes after fixing nozzles as technical specification approved by the department etc., including cost & Conveyance of all labour charges etc., complete finished item of work | Nos | 630 | 500 | 315000 |  | 0 | 500 | 315000 | 500 | 315000 | 0 | 0 | C
|  | 4: AE; 6: 630; 13: 632; 14: 398160; 15: 398160; 16: 0 | C
182 | 87 A | 234 | SOTC183 | Supply and fabricating,erecting and fixing inposition trusses of approved design with structural steel other than MS. | Kgs | 180 | 6500 | 1170000 |  | 0 | 6500 | 1170000 | 6500 | 1170000 | 0 | 0 | C
|  | 15: 0; 16: 0 | C
183 | 87 B | 150 | SOTC184 | Supply and fixing of pre painted Galvalume Trapezoidal Profile Roofing with 0.50mm Thickness. | Sqm | 1080 | 65 | 70200 |  | 0 | 65 | 70200 | 65 | 70200 | 0 | 0 | C
[15 empty] | 0 | 0
[10 empty] | PART-A |  | SUB TOTAL |  | 17755806.551 | 0
|  |  |  | Plumbing Works | [10 empty] | 0 | 0
184 | 75 | 225 | SOTC185 | 4" (101.6mm) multi floor trap with jali - UPVC/SWR | Nos | 270 | 25 | 6750 |  | 0 | 25 | 6750 | 25 | 6750 | 0 | 0 | P
|  | 4: AE; 6: 270; 13: 19; 14: 5130; 15: 5130; 16: 0 | P
185 | 76 | 151 | SOTC186 | 580mm x 440mm long Orissa pan white glazed Water Closet | Nos | 5400 | 4 | 21600 |  | 0 | 4 | 21600 | 4 | 21600 | 0 | 0 | P
|  | 15: 0; 16: 0 | P
186 | 77 | 152 | SOTC187 | European Water Closet of 1st quality | Nos | 6300 | 9 | 56700 |  | 0 | 9 | 56700 | 9 | 56700 | 0 | 0 | P
|  | 15: 0; 16: 0 | P
187 | 78 | 153 | SOTC188 | Indian make Flat Back Wash Hand Basin 1st quality | Nos | 3600 | 16 | 57600 |  | 0 | 16 | 57600 | 15 | 54000 | 0 | 3600 | P
|  | 15: 0; 16: 0 | P
188 | 79 | 154 | SOTC189 | CP finish brass soap dish | Nos | 1100 | 21 | 23100 |  | 0 | 21 | 23100 | 21 | 23100 | 0 | 0 | P
|  | 15: 0; 16: 0 | P
189 | 80 | 155 | SOTC190 | TV shape mirror with plastic frame of size 609.6mm x 457.2mm | Nos | 630 | 25 | 15750 |  | 0 | 25 | 15750 | 15 | 9450 | 0 | 6300 | P
|  | 15: 0; 16: 0 | P
190 | 81 | 156 | SOTC191 | 25.4mm dia , 609.6mm long aluminium anodized towel rods | Nos | 540 | 36 | 19440 |  | 0 | 36 | 19440 | 21 | 11340 | 0 | 8100 | P
|  | 15: 0; 16: 0 | P
191 | 82 | 156 | SOTC192 | 15 mm brass body CP finish bib tap of not less than 300 grams weight | Nos | 540 | 25 | 13500 |  | 0 | 25 | 13500 | 14 | 7560 | 0 | 5940 | P
|  | 15: 0; 16: 0 | P
192 | 87 C | 158 | SOTC193 | Self Closing Tap - Push Type | Nos | 720 | 25 | 18000 |  | 0 | 25 | 18000 | 15 | 10800 | 0 | 7200 | P
|  | 15: 0; 16: 0 | P
193 | 84 | 159 | SOTC194 | Chromium plated finish brass body quarter turn Bibcock cum Health Faucet | Nos | 3600 | 12 | 43200 |  | 0 | 12 | 43200 | 9 | 32400 | 0 | 10800 | P
|  | 14: 0; 15: 0; 16: 0 | P
194 | 85 | 160 | SOTC195 | Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings - 15.90mm OD pipe | Rmt | 270 | 55 | 14850 |  | 0 | 55 | 14850 | 55 | 14850 | 0 | 0 | P
|  | 4: AE; 6: 270; 13: 53.234; 14: 14373.18; 15: 14373.18; 16: 0 | P
195 | 85 | 161 | SOTC196 | Ashirvad/Ajay/Astral Flowguard or equivalent CPVC Pipes and Fittings - 22.20mm OD pipe | Rmt | 360 | 115 | 41400 |  | 0 | 115 | 41400 | 115 | 41400 | 0 | 0 | P
|  | 4: AE; 6: 360; 13: 14.7065; 14: 5294.34; 15: 5294.34; 16: 0 | P
196 | 85 | 162 | SOTC197 | Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings -28.60mm OD pipe | Rmt | 450 | 143 | 64350 |  | 0 | 143 | 64350 | 115.5 | 51975 | 0 | 12375 | P
|  | 15: 0; 16: 0 | P
197 | 86 | 163 | SOTC198 | Bronze Gate/ Globe valve - 25mm Nominal bore | Nos | 1440 | 15 | 21600 |  | 0 | 15 | 21600 | 15 | 21600 | 0 | 0 | P
|  | 4: AE; 6: 1440; 13: 5; 14: 7200; 15: 7200; 16: 0 | P
198 | 87 | 164 | SOTC199 | SWR PVC pipes (Prince/ Sudhakar/ Kisan/ Supreme or any ISI brand) 4 Kg/Sq.cm. - 75mmdia | Rmt | 450 | 145 | 65250 |  | 0 | 145 | 65250 | 84 | 37800 | 0 | 27450 | P
|  | 15: 0; 16: 0 | P
199 | 87 | 165 | SOTC200 | SWR PVC pipes (Prince/ Sudhakar/ Kisan/ Supreme or any ISI brand) 4 Kg/Sq.cm. -110mmdia | Rmt | 540 | 145 | 78300 |  | 0 | 145 | 78300 | 68.25 | 36855 | 0 | 41445 | P
|  | 15: 0; 16: 0 | P
200 | 90 | 226 | SOTC201 | Supplying and fixing15 mm nominal size 152.0 mm CP finish iron body shower rose 1st quality including cost and conveyance of all materials, labour charges , overheads & contractors profit for finished item of work in all floors. | Nos | 630 | 5 | 3150 |  | 0 | 5 | 3150 | 5 | 3150 | 0 | 0 | P
|  | 4: AE; 6: 630; 13: 1; 14: 630; 15: 630; 16: 0 | P
201 | 87 D | 166 | SOTC202 | Supply and Fixing of white glazed flat back bowl urinals | Nos | 2700 | 4 | 10800 |  | 0 | 4 | 10800 | 0 | 0 | 0 | 10800 | P
|  | 15: 0; 16: 0 | P
202 | 87 E | 227 | SOTC203 | Supply and fixing of 16mm to 20 mm thick ploished marbles slab partitions of size 4'0"*2'0" | Nos | 3600 | 10 | 36000 |  | 0 | 10 | 36000 | 0 | 0 | 0 | 36000 | P
|  | 15: 0; 16: 0 | P
[10 empty] | PART-A |  | SUB TOTAL |  | 473957.52 | 0
|  |  |  | Medical Gas Pipe Line | [10 empty] | 0 | 0
203 | 88.1 | 167 | SOTC204 | 28 mm dia. and 0.90 mm thick Copper Pipe Lines for Main lines | Rmt | 1750 | 700 | 1225000 |  | 0 | 700 | 1225000 | 700 | 1225000 | 0 | 0 | G
|  | 4: AE; 6: 1750; 13: 133; 14: 232750; 15: 232750; 16: 0 | G
204 | 88.1 | 168 | SOTC205 | 42 mm dia. and 1.20 mm thick Copper Pipe Lines for Main lines | Rmt | 2250 | 200 | 450000 |  | 0 | 200 | 450000 | 200 | 450000 | 0 | 0 | G
|  | 4: AE; 6: 2250; 13: 27; 14: 60750; 15: 60750; 16: 0 | G
205 | 88.1 | 169 | SOTC206 | 54 mm dia. and 1.20 mm thick Copper Pipe Lines for Main lines | Rmt | 2950 | 550 | 1622500 |  | 0 | 550 | 1622500 | 550 | 1622500 | 0 | 0 | G
|  | 4: AE; 6: 2950; 13: 14; 14: 41300; 15: 41300; 16: 0 | G
206 | 88.1 | 170 | SOTC207 | 12 mm dia. and 0.70 mm thick Copper Pipe Lines for distribution lines | Rmt | 650 | 320 | 208000 |  | 0 | 320 | 208000 | 320 | 208000 | 0 | 0 | G
|  | 4: AE; 6: 650; 13: 224; 14: 145600; 15: 145600; 16: 0 | G
207 | 88.1 | 171 | SOTC208 | 15 mm dia. and 0.90 mm thick Copper Pipe Lines for distribution lines | Rmt | 950 | 525 | 498750 |  | 0 | 525 | 498750 | 525 | 498750 | 0 | 0 | G
|  | 4: AE; 6: 950; 13: 232; 14: 220400; 15: 220400; 16: 0 | G
208 | 88.1 | 172 | SOTC209 | 22 mm dia. and 0.90 mm thick Copper Pipe Lines for distribution lines | Rmt | 1450 | 530 | 768500 |  | 0 | 530 | 768500 | 530 | 768500 | 0 | 0 | G
|  | 4: AE; 6: 1450; 13: 65; 14: 94250; 15: 94250; 16: 0 | G
209 | 88.2 | 228 | SOTC210 | 15 mm (1/2") Isolation Valves | Nos | 1500 | 40 | 60000 |  | 0 | 40 | 60000 | 31 | 46500 | 0 | 13500 | G
|  | 15: 0; 16: 0 | G
210 | 88.2 | 229 | SOTC211 | 22 mm (3/4") Isolation Valves | Nos | 2500 | 15 | 37500 |  | 0 | 15 | 37500 | 14 | 35000 | 0 | 2500 | G
|  | 15: 0; 16: 0 | G
211 | 88.2 | 173 | SOTC212 | 28 mm Isolation Valves | Nos | 3500 | 3 | 10500 | 2 | 7000 | 5 | 17500 | 5 | 17500 | 0 | 0 | G
|  | 4: AE; 6: 3500; 13: 4; 14: 14000; 15: 14000; 16: 0 | G
212 | 88.2 | 174 | SOTC213 | 42 mm Isolation Valves | Nos | 4500 | 2 | 9000 | 3 | 13500 | 5 | 22500 | 4 | 18000 | 0 | 4500 | G
|  | 15: 0; 16: 0 | G
213 | 88.2 | 175 | SOTC214 | 54 mm Isolation Valves | Nos | 5500 | 2 | 11000 | 1 | 5500 | 3 | 16500 | 3 | 16500 | 0 | 0 | G
|  | 4: AE; 6: 5500; 13: 7; 14: 38500; 15: 38500; 16: 0 | G
214 | 88.3 | 176 | SOTC215 | Gas Outlet Points with probes for Oxygen with S Brackets | Nos | 2850 | 189 | 538650 |  | 0 | 189 | 538650 | 189 | 538650 | 0 | 0 | G
|  | 4: AE; 6: 2850; 13: 17; 14: 48450; 15: 48450; 16: 0 | G
215 | 88.4 | 177 | SOTC216 | 2 Gas Digital Area Alarm Panels | Nos | 25000 | 2 | 50000 |  | 0 | 2 | 50000 | 0 | 0 | 0 | 50000 | G
|  | 15: 0; 16: 0 | G
216 | 88.4 | 178 | SOTC217 | 3 Gas Digital Area Alarm Panels | Nos | 30000 | 4 | 120000 |  | 0 | 4 | 120000 | 4 | 120000 | 0 | 0 | G
|  | 4: AE; 6: 30000; 13: 1; 14: 30000; 15: 30000; 16: 0 | G
217 | 88.4 | 179 | SOTC218 | 5 Gas Digital Area Alarm Panels | Nos | 40000 | 5 | 200000 | 1 | 40000 | 6 | 240000 | 0 | 0 | 0 | 240000 | G
|  | 15: 0; 16: 0 | G
218 | 88.4 | 180 | SOTC219 | Master Digital Alarm Panels | Nos | 50000 | 1 | 50000 |  | 0 | 1 | 50000 | 1 | 50000 | 0 | 0 | G
|  | 15: 0; 16: 0 | G
219 | 88.5 | 181 | SOTC220 | BPC Flow meter with Humidifier bottle and L adapter | Nos | 2250 | 27 | 60750 |  | 0 | 27 | 60750 | 27 | 60750 | 0 | 0 | G
|  | 4: AE; 6: 2250; 13: 16; 14: 36000; 15: 36000; 16: 0 | G
220 | 88.5 | 182 | SOTC221 | L Type Adapter for Oxygen Flow meters | Nos | 1250 | 27 | 33750 |  | 0 | 27 | 33750 | 27 | 33750 | 0 | 0 | G
|  | 15: 0; 16: 0 | G
221 | 88.5 | 183 | SOTC222 | Kit for conversion of Oxygen | Nos | 1650 | 27 | 44550 |  | 0 | 27 | 44550 | 18 | 29700 | 0 | 14850 | G
|  | 15: 0; 16: 0 | G
222 | 88.5 | 184 | SOTC223 | Suction Jars of 600 ml capacity | Nos | 3450 | 27 | 93150 |  | 0 | 27 | 93150 | 27 | 93150 | 0 | 0 | G
|  | 4: AE; 6: 3450; 13: 19; 14: 65550; 15: 65550; 16: 0 | G
223 | 88.5 | 185 | SOTC224 | Adapters for Vacuum | Nos | 750 | 27 | 20250 |  | 0 | 27 | 20250 | 27 | 20250 | 0 | 0 | G
|  | 15: 0; 16: 0 | G
224 | 88.5 | 186 | SOTC225 | Adapters for Air | Nos | 750 | 27 | 20250 |  | 0 | 27 | 20250 | 27 | 20250 | 0 | 0 | G
|  | 15: 0; 16: 0 | G
225 | 88.5 | 187 | SOTC226 | Adapters for Nitrous Oxide | Nos | 750 | 15 | 11250 |  | 0 | 15 | 11250 | 15 | 11250 | 0 | 0 | G
|  | 15: 0; 16: 0 | G
226 | 88.5 | 188 | SOTC227 | Vacuum Tube | Nos | 550 | 27 | 14850 | 58 | 31900 | 85 | 46750 | 85 | 46750 | 0 | 0 | G
|  | 4: AE; 6: 550; 13: 30; 14: 16500; 15: 16500; 16: 0 | G
227 | 88.6 | 189 | SOTC228 | Bed Head wall panel horizontal 1500 mm long single railing | Nos | 35000 | 27 | 945000 |  | 0 | 27 | 945000 | 27 | 945000 | 0 | 0 | G
|  | 4: AE; 6: 35000; 13: 4; 14: 140000; 15: 140000; 16: 0 | G
228 | 88.7 b | 190 | SOTC229 | Valve box -2 services | Nos | 9500 | 1 | 9500 |  | 0 | 1 | 9500 | 0 | 0 | 0 | 9500 | G
|  | 15: 0; 16: 0 | G
229 | 88.7 b | 191 | SOTC230 | Valve box -3 services | Nos | 14500 | 3 | 43500 |  | 0 | 3 | 43500 | 3 | 43500 | 0 | 0 | G
|  | 4: AE; 6: 14500; 13: 2; 14: 29000; 15: 29000; 16: 0 | G
230 | 88.7 b | 192 | SOTC231 | Valve box -6 services | Nos | 22500 | 1 | 22500 | 5 | 112500 | 6 | 135000 | 6 | 135000 | 0 | 0 | G
|  | 15: 0; 16: 0 | G
231 | 88.8 a | 193 | SOTC232 | 4 + 4 size of CO2 manifold System | Job | 40000 | 1 | 40000 | 1 | 40000 | 2 | 80000 | 2 | 80000 | 0 | 0 | G
|  | 4: AE; 6: 40000; 13: 1; 14: 40000; 15: 40000; 16: 0 | G
232 | 88.8 b | 194 | SOTC233 | 2 cylinder emergency manifold CO2 | Job | 14500 | 1 | 14500 | 1 | 14500 | 2 | 29000 | 2 | 29000 | 0 | 0 | G
|  | 15: 0; 16: 0 | G
233 | 88.8 c | 195 | SOTC234 | Fully Automatic CO2 Control System | Job | 185000 | 1 | 185000 | 1 | 185000 | 2 | 370000 | 2 | 370000 | 0 | 0 | G
|  | 15: 0; 16: 0 | G
234 | 88.9 | 237 | SOTC235 | Aneste Iwata Make TFS 150 C9 Model, Compresso Two stage, Motor 15 HP & 57.18 CFM, 60 CFM Air Dryer with 2000 Ltrs Receiver Twin System (For Air4, Air7) | Job | 1895000 | 1 | 1895000 |  | 0 | 1 | 1895000 | 1 | 1895000 | 0 | 0 | G
|  | 15: 0; 16: 0 | G
235 | 88.1 | 196 | SOTC236 | Supporting structure for MGPS lines with Ismb Columns, beams, MS angles, Flats and square rods | Job | 795000 | 1 | 795000 |  | 0 | 1 | 795000 | 1 | 795000 | 0 | 0 | G
|  | 15: 0; 16: 0 | G
236 | 88.11 | 197 | SOTC237 | 2x20 Oxygen Main manifold System | Job | 95000 | 1 | 95000 |  | 0 | 1 | 95000 | 1 | 95000 | 0 | 0 | G
|  | 15: 0; 16: 0 | G
237 | 88.12 | 198 | SOTC238 | Electrical Control Panel for MGPS | Job | 145000 | 1 | 145000 |  | 0 | 1 | 145000 | 1 | 145000 | 0 | 0 | G
|  | 15: 0; 16: 0 | G
238 | 88.13 | 238 | SOTC239 | Vaccum system Ingersoll Rand Make Model 15V x 10 Model with 5 HP Motor with 1000 Liters Reciever, Filters, Electricals, Etc Secretion Trap and Bacteria Filter | Job | 1495000 | 2 | 2990000 |  | 0 | 2 | 2990000 | 2 | 2990000 | 0 | 0 | G
|  | 15: 0; 16: 0 | G
239 |  | 235 | SOTC240 | Validation By Third Party Agency Charges per Each MOT | Each | 100000 | 4 | 400000 |  | 0 | 4 | 400000 | 4 | 400000 | 0 | 0 | G
|  | 4: AE; 6: 100000; 13: 5; 14: 500000; 15: 500000; 16: 0 | G
240 |  | 236 | SOTC241 | Anesthetic Gas Scavenging System (AGSS) | Job | 1213000 | 1 | 1213000 |  | 0 | 1 | 1213000 | 1 | 1213000 | 0 | 0 | G
[15 empty] | 0 | 0
[10 empty] | PART-A |  | SUB TOTAL |  | 16819300
241 |  |  |  | Electrical connections for 2 UPS | Job | 100000 |  |  | 1 | 100000 | 1 | 100000 | 0 |  | 0 | 100000 | E
[15 empty] | 0 | 0
242 |  |  |  | Double Arm Surgical Pendant | Nos | 1195000 | 0 | 0 | 6 | 7170000 | 6 | 7170000 | 6 | 7170000 | 0 | 0 | EQP
[15 empty] | 0 | 0
|  | 6: TOTAL; 8: 175773220.8; 10: 39541980; 12: 215315200.8; 14: 222626237.961; 15: 33207064.684; 16: 25896027.523 |  |  | 7311037.161
Sl.No |  |  |  | Item Description | UOM | Unit Rate (Rs.) | QTY | Amount (Rs.) |  |  | QTY | Amount (Rs.) | QTY | Amount (Rs.) | 0 | 0
|  |  |  | Civil Supplementary | [10 empty] | 0 | 0
1 |  | 4: Supply and installation of Under-deck Thermocol insulation sheets of 40 mm thick having more than 30 Kg/m3 density to ceiling by brush application of bituminous adhesive to the sheets and secured with screw along with washer at the centre of the sheet supported with GI wire running diagonally to the sheet of 2mm dia. (in ICUs & MOTs Integration Room); 5: Sqm; 6: 1014; 13: 262.74; 14: 266418.36; 15: 266418.36; 16: 0 | CS
2 |  | 4: Supply and placing of the Design Mix Plain Cement Concrete of M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Concrete Batching Plant with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials. (in 6 OTs); 5: Cum; 6: 11740; 13: 28.01; 14: 328837.4; 15: 328837.4; 16: 0 | CS
3 |  | 4: Supply and Laying of Floor leveller compund (self smoothing mortar) to level the surface, having bulk density not less than 2 Kg/l for a fresh mortor, compressive strength not less than 20 N/mm2, initial setting time not more than 40 minutes and offer a 25 minutes working time, The surface should be walkabe after 30 min of laying. (all rooms & corridors except OTs, TIRs and Sterile corridor); 5: Sqm; 6: 1460; 13: 882.44; 14: 1288362.4; 15: 1288362.4; 16: 0 | CS
4 |  | 4: Providing dadooing to walls with glazed full body ceramic wall tiles of size 800 x 1600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. (at Entrance); 5: Sqm; 6: 4665; 13: 119.385; 14: 556931.025; 15: 556931.025; 16: 0 | CS
5 |  | 4: Providing (1500 X 2100) single sliding door operated by elbow switches / foot switch as well as touchless sensor of 10mm thick toughened glass (Saint Gobin / Modi Guard) fixed in SS 304 grade 2 Track top channel of 45 mm (one track to hold fixed glass partition in position and second track with top rollers suitably angled to reduce resistance to movement to facilitate smooth sliding movement of the door). Single track bottom channel to be provided for fixed glass partition. Floor guide to be provided for smooth sliding of the door. Concealed door handle of (150 mm) to be provided in cutout on the sliding door for manual operation when required. All fittings provided should be of Titon /Ozone / Enox make in SS 304 - In TIRs; 5: Nos; 6: 270276; 13: 2; 14: 540552; 15: 540552; 16: 0 | CS
6 |  | 5: Sqm; 6: 3640; 13: 16; 14: 58240; 15: 58240; 16: 0 | CS
7 |  | 4: GI Powder Coated Sliding Doors (0.8mm shutter sheet thk & 1.2mm frame sheet thk with Single Rebate and Honeycomb Infill) Double Leaf Door 1200 x 2100mm with Accessories (Sliding Track for Double Door, Sliding Dead Lock Enox, Concealed Handles 100mm Ahlada, Flush Bolt 300mm Ahlada, SS304 Kick Plate upto 350mm ht, DG Clear Float Glass 350x750x6mm with Adhesive Tape & Silicon Sealant) (for change rooms to corridor entrance); 5: Nos; 6: 84133; 13: 1; 14: 84133; 15: 84133; 16: 0 | CS
8 |  | 4: Supply and installation of 50mm thick double skin modular wall Panels made of 0.8 mm thick powder coated GI on both the sides, with 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, flush on both sides with maximum allowable gap of 3- 4mm filled with food grade silicon sealant and placed on cold rolled galvanised bottom tracks with a recess to provide floor to wall coving flush with the wall panel. This includes all required harware for completion Panels to be covered with a protective film to avoid any damages during transportation and installation; 5: Sqm; 6: 7450; 13: 297.52; 14: 2216524; 15: 2216524; 16: 0 | CS
9 |  | 4: Supply and installation of 50mm thick double skin ceiling system made of 0.8 mm thick Powder Coated GI sheets on both sides, 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, panels flush towards room side with maximum allowable gap of 3-4mm at panel to panel joints filled with silicon sealant. Ceiling panels are suspended from the RCC slab by using concealed AL ceiling grid with tie rod and adjustable turn buckle arrangement etc. This includes all required hardware for completion. Panels to be covered with a protective film to avoid any damages during transportation and installation; 5: Sqm; 6: 7450; 13: 163.08; 14: 1214946; 15: 1214946; 16: 0 | CS
10 |  | 4: Acoustic Wall Panelling with framework consisting of 25mm high GI wall channels with fully knurled surface of 0.55mm thick bottom wedge of 80mm width, having two equal flanges of 26mm is anchored to GI studs of 50mm high. GI studs of 50mm High to be fixed to wall at 600mm centres, 25mm thick channels are then fixed perpendicular to the GI studs and suitable fixing channel is fixed to the cross channel to fix the panel to achieve overall air gap of 75mm from the wall and GI Clips for inside panel and Clips for border panel of 18mm to be fixed to the GI wall channel to achieve required shape. Secured arranging of polyester wool of – thickness/density, Prelam Board to be installed. 15mm thick Prelam perforated Wooden slat of required dia perforation & pitch is to be customised and then fixed to GI frame rigidly by using fixing channel fastened perpendicular to the cross channel with GI brackets. The boards shall be fixed to the GI frame with special cleats. (MOTs Integration Room); 5: Sqm; 6: 6350; 13: 110; 14: 698500; 15: 698500; 16: 0 | CS
11 |  | 4: Accooustic Ceiling Paneling with Perforated board Fine line Grid false ceiling using 11mm thick Perforated Board sheet tiles of size 595mm x 595mm fixing to steel precoated GI wall angle of size 25mm x 25mm x 0.70mm thick along the perimeter of ceiling screw fixed to brick work / partition at 610mm center to center and suspending the frame work using precoated GI Tee section (24mm x 38mm x 0.7mm) from soffit at 1220mm center to center fixed with GI Soffit Cleat, rawl plugs and steel expansion fasteners & connecting clip to the GI Tee section with 4mm dia GI rod with galvanised spring steel level clip of PVC unversal holding clips system at 1200mm center to center and Secured arranging of polyester wool of 50mm thick 1000 GSM, Prelam Board to be installed. 15mm thick Prelam perforated Wooden slat of required dia perforation & pitch is to be customised and then fixed to GI frame rigidly by using fixing channel fastened perpendicular to the cross channel with GI brackets. The boards shall be fixed to the GI frame with special cleats. (MOTs Integration Room); 5: Sqm; 6: 5700; 13: 62; 14: 353400; 15: 353400; 16: 0 | CS
12 |  | 4: Wooden Flooring with Engineered wood planks of 14mm thick (MOTs Integration Room); 5: Sqm; 6: 7300; 13: 65; 14: 474500; 15: 474500; 16: 0 | CS
13 |  | 4: Skirting for Wooden Flooring with Engineered wood planks of 14mm thick (MOTs Integration Room); 5: Rmt; 6: 900; 13: 40; 14: 36000; 15: 36000; 16: 0 | CS
14 |  | 4: 80% blockout Ruler Blinds for MOTs Integration Room Windows; 5: Nos; 6: 12000; 13: 3; 14: 36000; 15: 36000; 16: 0 | CS
15 |  | 4: Supply and installation of double pass RO system having 2 nos feed pumps of 1.5 HP with max flow of 4000 ltr/hr including construction of sand filter of dimensions (H=1650 mm, D=325 mm) with filter media as Quartz sand of SS vessel construction and Activated Carbon filter of dimensions (H= 1650mm) with filter media as Activated carbon (IV-600) of SS vessel construction, with 4 nos of spiral wound RO membrane of size 4 inch dia x 1 m length of make ION EXCHANGE (HYDROMEN) (or) equal, 2 nos UV system with service flow of 1000 ltr/hr (Before 2nd filter and after SS tank out-let) with PEX pipeline recirculation loop to avoid contamination in pipe to supply for 10 beds in Post ICU, 4 beds in Transplant ICU and 1 for each TIR.) Drinage outlet to be provided near each RO outlet.; 5: Job; 6: 6240000; 13: 1; 14: 6240000; 15: 6240000; 16: 0 | CS
16 |  | 4: Water Proofing of roof and peripheral walls of south west block, 8th floor, Gandhi Hospital which includes Dismantling of existing screed and lifting of debris to ground floor, Surface preparation and cracks treatment, Providing Angle fillet/taper of 75mm X 75mm with polymer modified mortor in the ratio of cement:sand:admixture (1:1.5:1.5) (Forsoc Nitobond SBR/M-Crete PC Bond @ 10% by weight of cement), Applying 1 coat of Forsoc Nitoproof WB Primer, Application of 2 coats of pitch free based liquid applied single component elastomeric waterproofing membrane (Forsoc Nito proof 600PF/BASF HLM5000), Laying 200 GSM Geotextile Fabric, Laying of 125mm Fiber Reinforced M20 grade protective concrete screed on terrace, Control joints treatment and External walls repair with window Frame-walls joints/Gaps treatment.; 5: Job; 6: 12611958; 13: 1; 14: 12611958; 15: 12611958; 16: 0 | CS
17 |  | 4: Supply of Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs with borders and design as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM (1:8) prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab , including neat cement slurry of honey like consistancy spread @ 3.3 kgs per Sqm. and jointed neately with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site (excluding cost of C.C. bed) including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in-charge etc.,and overheads & contractors profit complete for finished item of work. (APSS No.701 & 707).; 5: Sqm; 6: 2550; 13: 342; 14: 872100; 15: 872100; 16: 0 | CS
18 |  | 4: Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707); 5: Rmt; 6: 250; 13: 120; 14: 30000; 15: 30000; 16: 0 | CS
[10 empty] | SUBTOTAL |  | PART-B |  | 27907402.185
|  |  |  | MGPS Supplementary items | [10 empty] | 0 | 0
19 |  | 4: 4 Gas Digital Alarm Panels : 4 Gas Digital Alarm Panel consisting of atl necessary accessories ie Pressure sensors,reguIators,hand valves ,pressure gauges ecL(Oxygen, Nitrous oxide, Medical Air, Vacuum) (for TIRs); 5: Nos; 6: 42150; 13: 2; 14: 84300; 15: 84300; 16: 0 | GS
20 |  | 4: 6 Gas Digital Alarm Panele : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. (for OTs); 5: Nos; 6: 60008; 13: 6; 14: 360048; 15: 360048; 16: 0 | GS
21 |  | 4: Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. (for TIRs); 5: Nos; 6: 22201; 13: 2; 14: 44402; 15: 44402; 16: 0 | GS
22 |  | 4: 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen.; 5: Job; 6: 48103; 13: 1; 14: 48103; 15: 48103; 16: 0 | GS
23 |  | 4: Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED.; 5: Job; 6: 222013; 13: 1; 14: 222013; 15: 222013; 16: 0 | GS
24 |  | 4: 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide.; 5: Job; 6: 48103; 13: 1; 14: 48103; 15: 48103; 16: 0 | GS
25 |  | 4: 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide.; 5: Job; 6: 17401; 13: 1; 14: 17401; 15: 17401; 16: 0 | GS
26 |  | 4: Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041 C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED; 5: Job; 6: 222013; 13: 1; 14: 222013; 15: 222013; 16: 0 | GS
[10 empty] | SUBTOTAL |  | PART-B |  | 1046383 | 0
|  |  |  | ELV Supplementary Items | [10 empty] | 0 | 0
27 |  | 4: Recording in counselling room; 5: Job; 6: 155378; 13: 1; 14: 155378; 15: 155378; 16: 0 | ELVS
28 |  | 4: Local Area Network (LAN) System; 5: Job; 6: 460242; 13: 1; 14: 460242; 15: 460242; 16: 0 | ELVS
[10 empty] | SUBTOTAL |  | PART-B |  | 615620 | 0
|  |  |  | Electrical Supplementary | [10 empty] | 0 | 0
29 |  | 4: Supply, Transportation and installation of 20KVA / 312V DC on line UPS system (for emergency lighting in all rooms & Corridor except OTs & TIRs); 5: Nos; 6: 629358; 13: 2; 14: 1258716; 15: 1258716; 16: 0 | ES
30 |  | 4: 800 KVA Transformer OLTC for transformers with RTCC: Supply, Transportation, Installation, Testing and Commissioning of 800 KVA TRANSFORMER with all test reports. The Transformer shall be designed and manufactured as per IS:1180 OLTC with level-II with initial filling of oil as per IS 335-1993. 1000 A LT Breaker Kiosk - 01 No.The basic details of the Transformer are as under. Makes: Kirloskar / PETE / Esennar / Voltamp / Crompton / ABB / Schneider.; 5: Nos; 6: 4814994; 13: 1; 14: 4814994; 15: 4814994; 16: 0 | ES
31 |  | 4: 750 KVA Generator Set with AMF Control Panel Supply, Transportation, erection and commissioning (Excluding Foundation) of 3 Phase, 415, 50Hz, water cooled multi cylinder diesel generator set with alternator of 750 KVA output continuous rating directly coupled Engine and Alternator 750 KVA, 415 Volts with guard and mounted on a common base plate of Robust construction and complete with AMF panel having IP-52 protection, Acoustic Enclosure as per CPCB norms , sound absorbing material, t to restrict sound level up to 75 dB up to 1 Mtr distance and as per CPCB norms etc.; 5: Nos; 6: 9540000; 13: 1; 14: 9540000; 15: 9540000; 16: 0 | ES
[10 empty] | SUBTOTAL |  | PART-B |  | 15613710 | 0
|  |  |  | Medical Equipment Supplementary | [10 empty] | 0 | 0
32 |  | 4: Monitor Stand beside Bed in ICUs & TIRs; 5: Nos; 6: 6176; 13: 31; 14: 191456; 15: 191456; 16: 0 | EQPS
[10 empty] | SUBTOTAL |  | PART-B |  | 191456
[10 empty] | TOTAL |  | PART-B |  | 45374571.185 | 45374571.185 | 0
|  |  |  | GRAND TOTAL |  | PART (A+B) |  | 175773220.8 |  | 39541980 |  | 215315200.8 |  | 268000809.146 | 78581635.869 | 25896027.523
[12 empty] | TOTAL EXCESS |  | 52685608.346
[12 empty] | TCV Incl GST |  | 268000809.146
[12 empty] | BASIC VALUE |  | 227119329.7847
|  | DY. EXECUTIVE ENGINEER |  |  |  | EXECUTIVE ENGINEER | [7 empty] | SUPERINTENDENT ENGINEER
|  | TSMSIDC, MEDCHAL MALKAJGIRI |  |  |  | TSMSIDC, HYDERABAD DIVISION-1 | [7 empty] | TSMSIDC, HYDERABAD CIRCLE

## Sheet5 (hidden)
S.No | Description | Amount
1 | Terrace & Exterior walls water proofing | 12611958
2 | Double Pass Reverse Osmosis (RO) plant with recirculation loop | 6240000
3 | 800 KVA Transformer | 4814994
4 | 750 KVA DG set with AMF panel | 9540000
5 | O2 & N2O Manifold, Auto Control Systems & 4 & 6 Gas Digital Alarm Systems | 1046383
6 | 20 KVA/312V DC Online UPS System | 1258716
7 | Recording Counselling Room & Local Area Network | 615620
8 | Enhance the aesthetics at the entrance lobby | 556931
9 | Miscellaneous works: Works such as Under-deck thermocol insulation, PCC M 25 grade, Supply and laying of Floor leveler compound (self smoothing mortar), Monitor Stand beside Bed in ICUs & TIRs (31 Nos) & V-Board Partitions on top of false ceiling, GI powder coated sliding doors, PCGI wall & ceiling panels, acoustic wall & ceiling paneling, wooden flooring in MOT’s integration room, double charged vitrified tiles etc. are required as per the site condition. | 8689969
45374571

## seignorage (hidden)
S.No | Item S.No | Item Code | Item Name | UOM | QTY | QTY |  |  | Co-efficients |  |  | Rates |  |  | Amount |  |  | Total Amount
[6 empty] | Sand (QTY) | Metal (QTY) | Brick (QTY) | Sand | Metal | Bricks | Sand Rate | Metal Rate | Brick Rate | Sand Amount | Metal Amount | Brick Amount
1 | 116 | SOTC145 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Reinforced cement concrete) | Cum | 10 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
2 | 117 | SOTC146 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Unreinforced cement concrete) | Cum | 51.9015 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
3 | 118 | SOTC147 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Brick Masonary) | Cum | 152.691 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
4 | 119 | SOTC148 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Kadapa slabs or shahabad stone slabs on sand bed) | Sqm | 692.9265 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
5 | 120 | SOTC149 | Dismantling doors, windows and clear storey windows, Ventilators etc., (wood or steel) shutters including Chowkhats, architraves,hold fasts and other attachments etc., and stacking them within 100m lead including charge etc., complete for finished item of work. (Not exceeding 3 sqm in area) | Nos | 203 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
6 | 121 | SOTC150 | Conveyance of un-useful excavated earth to a distance of 16 KM for disposal including hire charges of T and P, labour charges etc., complete for finished item of work. | Cum | 314.769 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
7 | 122 | SOTC151 | RCC M 25 grade design mix (For lintels) | Cum | 3.171 | 0.79275 | 1.5855 |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 13.9524 | 95.13 | 0 | 109.0824
8 | 123 | SOTC152 | RCC M 20 grade design mix (50mm thick platforms) | Sqm | 0 | 0 | 0 |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
9 | 124 | SOTC153 | RCC M 20 grade design mix (25 mm thick Shelves) | Sqm | 0 | 0 | 0 |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
10 | 125 | SOTC154 | Brick Masonry work in CM (1:6) prop in superstructure | Cum | 111.951 | 14.238 | 0 | 7945 | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 250.5888 | 0 | 244.0704 | 494.6592
11 | 126 | SOTC155 | Reinforced Masonry for partition walls (100 mm thick) in CM (1:4) | Sqm | 404.9325 | 4.8 |  | 2874 | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 84.48 | 0 | 88.2893 | 172.7693
12 | 127 | SOTC156 | PCC (1:3:6) nominal mix using 20mm size graded m/c (For bed blocks and hold fasts) (OTs screed) | Cum | 0 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
13 | 128 | SOTC157 | Filling with light weight concrete in Cement Concrete (1:5:10) proportion using brick jelly for low roofs | Cum | 16.8651 | 5.2703 |  | 6850 | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 92.7581 | 0 | 210.432 | 303.1901
14 | 129 | SOTC158 | Thermo Mechanically Treated (Fe -500/500D/550D) for RCC works | MT | 0.7686 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
15 | 130 | SOTC159 | Plastering 12mm thick in two coats with base coat of 8mm thick in CM (1:6) and top coat of 4mm thick in CM (1:4). for Internal walls. | Sqm | 2148.804 | 28.7424 |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 505.8663 | 0 | 0 | 505.8663
16 | 131 | SOTC160 | Impervious coat to exposed RCC roof slab surfaces (APSS No. 901 and 903) For Toilets | Sqm | 43.05 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
17 | 222 | SOTC161 | Providing and applying Wall putty of White Cement or Polymer or Cement based of average 1 to 2 mm thickness over plastered surface to prepare the surface even and smooth after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, applying emery paper, Sand the surface, clean & wipe off loose dust, applying knifing paste filler by putty knife / muslin pad, air dry for 2 - 3 | Sqm | 1811.5335 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
18 | 132 | SOTC162 | Flooring with non-skid full body ceramic floor tiles | Sqm | 98.0805 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
19 | 133 | SOTC163 | Dadooing to walls with glazed full body Porcelain wall tiles | Sqm | 340 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
20 | 134 | SOTC164 | Dadooing to walls with glazed full body Ceramic tiles | Sqm | 270.2175 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
21 | 135 | SOTC165 | Painting one coat water based cement primer of interior grade I and two coats of acrylic emulsion paint for ceiling and Walls | Sqm | 1372.014 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
22 | 136 | SOTC166 | Painting to new wood work | Sqm | 75 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
23 | 137 | SOTC167 | Painting to new iron work | Sqm | 126.42 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
24 | 138 | SOTC168 | Two shutter cupboards | Sqm | 0 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
25 | 139 | SOTC169 | UPVC Fixed Louvered Ventilator | Sqm | 16.5165 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
26 | 140 | SOTC170 | UPVC 3 track Sliding Windows | Sqm | 45.276 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
27 | 141 | SOTC171 | MS Grills to Windows | Sqm | 126.42 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
28 | 142 | SOTC172 | Flooring with 16 to 18 mm thick high polished granite stone slabs black colour for platforms (S.S.701 and special) | Sqm | 422 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
29 | 143 | SOTC173 | Doors as per approved drawings with medium teak wood frame (1500mm x 2600mm) | Sqm | 15.4 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
30 | 144 | SOTC174 | Doors as per approved drawings with medium teak wood frame (1000mm x 2100mm) | Sqm | 17.2 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
31 | 145 | SOTC175 | Doors Shutters WPC(800mm x 2100mm) | Sqm | 33.3795 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
32 | 146 | SOTC176 | Scientific Doors with metal door frames and door shutters made of galvanize steel | Sqm | 77.65 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
33 | 147 | SOTC177 | False ceiling as per Technical specification | Sqm | 750 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
34 | 148 | SOTC178 | Vinyl flooring | Sqm | 664 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
35 | 149 | SOTC179 | Impervious coat to exposed RCC roof slab surfacesof 20mm thick (APSS No. 901 and 903) | Sqm | 0 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
36 | 233 | SOTC180 | Fixed Glass Window – 1200 x 1200 | Sqm | 61.01 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
37 | 223 | SOTC181 | Grouting the holes with neat cement slurry of 20mm dia with all required accessories of all materials etc., including cost & Conveyance of all labour Charges etc., complete finished item of work (*As per SSR2021-22 of S.NO:-8) | Nos | 0 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
38 | 224 | SOTC182 | Pressure grouting the drilled holes with neat cement slurry or with approved grout admixture using pump - excluding cost of drilling holes after fixing nozzles as technical specification approved by the department etc., including cost & Conveyance of all labour charges etc., complete finished item of work | Nos | 1132 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
39 | 234 | SOTC183 | Supply and fabricating,erecting and fixing inposition trusses of approved design with structural steel other than MS. | Kgs | 6500 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
40 | 150 | SOTC184 | Supply and fixing of pre painted Galvalume Trapezoidal Profile Roofing with 0.50mm Thickness. | Sqm | 65 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
41 |  |  | Supply and installation of Under-deck Thermocol insulation sheets of 40 mm thick having more than 30 Kg/m3 density to ceiling by brush application of bituminous adhesive to the sheets and secured with screw along with washer at the centre of the sheet supported with GI wire running diagonally to the sheet of 2mm dia. (in ICUs & MOTs Integration Room) | Sqm | 262.74 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
42 |  |  | Supply and placing of the Design Mix Plain Cement Concrete of M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Concrete Batching Plant with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials. (in 6 OTs) | Cum | 28.01 | 7.0025 | 14.005 |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 123.244 | 840.3 | 0 | 963.544
43 |  |  | Supply and Laying of Floor leveller compund (self smoothing mortar) to level the surface, having bulk density not less than 2 Kg/l for a fresh mortor, compressive strength not less than 20 N/mm2, initial setting time not more than 40 minutes and offer a 25 minutes working time, The surface should be walkabe after 30 min of laying. (all rooms & corridors except OTs, TIRs and Sterile corridor) | Sqm | 882.44 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
44 |  |  | Providing dadooing to walls with glazed full body ceramic wall tiles of size 800 x 1600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. (at Entrance) | Sqm | 119.385 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
45 |  |  | Providing (1500 X 2100) single sliding door operated by elbow switches / foot switch as well as touchless sensor of 10mm thick toughened glass (Saint Gobin / Modi Guard) fixed in SS 304 grade 2 Track top channel of 45 mm (one track to hold fixed glass partition in position and second track with top rollers suitably angled to reduce resistance to movement to facilitate smooth sliding movement of the door). Single track bottom channel to be provided for fixed glass partition. Floor guide to be provided for smooth sliding of the door. Concealed door handle of (150 mm) to be provided in cutout on the sliding door for manual operation when required. All fittings provided should be of Titon /Ozone / Enox make in SS 304 - In TIRs | Nos | 2 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
46 |  |  | V-Board Partitions on top of false ceiling for partitioning of sterile corridor and non-sterile corridor (for dividing corridors into zones above ceiling) | Sqm | 16 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
47 |  |  | GI Powder Coated Sliding Doors (0.8mm shutter sheet thk & 1.2mm frame sheet thk with Single Rebate and Honeycomb Infill) Double Leaf Door 1200 x 2100mm with Accessories (Sliding Track for Double Door, Sliding Dead Lock Enox, Concealed Handles 100mm Ahlada, Flush Bolt 300mm Ahlada, SS304 Kick Plate upto 350mm ht, DG Clear Float Glass 350x750x6mm with Adhesive Tape & Silicon Sealant) (for change rooms to corridor entrance) | Nos | 1 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
48 |  |  | Supply and installation of 50mm thick double skin modular wall Panels made of 0.8 mm thick powder coated GI on both the sides, with 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, flush on both sides with maximum allowable gap of 3- 4mm filled with food grade silicon sealant and placed on cold rolled galvanised bottom tracks with a recess to provide floor to wall coving flush with the wall panel. This includes all required harware for completion Panels to be covered with a protective film to avoid any damages during transportation and installation | Sqm | 297.52 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
49 |  |  | Supply and installation of 50mm thick double skin ceiling system made of 0.8 mm thick Powder Coated GI sheets on both sides, 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, panels flush towards room side with maximum allowable gap of 3-4mm at panel to panel joints filled with silicon sealant. Ceiling panels are suspended from the RCC slab by using concealed AL ceiling grid with tie rod and adjustable turn buckle arrangement etc. This includes all required hardware for completion. Panels to be covered with a protective film to avoid any damages during transportation and installation | Sqm | 163.08 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
50 |  |  | Acoustic Wall Panelling with framework consisting of 25mm high GI wall channels with fully knurled surface of 0.55mm thick bottom wedge of 80mm width, having two equal flanges of 26mm is anchored to GI studs of 50mm high. GI studs of 50mm High to be fixed to wall at 600mm centres, 25mm thick channels are then fixed perpendicular to the GI studs and suitable fixing channel is fixed to the cross channel to fix the panel to achieve overall air gap of 75mm from the wall and GI Clips for inside panel and Clips for border panel of 18mm to be fixed to the GI wall channel to achieve required shape. Secured arranging of polyester wool of – thickness/density, Prelam Board to be installed. 15mm thick Prelam perforated Wooden slat of required dia perforation & pitch is to be customised and then fixed to GI frame rigidly by using fixing channel fastened perpendicular to the cross channel with GI brackets. The boards shall be fixed to the GI frame with special cleats. (MOTs Integration Room) | Sqm | 110 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
51 |  |  | Accooustic Ceiling Paneling with Perforated board Fine line Grid false ceiling using 11mm thick Perforated Board sheet tiles of size 595mm x 595mm fixing to steel precoated GI wall angle of size 25mm x 25mm x 0.70mm thick along the perimeter of ceiling screw fixed to brick work / partition at 610mm center to center and suspending the frame work using precoated GI Tee section (24mm x 38mm x 0.7mm) from soffit at 1220mm center to center fixed with GI Soffit Cleat, rawl plugs and steel expansion fasteners & connecting clip to the GI Tee section with 4mm dia GI rod with galvanised spring steel level clip of PVC unversal holding clips system at 1200mm center to center and Secured arranging of polyester wool of 50mm thick 1000 GSM, Prelam Board to be installed. 15mm thick Prelam perforated Wooden slat of required dia perforation & pitch is to be customised and then fixed to GI frame rigidly by using fixing channel fastened perpendicular to the cross channel with GI brackets. The boards shall be fixed to the GI frame with special cleats. (MOTs Integration Room) | Sqm | 62 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
52 |  |  | Wooden Flooring with Engineered wood planks of 14mm thick (MOTs Integration Room) | Sqm | 65 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
53 |  |  | Skirting for Wooden Flooring with Engineered wood planks of 14mm thick (MOTs Integration Room) | Rmt | 40 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
54 |  |  | 80% blockout Ruler Blinds for MOTs Integration Room Windows | Nos | 3 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
55 |  |  | Supply and installation of double pass RO system with raw water tank capacity of 5000 ltr plastic tank having 2 nos feed pumps of 1.5 HP with max flow of 9000 ltr/hr including construction of sand filter of dimensions (H=1665 mm, D=325 mm) with filter media as Quartz sand of SS vessel construction and Activated Carbon filter of dimensions (H= 1665mm) with filter media as Activated carbon (IV-600) of SS vessel construction, with 4 nos of spiral wound RO membrane of size 8 inch dia x 1 m length of make G.E OSMONICS (or) HYDRAUNAUTICS, 4 nos UV system with service flow of 1500 ltr/hr (Before Snd filter and after SS tank out-let) with cPVC pipeline recirculation loop to avoid contamination in pipe to supply for 10 beds in Post ICU, 4 beds in Transplant ICU and 1 for each TIR.) Drinage outlet to be provided near each RO outlet. | Job | 1 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
56 |  |  | Water Proofing of roof and peripheral walls of south west block, 8th floor, Gandhi Hospital which includes Dismantling of existing screed and lifting of debris to ground floor, Surface preparation and cracks treatment, Providing Angle fillet/taper of 75mm X 75mm with polymer modified mortor in the ratio of cement:sand:admixture (1:1.5:1.5) (Forsoc Nitobond SBR/M-Crete PC Bond @ 10% by weight of cement), Applying 1 coat of Forsoc Nitoproof WB Primer, Application of 2 coats of pitch free based liquid applied single component elastomeric waterproofing membrane (Forsoc Nito proof 600PF/BASF HLM5000), Laying 200 GSM Geotextile Fabric, Laying of 125mm Fiber Reinforced M20 grade protective concrete screed on terrace, Control joints treatment and External walls repair with window Frame-walls joints/Gaps treatment. | Job | 1 |  |  |  | 0.4 | 0.8 | 0.512 | 44 | 75 | 0.06 | 0 | 0 | 0 | 0
GRAND TOTAL | [17 empty] | 2549.1112
404.93
40.493
0.014091
2873.6782
0.012
34.4841
6.0089
1.2018
[5 empty] | sand | 4.8071

## RE (hidden)
REVISED ESTIMATE OF SOTC 8TH FLOOR, SOUTH-WEST BLOCK, GANDHI HOSPITAL
S.No | Tech. Spec Cl. No in TED | Item S.No | Item Code | Item Name |  |  | As Per Agreement (with 4 Ots) |  | Additional Sanction fot 2 Ots |  | Total (6 Ots) |  | As Per Work Done/To Be Done
[5 empty] | UOM | Unit Rate (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.)
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
|  | 4: Modular Operation Theatres |  |  |  |  | Workdone Amount | Sanction Amount | Excess Amount | Less Amount | as per agreement | as per additional 2 Ots
1 | 1 | 1 | SOTC001 | Stainless Steel Pre-fabricated Wall panels. (MOTs & MOT Corridor) - Wall panels | Sqm | 15010 | 400 | 6004000 | 350 | 5253500 | 750 | 11257500 | 491.9486 | 7384148.486 | C | C | CIVIL | 1 | 43223650.441 | 48053380.8 | #REF! | #REF! | 40701300.8 | 7352080
[16 empty] | E | ELECTRICAL | 3 | 49845130 | 50777380 | #REF! | #REF! | 45337380 | 5440000
2 | 1 | 199 | SOTC002 | Stainless Steel Pre-fabricated Ceiling panels In MOTs & MOTs Corridor | Sqm | 15010 | 385 | 5778850 | 78 | 1170780 | 463 | 6949630 | 263.165 | 3950106.65 | C | ELV |  | 5 | 3150000 | 2850000 | #REF! | #REF! | 2850000 | 0
[16 empty] | FF | FIRE FIGHTING | 7 | 4118200 | 3892000 | #REF! | #REF! | 3892000 | 0
3 | 1.5 | 2 | SOTC003 | Dynamic Hatch Box | Nos | 295000 | 2 | 590000 | 1 | 295000 | 3 | 885000 | 0 | 0 | EQP | EQP | EQUIPMENT | 8 | 72882500 | 67867500 | #REF! | #REF! | 46177500 | 21690000
[16 empty] | AC | AIR CONDITIONING | 10 | 32960000 | 25714000 | #REF! | #REF! | 21104000 | 4610000
4 | 2.1 | 3 | SOTC004 | Electro conductive Flooring inside MOTs | Sqm | 4035 | 160 | 645600 | 80 | 322800 | 240 | 968400 | 217.7802 | 878743.107 | C | P | PLUMBING | 11 | 499157.52 | 611340 | #REF! | #REF! | 611340 | 0
[16 empty] | G | MGPS | 12 | 16967800 | 15549600 | #REF! | #REF! | 15099700 | 449900
5 | 2.2 | 4 | SOTC005 | Flooring with Vinyl Sheets In MOT Corridor | Sqm | 3750 | 175 | 656250 | 50 | 187500 | 225 | 843750 | 87.0329 | 326373.525 | C | CS | CIVIL SUPPLIMENTAL | 2 | 27907402.185 | 0 | #REF! | #REF! | 0 | 0
[16 empty] | ES | ELECTRICAL SUPPLIMENTAL | 4 | 15613710 | 0 | #REF! | #REF! | 0 | 0
6 | 3 | 5 | SOTC006 | Uni Directional Ceiling Laminar Airflow Systems | Nos | 465000 | 4 | 1860000 | 2 | 930000 | 6 | 2790000 | 6 | 2790000 | AC | ELVS | ELV SUPPLIMENTAL | 6 | 615620 | 0 | #REF! | #REF! | 0 | 0
[16 empty] | EQPS | EQUIPMENT SUPPLIMENTAL | 9 | 191456 | 0 | #REF! | #REF! | 0 | 0
7 | 3.1 | 6 | SOTC007 | Air Handling Units (AHUs) 11 TR | Nos | 1495000 | 4 | 5980000 | 2 | 2990000 | 6 | 8970000 | 6 | 8970000 | AC | GS | MGPS SUPPLIMENTAL | 13 | 1046383 | 0 | #REF! | #REF! | 0 | 0
8 | 3.2 | 7 | SOTC008 | Condensing Units | Nos | 345000 | 4 | 1380000 | 2 | 690000 | 6 | 2070000 | 6 | 2070000 | AC
|  | 4: AE; 6: 345000; 13: 4; 14: 1380000 | AC
9 | 4 | 8 | SOTC009 | Pressure Relief Dampers | Nos | 22500 | 4 | 90000 | 2 | 45000 | 6 | 135000 | 6 | 135000 | EQP
10 | 5.1 | 9 | SOTC010 | Single arm Anesthesia Pendants (Imported) | Nos | 1195000 | 4 | 4780000 | 2 | 2390000 | 6 | 7170000 | 6 | 7170000 | EQP
11 | 5.2 | 10 | SOTC011 | Triple Dome Ceiling OT LED Lights (Imported) | Nos | 4750000 | 2 | 9500000 |  | 0 | 2 | 9500000 | 2 | 9500000 | EQP
|  | 4: AE; 6: 4750000; 13: 2; 14: 9500000 | EQP
12 | 5.3 | 11 | SOTC012 | Double Dome Ceiling OT LED Lights (Imported) | Nos | 3550000 | 2 | 7100000 | 2 | 7100000 | 4 | 14200000 | 2 | 7100000 | EQP
13 | 5.4 | 12 | SOTC013 | Detachable Hi Definition Cameras in Triple Dome Ceiling OT Lights | Nos | 995000 | 2 | 1990000 | 1 | 995000 | 3 | 2985000 | 3 | 2985000 | EQP
|  | 4: AE; 13: 1; 14: 995000 | EQP
14 | 91 | 13 | SOTC014 | Ceiling/Wall mounted CCTV Room Camera | Nos | 22500 | 4 | 90000 | 2 | 45000 | 6 | 135000 | 6 | 135000 | E
15 | 6 | 14 | SOTC015 | LED Peripheral Lights cum clean room (OT) luminaries | Nos | 18750 | 62 | 1162500 | 40 | 750000 | 102 | 1912500 | 102 | 1912500 | E
|  | 4: AE; 6: 18750; 13: 5; 14: 93750 | E
16 | 7 | 239 | SOTC016 | View Window with Motorised Blinds of 1 Mt Length & 1 Mt Height | Nos | 115000 | 7 | 805000 | 2 | 230000 | 9 | 1035000 | 9 | 1035000 | EQP
|  | 4: AE; 6: 115000; 13: 5; 14: 575000 | EQP
17 | 8 | 15 | SOTC017 | Hermetically Sealed Doors (1.80mt x 2.10 mt) | Nos | 115000 | 4 | 460000 | 2 | 230000 | 6 | 690000 | 6 | 690000 | C
|  | 4: AE; 6: 115000; 13: 3; 14: 345000 | C
18 | 8 | 240 | SOTC018 | (1.50mt x 2.10 mt) Sliding Automatic Sliding Doors with View Windoy of 1 Mt x 1 Mt | Nos | 525000 | 2 | 1050000 |  | 0 | 2 | 1050000 | 2 | 1050000 | C
19 | 10 | 16 | SOTC019 | Storage Units | Nos | 75000 | 4 | 300000 | 2 | 150000 | 6 | 450000 | 6 | 450000 | C
20 | 11 | 17 | SOTC020 | Writing Board (List Board) | Nos | 18750 | 4 | 75000 | 2 | 37500 | 6 | 112500 | 6 | 112500 | C
21 | 12 | 18 | SOTC021 | X-Ray CT Scan LED viewing Screen | Nos | 37500 | 4 | 150000 | 2 | 75000 | 6 | 225000 | 6 | 225000 | EQP
22 | 13 | 19 | SOTC022 | Touch Screen Surgeon Control Panels | Nos | 385000 | 4 | 1540000 | 2 | 770000 | 6 | 2310000 | 6 | 2310000 | EQP
|  | 4: AE; 6: 385000; 13: 3; 14: 1155000 | EQP
23 | 14 | 20 | SOTC023 | 3-Bay Scrub Stations/Sinks | Nos | 368750 | 2 | 737500 |  | 0 | 2 | 737500 | 2 | 737500 | EQP
|  | 4: AE; 6: 368750; 13: 2; 14: 737500 | EQP
24 | 16 | 21 | SOTC024 | Video and Image Management system | Nos | 8000000 | 1 | 8000000 |  | 0 | 1 | 8000000 | 1 | 8000000 | EQP
25 | 16.1 | 22 | SOTC025 | Medical Grade Monitors 32 inch 4 K Resolution | Nos | 1295000 | 4 | 5180000 | 2 | 2590000 | 6 | 7770000 | 6 | 7770000 | EQP
26 | 16.2 | 23 | SOTC026 | Wall mounted large screen display 55 inch (Commercial Grade) | Nos | 495000 | 2 | 990000 |  | 0 | 2 | 990000 | 2 | 990000 | EQP
27 | 16.3 & 16.4 | 24 | SOTC027 | Cable connections for integration within MOTs and with Workshop Projector Hall, Networks with OFC Cable | Job | 997500 | 4 | 3990000 | 2 | 1995000 | 6 | 5985000 | 6 | 5985000 | E
28 | 16.5 | 25 | SOTC028 | Wireless Microphone | Nos | 255000 | 1 | 255000 |  | 0 | 1 | 255000 | 1 | 255000 | EQP
29 | 16.6 | 26 | SOTC029 | Digital mixer Amplifier | Nos | 245000 | 1 | 245000 |  | 0 | 1 | 245000 | 1 | 245000 | EQP
30 | 16.7 | 27 | SOTC030 | Ceiling Mounted Speakers | Nos | 15000 | 4 | 60000 | 2 | 30000 | 6 | 90000 | 6 | 90000 | EQP
31 | 16.8 | 28 | SOTC031 | Video Conferencing System | Nos | 1195000 | 1 | 1195000 |  | 0 | 1 | 1195000 | 1 | 1195000 | EQP
32 | 17.1 | 29 | SOTC032 | Home Theatre Power Conditioner, 230 V | Nos | 145000 | 1 | 145000 |  | 0 | 1 | 145000 | 1 | 145000 | EQP
33 | 17.2 | 30 | SOTC033 | Amplifier (8 Channel) | Nos | 245000 | 1 | 245000 |  | 0 | 1 | 245000 | 1 | 245000 | EQP
34 | 17.3 | 31 | SOTC034 | HiFi Active Sub Woofer | Nos | 50000 | 1 | 50000 |  | 0 | 1 | 50000 | 1 | 50000 | EQP
35 | 17.5 | 32 | SOTC035 | 4K Laser Projection TV | Nos | 1495000 | 1 | 1495000 |  | 0 | 1 | 1495000 | 1 | 1495000 | EQP
36 | 17.6 & 17.7 | 200 | SOTC036 | Equalization & Loud Speaker Control System | Nos | 40000 | 1 | 40000 |  | 0 | 1 | 40000 | 1 | 40000 | EQP
37 | 17.8 | 33 | SOTC037 | Sound Analog Mixer | Nos | 245000 | 1 | 245000 |  | 0 | 1 | 245000 | 1 | 245000 | EQP
38 | 19 | 201 | SOTC038 | Electrical Installations in MOTs & TIRs | Job | 195000 | 7 | 1365000 | 2 | 390000 | 9 | 1755000 | 9 | 1755000 | E
[10 empty] | PART - A |  | SUB TOTAL |  | 112373121.768
Transplant Isolation Rooms
39 | 1 | 34 | SOTC039 | Stainless Steel Pre-fabricated Wall panels in TIRs & TIR Corridor | Sqm | 15010 | 202 | 3032020 | 0 | 0 | 202 | 3032020 | 202 | 3032020 | C
|  | 4: AE; 6: 15010; 13: 136.9318; 14: 2055346.318 | C
40 | 1 | 35 | SOTC040 | Stainless Steel Pre-fabricated Ceiling panels in TIRs and TIR Corridor | Sqm | 15010 | 146 | 2191460 | 0 | 0 | 146 | 2191460 | 146 | 2191460 | C
|  | 4: AE; 6: 15010; 13: 33.22; 14: 498632.2 | C
41 | 2.1 | 202 | SOTC041 | Electro conductive Flooring inside TIRs | Sqm | 4035 | 146 | 589110 |  | 0 | 146 | 589110 | 73.6644 | 297235.854 | C
42 | 2.2 | 36 | SOTC042 | Flooring with Vinyl Sheets In TIR Corridor | Sqm | 3750 | 61 | 228750 |  | 0 | 61 | 228750 | 61 | 228750 | C
|  | 4: AE; 6: 3750; 13: 70.4074; 14: 264027.75 | C
43 | 3 | 37 | SOTC043 | Uni Directional Ceiling Laminar Airflow Systems | Nos | 395000 | 3 | 1185000 |  | 0 | 3 | 1185000 | 3 | 1185000 | AC
44 | 3.1 | 38 | SOTC044 | Air Handling Units (AHUs) 11 TR | Nos | 1495000 | 2 | 2990000 |  | 0 | 2 | 2990000 | 2 | 2990000 | AC
45 | 3.1 | 39 | SOTC045 | Air Handling Units (AHUs) 8.5 TR | Nos | 1195000 | 1 | 1195000 |  | 0 | 1 | 1195000 | 1 | 1195000 | AC
46 | 3.2 | 40 | SOTC046 | Condensing Units | Nos | 345000 | 3 | 1035000 |  | 0 | 3 | 1035000 | 3 | 1035000 | AC
|  | 4: AE; 6: 345000; 13: 3; 14: 1035000 | AC
47 | 4 | 41 | SOTC047 | Pressure Relief Dampers | Nos | 22500 | 3 | 67500 |  | 0 | 3 | 67500 | 3 | 67500 | EQP
48 | 8 | 42 | SOTC049 | Hermetically Sealed Doors (1.80mt x 2.10 mt) | Nos | 525000 | 3 | 1575000 |  | 0 | 3 | 1575000 | 3 | 1575000 | C
49 | 15 | 43 | SOTC050 | 12mm thick glazed Glass partition walls in TIRs | Sqm | 650 | 40 | 26000 |  | 0 | 40 | 26000 | 40 | 26000 | C
50 | 15 | 44 | SOTC051 | Wall mounted LED TV43 inchesFull HD | Nos | 165000 | 3 | 495000 |  | 0 | 3 | 495000 | 3 | 495000 | EQP
51 | 91 | 45 | SOTC052 | Ceiling/Wall mounted CCTV Room Camera | Nos | 12000 | 3 | 36000 |  | 0 | 3 | 36000 | 3 | 36000 | E
52 | 88.6 | 46 | SOTC053 | BED HEAD PANEL FOR TIR WITH DOUBLE OUTLETS AND ELECTRICAL OUTLETS | Nos | 49500 | 3 | 148500 |  | 0 | 3 | 148500 | 3 | 148500 | G
53 | 12 | 47 | SOTC054 | X-RAY VIEWERS FOR ALL ICUS AND PRE OPP AREAS AND DOCTORS ROOMS | Nos | 37500 | 5 | 187500 |  | 0 | 5 | 187500 | 5 | 187500 | EQP
|  | 4: AE; 13: 1; 14: 37500 | EQP
54 | 11 | 48 | SOTC055 | WRITING BOARDS FOR ICUS, PRE OPP | Nos | 18750 | 5 | 93750 |  | 0 | 5 | 93750 | 5 | 93750 | C
|  | 4: AE; 6: 18750; 13: 1; 14: 18750 | C
[10 empty] | PART-A |  | SUB TOTAL |  | 18692972.122
Electrical Works
55 | 91 | 49 | SOTC056 | CCTV CEILING CAMERA | Nos | 9500 | 10 | 95000 |  | 0 | 10 | 95000 | 10 | 95000 | E
56 | 22 a | 50 | SOTC057 | Supply and Fixing of 25mm dia Conduit Pipes surface on wall. | Rmt | 110 | 10000 | 1100000 |  | 0 | 10000 | 1100000 | 10000 | 1100000 | E
57 | 22 b | 51 | SOTC058 | Supply and Fixing of 25mm dia Conduit Pipes Concealed on wall. | Rmt | 115 | 4000 | 460000 |  | 0 | 4000 | 460000 | 4000 | 460000 | E
58 | 23 a | 52 | SOTC059 | Wiring with run of 2 of 1.5 Sqmm Copper cable for points wiring. | Pts | 1525 | 570 | 869250 |  | 0 | 570 | 869250 | 570 | 869250 | E
59 | 23 b | 53 | SOTC060 | Wiring with run of 2 of 1.5 Sqmm Copper cable for stairecase points wiring. | Pts | 1100 | 10 | 11000 |  | 0 | 10 | 11000 | 10 | 11000 | E
60 | 23 c | 54 | SOTC061 | Supply and fixing of 6A/10A ISI Mark 3/2 pin Modular socket Common switch board | Pts | 900 | 25 | 22500 |  | 0 | 25 | 22500 | 25 | 22500 | E
61 | 23 d | 55 | SOTC062 | Wiring with 3 of 1.5 sq.mm with 6A switch and 6A, 3/2 pin socket Modular type with 6A switch control fixing on separate board. | Pts | 2800 | 50 | 140000 |  | 0 | 50 | 140000 | 50 | 140000 | E
62 | 23 e | 56 | SOTC063 | Supply and fixing of 6A switchs - 2 Nos and 6A 3/2 pin socket - 3 Nos Modular type with cover plate | Pts | 1400 | 200 | 280000 |  | 0 | 200 | 280000 | 200 | 280000 | E
63 | 23 f | 203 | SOTC064 | Supply & fixing of 16A/6A, 2 in one socket with 16A switch control modular type | Nos | 900 | 200 | 180000 |  | 0 | 200 | 180000 | 200 | 180000 | E
64 | 23 g | 204 | SOTC065 | Supply & fixing of 32A, socket with switch control modular | Nos | 1600 | 18 | 28800 |  | 0 | 18 | 28800 | 18 | 28800 | E
65 | 23 h | 205 | SOTC066 | Supply & fixing of 64A, socket with 64A switch control modular type | Nos | 18000 | 4 | 72000 |  | 0 | 4 | 72000 | 4 | 72000 | E
66 | 24 a | 57 | SOTC067 | Supply and Run of 1 of 1.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 36 | 2000 | 72000 |  | 0 | 2000 | 72000 | 2000 | 72000 | E
67 | 24 b | 58 | SOTC068 | Supply and Run of 3 of 1.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable . | Rmt | 100 | 2000 | 200000 |  | 0 | 2000 | 200000 | 2000 | 200000 | E
68 | 24 c | 59 | SOTC069 | Supply and Run of 3 of 2.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 145 | 8000 | 1160000 |  | 0 | 8000 | 1160000 | 8000 | 1160000 | E
69 | 24 d | 60 | SOTC070 | Supply and Run of 3 runs of 4.0 sq mm (phase neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 230 | 5000 | 1150000 |  | 0 | 5000 | 1150000 | 5000 | 1150000 | E
70 | 24 e | 61 | SOTC071 | Supply and Run of 3 of 6.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 325 | 300 | 97500 |  | 0 | 300 | 97500 | 300 | 97500 | E
71 | 24 f | 62 | SOTC072 | Supply and Run of 5 of 6.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 545 | 300 | 163500 |  | 0 | 300 | 163500 | 300 | 163500 | E
72 | 24 g | 63 | SOTC073 | Supply and Run of 5 of 10.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 850 | 500 | 425000 |  | 0 | 500 | 425000 | 500 | 425000 | E
73 | 25 a | 64 | SOTC074 | Supply and fixing of DP Metal Enclosure with IP 20 Protection DB Make with 1 No 20A, 10 KA DP MCB | Nos | 1800 | 8 | 14400 |  | 0 | 8 | 14400 | 8 | 14400 | E
74 | 25 b | 65 | SOTC075 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 (For Lighting DBs) | Nos | 13000 | 10 | 130000 |  | 0 | 10 | 130000 | 10 | 130000 | E
75 | 25 c | 230 | SOTC076 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 (For Power DB's) | Nos | 13000 | 14 | 182000 |  | 0 | 14 | 182000 | 14 | 182000 | E
76 | 25 d | 66 | SOTC077 | Supply and fixing of 8 Way VTPN DB with IP 43 Protection as per IS:13032 | Nos | 50000 | 5 | 250000 |  | 0 | 5 | 250000 | 5 | 250000 | E
77 | 25 e | 67 | SOTC078 | Supply and fixing of cable adopteres box with cover for DBs including, massanory work etc., complete., | Nos | 6000 | 10 | 60000 |  | 0 | 10 | 60000 | 10 | 60000 | E
78 | 26 a | 206 | SOTC079 | Providing independent earthing for Important equipment with 40mm dia 'B' class 2.5m long G.I pipe (GI Earthing) | Nos | 22500 | 18 | 405000 |  | 0 | 18 | 405000 | 18 | 405000 | E
79 | 26 b | 68 | SOTC080 | Providing independent earthing by exacavating a pit to a depth of 2.25Mtr in all soils as per size specified in the data for Sophisticated Electronic equipment (Copper Earthing) | Nos | 54000 | 18 | 972000 |  | 0 | 18 | 972000 | 18 | 972000 | E
80 | 26 b 1 | 69 | SOTC081 | Providing independent earthing for Important equipment with 100mm dia Heavy gauge C.I Earthing | Nos | 25000 | 6 | 150000 |  | 0 | 6 | 150000 | 6 | 150000 | E
81 | 26 c | 70 | SOTC082 | Supply and Run of 50mm x 6mm G.I Strip | Rmt | 450 | 400 | 180000 |  | 0 | 400 | 180000 | 400 | 180000 | E
82 | 26 d | 71 | SOTC083 | Supply and Run of 25mm x 3mm copper strip | Rmt | 300 | 400 | 120000 |  | 0 | 400 | 120000 | 400 | 120000 | E
83 | 27 a | 207 | SOTC084 | Supply, transportation and fixing of 22W +/ 10% , >/ 2300 lumens, 1200mm length LED light | Nos | 4800 | 20 | 96000 |  | 0 | 20 | 96000 | 20 | 96000 | E
84 | 27 b | 208 | SOTC085 | Supply, transportation and fixing 32-36W (>=3600 Lumens), 2' x2' (600mm x 600mm) slim panel LED luminaire | Nos | 4000 | 60 | 240000 |  | 0 | 60 | 240000 | 60 | 240000 | E
85 | 27 c | 209 | SOTC086 | Supply, transportation and fixing 12 W +/-10% (>= 1200 Lumens) Down lighter back lit LED Down Light Recessed / Surface | Nos | 1400 | 215 | 301000 |  | 0 | 215 | 301000 | 215 | 301000 | E
86 | 27 d | 210 | SOTC087 | Supply, transportation and fixing 18 W +/-10% (>= 1800 Lumens) Down lighter back lit LED Down Light | Nos | 1800 | 95 | 171000 |  | 0 | 95 | 171000 | 95 | 171000 | E
87 | 27 e | 72 | SOTC088 | Supply, transportation and fixing ISI mark batten holder / slanting holder | Nos | 160 | 8 | 1280 |  | 0 | 8 | 1280 | 8 | 1280 | E
88 | 27 f | 231 | SOTC089 | Supply, Transportation of energy efficient fan, 1200 mm sweep, aluminium body, consuming 28 W, BEE 5 star rated, ceiling fan | Nos | 3700 | 40 | 148000 |  | 0 | 40 | 148000 | 40 | 148000 | E
89 | 27 f 1 | 73 | SOTC090 | Supply and fixing of Modular type Stepped electronic regulator. | Nos | 1000 | 40 | 40000 |  | 0 | 40 | 40000 | 40 | 40000 | E
90 | 27 f 2 | 74 | SOTC091 | Labour charges for fixing of ceiling fan and regulator | Nos | 210 | 40 | 8400 |  | 0 | 40 | 8400 | 40 | 8400 | E
91 | 27 f 3 | 75 | SOTC092 | Supply and erecting 19/20mm steel tube down rod of one meter length | Nos | 600 | 40 | 24000 |  | 0 | 40 | 24000 | 40 | 24000 | E
92 | 27 g | 211 | SOTC093 | Supply of 12" (300mm) Light duty exhaust fan | Nos | 3000 | 5 | 15000 |  | 0 | 5 | 15000 | 5 | 15000 | E
93 | 27 h | 212 | SOTC094 | Supply,Transportation of 12" (300mm) ISI, 900 RPM Heavy duty exhaust fan | Nos | 4900 | 10 | 49000 |  | 0 | 10 | 49000 | 10 | 49000 | E
94 | 27 i | 76 | SOTC095 | Labour charges for fixing the exhaust fan in wall with necessary connections | Nos | 900 | 15 | 13500 |  | 0 | 15 | 13500 | 15 | 13500 | E
95 | 27 j | 77 | SOTC096 | Supply and fixing of GI louver shutter including GI mesh | Nos | 3200 | 15 | 48000 |  | 0 | 15 | 48000 | 15 | 48000 | E
96 | 28 a | 213 | SOTC097 | Main Power Panel with 1000A 4 Pole ACB as incomer - 1 No and out goings 800 A 4P MCCB - 1 No., 630 A 4P MCCB - 1 No., 400A 4P MCCB - 4 Nos & 250A 4P MCCB - 3 No's with required Digital Ammeter and Voltmer, LED Indicators | Nos | 1315000 | 1 | 1315000 |  | 0 | 1 | 1315000 | 1 | 1315000 | E
97 | 28 b | 214 | SOTC098 | Floor Power Panel : Incomer: 630A 4 Pole MCCB,- 1 No Outgoings 250 A 4P MCCB - 4 No's 125 A 4P MCCB - 10 No's, 63 A 4P MCCB - 4 No's with required Digital Ammeter and Voltmer, LED Indicators | Nos | 875000 | 1 | 875000 |  | 0 | 1 | 875000 | 1 | 875000 | E
98 | 28 c | 215 | SOTC099 | Electrical Lighting Panels : Incomer: 250 A 4 Pole MCCB - 1 No, Out Goings 125 A 4P MCCB - 4 No's 63 A 4P MCCB - 3 No's with required Digital Ammeter and Voltmer, LED Indicators | Nos | 370000 | 2 | 740000 |  | 0 | 2 | 740000 | 2 | 740000 | E
99 | 29 d | 78 | SOTC100 | 130KVAR Out Door Capacitor panel : Incomer: 250A FP MCCB - 1 No, 63A 10KA TP MCB - 9 Nos. 20 KVAR Capacitor Duty contactors - 5 Nos., 10 KVAR Capacitor Duty contactors - 2 Nos, .5 KVAR Capacitor Duty contactors - 2 Nos. 12 stage APFC Relay - 1 No | Nos | 450000 | 1 | 450000 |  | 0 | 1 | 450000 | 1 | 450000 | E
100 | 29 a | 232 | SOTC101 | 630 KVA Transformer OLTC for transformers with RTCC: Supply, Transportation, Installation, Testing and Commissioning of 630 KVA TRANSFORMER with all test reports. The Transformer shall be designed and manufactured as per IS:1180 OLTC with level-II with initial filling of oil as per IS 335-1993. 1000 A LT Breaker Kiosk - 01 No.The basic details of the Transformer are as under. Makes: Kirloskar / PETE / Esennar / Voltamp / Crompton / ABB / Schneider. | Nos | 4000000 | 1 | 4000000 |  | 0 | 1 | 4000000 | 0 | 0 | E
101 | 30 a | 79 | SOTC102 | Supply of 25 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 300 | 200 | 60000 |  | 0 | 200 | 60000 | 200 | 60000 | E
102 | 30 b | 80 | SOTC103 | Supply of 50 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 560 | 200 | 112000 |  | 0 | 200 | 112000 | 200 | 112000 | E
103 | 30 c | 81 | SOTC104 | Supply of 70 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 750 | 75 | 56250 |  | 0 | 75 | 56250 | 75 | 56250 | E
104 | 30 d | 82 | SOTC105 | Supply of 120 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 1050 | 50 | 52500 |  | 0 | 50 | 52500 | 50 | 52500 | E
105 | 30 e | 83 | SOTC106 | Supply of 185 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 1500 | 50 | 75000 |  | 0 | 50 | 75000 | 50 | 75000 | E
106 | 30 f | 84 | SOTC107 | Supply of 240 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 1900 | 100 | 190000 |  | 0 | 100 | 190000 | 100 | 190000 | E
107 | 30 g | 85 | SOTC108 | Supply of 300 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 2400 | 500 | 1200000 |  | 0 | 500 | 1200000 | 500 | 1200000 | E
108 | 31 a | 86 | SOTC109 | Termination of UG cables of 3.5 core 25 Sq.mm | Nos | 850 | 8 | 6800 |  | 0 | 8 | 6800 | 8 | 6800 | E
109 | 31 b | 87 | SOTC110 | Termination of UG cables of 3.5 core 50 Sq.mm | Nos | 1200 | 8 | 9600 |  | 0 | 8 | 9600 | 8 | 9600 | E
110 | 31 c | 88 | SOTC111 | Termination of UG cables of 3.5 core 70 Sq.mm | Nos | 1500 | 8 | 12000 |  | 0 | 8 | 12000 | 8 | 12000 | E
111 | 31 d | 89 | SOTC112 | Termination of UG cables of 3.5 core 120 Sq.mm | Nos | 1900 | 4 | 7600 |  | 0 | 4 | 7600 | 4 | 7600 | E
112 | 31 e | 90 | SOTC113 | Termination of UG cables of 3.5 core 185 Sq.mm | Nos | 2500 | 4 | 10000 |  | 0 | 4 | 10000 | 4 | 10000 | E
113 | 31 f | 91 | SOTC114 | Termination of UG cables of 3.5 core 240 Sq.mm | Nos | 3500 | 4 | 14000 |  | 0 | 4 | 14000 | 4 | 14000 | E
114 | 31 g | 92 | SOTC115 | Termination of UG cables of 3.5 core 300 Sq.mm | Nos | 4000 | 12 | 48000 |  | 0 | 12 | 48000 | 12 | 48000 | E
115 | 31 h | 93 | SOTC116 | Earth work excavation of Trench laying of U.G cables up to 70 sqmm | Rmt | 1100 | 100 | 110000 |  | 0 | 100 | 110000 | 100 | 110000 | E
116 | 31 i | 94 | SOTC117 | Earth work excavation of Trench laying of U.G cables from 95 Sqmm | Rmt | 1150 | 100 | 115000 |  | 0 | 100 | 115000 | 100 | 115000 | E
117 | 31 j | 95 | SOTC118 | Laying of PVC armoured under ground cable up to 95 Sqmm on wall | Rmt | 125 | 200 | 25000 |  | 0 | 200 | 25000 | 200 | 25000 | E
118 | 31 k | 96 | SOTC119 | Laying of PVC armoured under ground cable from 120 Sq.mm to 400 Sqmm saddles on wall | Rmt | 270 | 700 | 189000 |  | 0 | 700 | 189000 | 700 | 189000 | E
119 | 32 a | 97 | SOTC120 | Supply, Transportation and Installation of 150mm x 50mm x 2mm thick hot dip GI perforated cable tray | Rmt | 1295 | 200 | 259000 |  | 0 | 200 | 259000 | 200 | 259000 | E
120 | 32 b | 98 | SOTC121 | Supply, Transportation and Installation of 300mm x 50mm x 2mm thick thick hot dip GI perforated cable tray | Rmt | 4500 | 100 | 450000 |  | 0 | 100 | 450000 | 100 | 450000 | E
121 | 33 a | 99 | SOTC122 | Supply, Transportation and installation of 10KVA / 312V DC on line UPS system | Nos | 400000 | 7 | 2800000 | 2 | 800000 | 9 | 3600000 | 9 | 3600000 | E
122 | 33 b | 100 | SOTC123 | Supply and fixing of 12V, 150 AH MF battery | Nos | 25000 | 182 | 4550000 | 52 | 1300000 | 234 | 5850000 | 234 | 5850000 | E
|  | 4: AE; 6: 25000; 13: 118; 14: 2950000 | E
123 | 33 c | 101 | SOTC124 | Supply and providing of UPS cum battery rack 20 batteries | Nos | 30000 | 7 | 210000 | 2 | 60000 | 9 | 270000 | 9 | 270000 | E
|  | 4: AE; 6: 30000; 13: 2; 14: 60000 | E
124 | 33 d | 102 | SOTC125 | Supply, Transportation, Installation, Testing and commissioning of storage / Pressure type 5 Star rated water heater with ABS plastic body of 15 Ltrs | Nos | 16000 | 7 | 112000 |  | 0 | 7 | 112000 | 7 | 112000 | E
|  | 4: AE; 6: 16000; 13: 4; 14: 64000 | E
125 | 34 | 103 | SOTC126 | 26 persons ICU bed cum passenger lift (1768 Kgs) G+8 Floors, 9 stops,9 Openings (Cost Includes amount for Construction of Shaft / Cladding from Ground to 8th Floor) | Nos | 10495000 | 1 | 10495000 |  | 0 | 1 | 10495000 | 1 | 10495000 | E
E
[10 empty] | PART-A |  | SUB TOTAL |  | 39927880
Air Conditioning
126 | 35.1 | 104 | SOTC127 | 1.50 TR with , 18000 BTU/Hr High Wall mount Split Air Conditioners | Nos | 150000 | 6 | 900000 |  | 0 | 6 | 900000 | 6 | 900000 | AC
|  | 4: AE; 6: 150000; 13: 1; 14: 150000 | AC
127 | 35.2 | 105 | SOTC128 | 2.0 TR with , 24000 BTU/Hr High Wall mount Split Air Conditioners | Nos | 210000 | 2 | 420000 |  | 0 | 2 | 420000 | 2 | 420000 | AC
|  | 4: AE; 6: 210000; 13: 4; 14: 840000 | AC
128 | 35.3 | 106 | SOTC129 | Voltage stabilizer for 4 KVA maximum load | Nos | 7000 | 6 | 42000 |  | 0 | 6 | 42000 | 6 | 42000 | AC
|  | 4: AE; 6: 7000; 13: 1; 14: 7000 | AC
129 | 35.4 | 107 | SOTC130 | Voltage stabilizer for 5 KVA maximum load | Nos | 8500 | 2 | 17000 |  | 0 | 2 | 17000 | 2 | 17000 | AC
|  | 4: AE; 6: 8500; 13: 4; 14: 34000 | AC
130 | 35.5 | 216 | SOTC131 | Ductable Air Conditioners 11.0 TR with ISEER ≥ 4 | Nos | 1200000 | 1 | 1200000 |  | 0 | 1 | 1200000 | 1 | 1200000 | AC
131 | 35.6 | 217 | SOTC132 | Ductable Air Conditioners 8.5 TR with ISEER ≥ 4 | Nos | 1000000 | 2 | 2000000 |  | 0 | 2 | 2000000 | 2 | 2000000 | AC
|  | 4: AE; 6: 1000000; 13: 2; 14: 2000000 | AC
132 | 35.7 | 218 | SOTC133 | Ductable Air Conditioners 5.5 TR with ISEER ≥ 4 | Nos | 900000 | 1 | 900000 |  | 0 | 1 | 900000 | 1 | 900000 | AC
|  | 4: AE; 6: 900000; 13: 2; 14: 1800000 | AC
[10 empty] | PART-A |  | SUB TOTAL |  | 10310000
Fire Fighting
133 | 36.2 | 108 | SOTC134 | Automatic Smoke Detection System | Job | 1425000 | 1 | 1425000 |  | 0 | 1 | 1425000 | 1 | 1425000 | FF
134 | 36.3 | 109 | SOTC135 | Automatic Fire Alarm System | Job | 1400000 | 1 | 1400000 |  | 0 | 1 | 1400000 | 1 | 1400000 | FF
135 | 36.4 | 219 | SOTC136 | Supply & Fixing of 4.5Kg, CO2 Type Fire Extinguisher. | Nos | 27000 | 6 | 162000 |  | 0 | 6 | 162000 | 6 | 162000 | FF
136 | 36.5 | 110 | SOTC137 | Supply and fixing of ABC stored pressure squeeze grip type fire extinguishers, 9 kg capacity. | Nos | 16000 | 6 | 96000 |  | 0 | 6 | 96000 | 6 | 96000 | FF
137 | 36.6 | 111 | SOTC138 | Supply and fixing of ABC Powder MAP 4 Kg Fire extinguisher | Nos | 11000 | 10 | 110000 |  | 0 | 10 | 110000 | 10 | 110000 | FF
138 | 36.7 | 112 | SOTC139 | Supply and fixing of 2 Kg Fire extinguisher Clean Agent | Nos | 22500 | 10 | 225000 |  | 0 | 10 | 225000 | 10 | 225000 | FF
139 | 36.8 | 113 | SOTC140 | Supply and fixing of Escape signage boards in Rigid Photo luminescent based glow | Nos | 2000 | 150 | 300000 |  | 0 | 150 | 300000 | 150 | 300000 | FF
140 | 36.9 | 220 | SOTC141 | Supply & Fixing of Powder Coated Fire Rated doors. | Sqm | 29000 | 6 | 174000 |  | 0 | 6 | 174000 | 6 | 174000 | FF
|  | 4: AE; 6: 29000; 13: 7.8; 14: 226200 | FF
[10 empty] | PART-A |  | SUB TOTAL |  | 4118200
ELV
141 | 37 | 221 | SOTC142 | Telephone & EPABX System | Job | 1000000 | 1 | 1000000 |  | 0 | 1 | 1000000 | 1 | 1000000 | ELV
142 | 38 | 114 | SOTC143 | Local Area Network (LAN) System | Job | 1250000 | 1 | 1250000 |  | 0 | 1 | 1250000 | 1 | 1250000 | ELV
143 | 39 | 115 | SOTC144 | Biometric Access Control System | Nos | 300000 | 2 | 600000 |  | 0 | 2 | 600000 | 2 | 600000 | ELV
|  | 4: AE; 6: 300000; 13: 1; 14: 300000 | ELV
[10 empty] | PART-A |  | SUB TOTAL |  | 3150000
Civil Works
144 |  | 116 | SOTC145 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Reinforced cement concrete) | Cum | 5400 | 10 | 54000 |  | 0 | 10 | 54000 | 10 | 54000 | C
145 |  | 117 | SOTC146 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Unreinforced cement concrete) | Cum | 4500 | 1.5 | 6750 |  | 0 | 1.5 | 6750 | 1.5 | 6750 | C
|  | 4: AE; 6: 4500; 13: 50.4015; 14: 226806.75 | C
146 |  | 118 | SOTC147 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Brick Masonary) | Cum | 900 | 118 | 106200 |  | 0 | 118 | 106200 | 118 | 106200 | C
|  | 4: AE; 6: 900; 13: 34.691; 14: 31221.9 | C
147 |  | 119 | SOTC148 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Kadapa slabs or shahabad stone slabs on sand bed) | Sqm | 630 | 25 | 15750 |  | 0 | 25 | 15750 | 25 | 15750 | C
|  | 4: AE; 6: 630; 13: 667.9265; 14: 420793.695 | C
148 |  | 120 | SOTC149 | Dismantling doors, windows and clear storey windows, Ventilators etc., (wood or steel) shutters including Chowkhats, architraves,hold fasts and other attachments etc., and stacking them within 100m lead including charge etc., complete for finished item of work. (Not exceeding 3 sqm in area) | Nos | 1800 | 57 | 102600 |  | 0 | 57 | 102600 | 57 | 102600 | C
|  | 4: AE; 6: 1800; 13: 146; 14: 262800 | C
149 |  | 121 | SOTC150 | Conveyance of un-useful excavated earth to a distance of 16 KM for disposal including hire charges of T and P, labour charges etc., complete for finished item of work. | Cum | 900 | 250 | 225000 |  | 0 | 250 | 225000 | 250 | 225000 | C
|  | 4: AE; 6: 900; 13: 64.769; 14: 58292.1 | C
150 | 40 | 122 | SOTC151 | RCC M 25 grade design mix (For lintels) | Cum | 18900 | 3 | 56700 |  | 0 | 3 | 56700 | 3 | 56700 | C
|  | 4: AE; 6: 18900; 13: 0.17; 14: 3213 | C
151 | 41 | 123 | SOTC152 | RCC M 20 grade design mix (50mm thick platforms) | Sqm | 1170 | 12 | 14040 |  | 0 | 12 | 14040 | 0 | 0 | C
C
152 | 41 | 124 | SOTC153 | RCC M 20 grade design mix (25 mm thick Shelves) | Sqm | 900 | 12 | 10800 |  | 0 | 12 | 10800 | 0 | 0 | C
C
153 | 42 | 125 | SOTC154 | Brick Masonry work in CM (1:6) prop in superstructure | Cum | 15300 | 3 | 45900 |  | 0 | 3 | 45900 | 3 | 45900 | C
|  | 4: AE; 6: 15300; 13: 108.951; 14: 1666950.3 | C
154 | 43 | 126 | SOTC155 | Reinforced Masonry for partition walls (100 mm thick) in CM (1:4) | Sqm | 2700 | 500 | 1350000 |  | 0 | 500 | 1350000 | 404.9325 | 1093317.75 | C
C
155 | 44 | 127 | SOTC156 | PCC (1:3:6) nominal mix using 20mm size graded m/c (For bed blocks and hold fasts) (OTs screed) | Cum | 9000 | 1.5 | 13500 |  | 0 | 1.5 | 13500 | 0 | 0 | C
C
156 | 45 | 128 | SOTC157 | Filling with light weight concrete in Cement Concrete (1:5:10) proportion using brick jelly for low roofs | Cum | 7200 | 23 | 165600 |  | 0 | 23 | 165600 | 16.8651 | 121428.72 | C
C
157 | 46 | 129 | SOTC158 | Thermo Mechanically Treated (Fe -500/500D/550D) for RCC works | MT | 126000 | 1.25 | 157500 |  | 0 | 1.25 | 157500 | 0.7686 | 96843.6 | C
C
158 | 49 | 130 | SOTC159 | Plastering 12mm thick in two coats with base coat of 8mm thick in CM (1:6) and top coat of 4mm thick in CM (1:4). for Internal walls. | Sqm | 1224 | 1600 | 1958400 |  | 0 | 1600 | 1958400 | 1600 | 1958400 | C
|  | 4: AE; 6: 1224; 13: 548.804; 14: 671736.096 | C
159 | 51 | 131 | SOTC160 | Impervious coat to exposed RCC roof slab surfaces (APSS No. 901 and 903) For Toilets | Sqm | 360 | 77.78 | 28000.8 |  | 0 | 77.78 | 28000.8 | 43.05 | 15498 | C
C
160 | 92 | 222 | SOTC161 | Providing and applying Wall putty of White Cement or Polymer or Cement based of average 1 to 2 mm thickness over plastered surface to prepare the surface even and smooth after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, applying emery paper, Sand the surface, clean & wipe off loose dust, applying knifing paste filler by putty knife / muslin pad, air dry for 2 - 3 | Sqm | 270 | 4447 | 1200690 |  | 0 | 4447 | 1200690 | 1811.5335 | 489114.045 | C
C
161 | 53 | 132 | SOTC162 | Flooring with non-skid full body ceramic floor tiles | Sqm | 1710 | 85 | 145350 |  | 0 | 85 | 145350 | 85 | 145350 | C
|  | 4: AE; 6: 1710; 13: 13.0805; 14: 22367.655 | C
162 | 55 | 133 | SOTC163 | Dadooing to walls with glazed full body Porcelain wall tiles | Sqm | 1440 | 225 | 324000 |  | 0 | 225 | 324000 | 225 | 324000 | C
|  | 4: AE; 6: 1440; 13: 115; 14: 165600 | C
163 | 56 | 134 | SOTC164 | Dadooing to walls with glazed full body Ceramic tiles | Sqm | 1440 | 350 | 504000 |  | 0 | 350 | 504000 | 270.2175 | 389113.2 | C
C
164 | 57 | 135 | SOTC165 | Painting one coat water based cement primer of interior grade I and two coats of acrylic emulsion paint for ceiling and Walls | Sqm | 360 | 4447 | 1600920 |  | 0 | 4447 | 1600920 | 1372.014 | 493925.04 | C
C
165 | 59 | 136 | SOTC166 | Painting to new wood work | Sqm | 360 | 313 | 112680 |  | 0 | 313 | 112680 | 75 | 27000 | C
C
166 | 60 | 137 | SOTC167 | Painting to new iron work | Sqm | 270 | 88 | 23760 |  | 0 | 88 | 23760 | 88 | 23760 | C
|  | 4: AE; 6: 270; 13: 38.42; 14: 10373.4 | C
167 | 61 | 138 | SOTC168 | Two shutter cupboards | Sqm | 9000 | 100 | 900000 |  | 0 | 100 | 900000 | 0 | 0 | C
C
168 | 64 | 139 | SOTC169 | UPVC Fixed Louvered Ventilator | Sqm | 12000 | 7 | 84000 |  | 0 | 7 | 84000 | 7 | 84000 | C
|  | 4: AE; 6: 12000; 13: 9.5165; 14: 114198 | C
169 |  | 140 | SOTC170 | UPVC 3 track Sliding Windows | Sqm | 9000 | 15 | 135000 |  | 0 | 15 | 135000 | 15 | 135000 | C
|  | 4: AE; 6: 9000; 13: 30.276; 14: 272484 | C
170 |  | 141 | SOTC171 | MS Grills to Windows | Sqm | 1800 | 150 | 270000 |  | 0 | 150 | 270000 | 126.42 | 227556 | C
C
171 | 66 | 142 | SOTC172 | Flooring with 16 to 18 mm thick high polished granite stone slabs black colour for platforms (S.S.701 and special) | Sqm | 6300 | 50 | 315000 |  | 0 | 50 | 315000 | 50 | 315000 | C
|  | 14: 0 | C
172 | 67 | 143 | SOTC173 | Doors as per approved drawings with medium teak wood frame (1500mm x 2600mm) | Sqm | 6300 | 50 | 315000 |  | 0 | 50 | 315000 | 15.4 | 97020 | C
C
173 | 68 | 144 | SOTC174 | Doors as per approved drawings with medium teak wood frame (1000mm x 2100mm) | Sqm | 7400 | 45 | 333000 |  | 0 | 45 | 333000 | 17.2 | 127280 | C
C
174 | 69 | 145 | SOTC175 | Doors Shutters WPC(800mm x 2100mm) | Sqm | 5400 | 40 | 216000 |  | 0 | 40 | 216000 | 33.3795 | 180249.3 | C
C
175 | 70 | 146 | SOTC176 | Scientific Doors with metal door frames and door shutters made of galvanize steel | Sqm | 18000 | 45 | 810000 |  | 0 | 45 | 810000 | 45 | 810000 | C
|  | 4: AE; 6: 18000; 13: 24.3; 14: 437400 | C
176 | 71 | 147 | SOTC177 | False ceiling as per Technical specification | Sqm | 1800 | 1400 | 2520000 |  | 0 | 1400 | 2520000 | 750 | 1350000 | C
C
177 | 72 | 148 | SOTC178 | Vinyl flooring | Sqm | 3000 | 500 | 1500000 |  | 0 | 500 | 1500000 | 500 | 1500000 | C
|  | 4: AE; 6: 3000; 13: 164; 14: 492000 | C
178 | 74 | 149 | SOTC179 | Impervious coat to exposed RCC roof slab surfacesof 20mm thick (APSS No. 901 and 903) | Sqm | 1260 | 350 | 441000 |  | 0 | 350 | 441000 | 0 | 0 | C
C
179 | 63 | 233 | SOTC180 | Fixed Glass Window – 1200 x 1200 | Sqm | 5400 | 53.55 | 289170 |  | 0 | 53.55 | 289170 | 53.55 | 289170 | C
|  | 4: AE; 6: 5400; 13: 7.46; 14: 40284 | C
180 | 95 | 223 | SOTC181 | Grouting the holes with neat cement slurry of 20mm dia with all required accessories of all materials etc., including cost & Conveyance of all labour Charges etc., complete finished item of work (*As per SSR2021-22 of S.NO:-8) | Nos | 180 | 500 | 90000 |  | 0 | 500 | 90000 | 0 | 0 | C
C
181 | 96 | 224 | SOTC182 | Pressure grouting the drilled holes with neat cement slurry or with approved grout admixture using pump - excluding cost of drilling holes after fixing nozzles as technical specification approved by the department etc., including cost & Conveyance of all labour charges etc., complete finished item of work | Nos | 630 | 500 | 315000 |  | 0 | 500 | 315000 | 500 | 315000 | C
|  | 4: AE; 6: 630; 13: 632; 14: 398160 | C
182 | 87 A | 234 | SOTC183 | Supply and fabricating,erecting and fixing inposition trusses of approved design with structural steel other than MS. | Kgs | 180 | 6500 | 1170000 |  | 0 | 6500 | 1170000 | 6500 | 1170000 | C
C
183 | 87 B | 150 | SOTC184 | Supply and fixing of pre painted Galvalume Trapezoidal Profile Roofing with 0.50mm Thickness. | Sqm | 1080 | 65 | 70200 |  | 0 | 65 | 70200 | 65 | 70200 | C
[10 empty] | PART-A |  | SUB TOTAL |  | 17755806.551
Plumbing Works
184 | 75 | 225 | SOTC185 | 4" (101.6mm) multi floor trap with jali - UPVC/SWR | Nos | 270 | 25 | 6750 |  | 0 | 25 | 6750 | 25 | 6750 | P
|  | 4: AE; 6: 270; 13: 19; 14: 5130 | P
185 | 76 | 151 | SOTC186 | 580mm x 440mm long Orissa pan white glazed Water Closet | Nos | 5400 | 4 | 21600 |  | 0 | 4 | 21600 | 4 | 21600 | P
P
186 | 77 | 152 | SOTC187 | European Water Closet of 1st quality | Nos | 6300 | 9 | 56700 |  | 0 | 9 | 56700 | 9 | 56700 | P
P
187 | 78 | 153 | SOTC188 | Indian make Flat Back Wash Hand Basin 1st quality | Nos | 3600 | 16 | 57600 |  | 0 | 16 | 57600 | 15 | 54000 | P
P
188 | 79 | 154 | SOTC189 | CP finish brass soap dish | Nos | 1100 | 21 | 23100 |  | 0 | 21 | 23100 | 21 | 23100 | P
P
189 | 80 | 155 | SOTC190 | TV shape mirror with plastic frame of size 609.6mm x 457.2mm | Nos | 630 | 25 | 15750 |  | 0 | 25 | 15750 | 15 | 9450 | P
P
190 | 81 | 156 | SOTC191 | 25.4mm dia , 609.6mm long aluminium anodized towel rods | Nos | 540 | 36 | 19440 |  | 0 | 36 | 19440 | 21 | 11340 | P
P
191 | 82 | 156 | SOTC192 | 15 mm brass body CP finish bib tap of not less than 300 grams weight | Nos | 540 | 25 | 13500 |  | 0 | 25 | 13500 | 14 | 7560 | P
P
192 | 87 C | 158 | SOTC193 | Self Closing Tap - Push Type | Nos | 720 | 25 | 18000 |  | 0 | 25 | 18000 | 15 | 10800 | P
P
193 | 84 | 159 | SOTC194 | Chromium plated finish brass body quarter turn Bibcock cum Health Faucet | Nos | 3600 | 12 | 43200 |  | 0 | 12 | 43200 | 12 | 43200 | P
|  | 4: AE; 6: 3600; 13: 4; 14: 14400 | P
194 | 85 | 160 | SOTC195 | Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings - 15.90mm OD pipe | Rmt | 270 | 55 | 14850 |  | 0 | 55 | 14850 | 55 | 14850 | P
|  | 4: AE; 6: 270; 13: 53.234; 14: 14373.18 | P
195 | 85 | 161 | SOTC196 | Ashirvad/Ajay/Astral Flowguard or equivalent CPVC Pipes and Fittings - 22.20mm OD pipe | Rmt | 360 | 115 | 41400 |  | 0 | 115 | 41400 | 115 | 41400 | P
|  | 4: AE; 6: 360; 13: 14.7065; 14: 5294.34 | P
196 | 85 | 162 | SOTC197 | Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings -28.60mm OD pipe | Rmt | 450 | 143 | 64350 |  | 0 | 143 | 64350 | 115.5 | 51975 | P
P
197 | 86 | 163 | SOTC198 | Bronze Gate/ Globe valve - 25mm Nominal bore | Nos | 1440 | 15 | 21600 |  | 0 | 15 | 21600 | 15 | 21600 | P
|  | 4: AE; 6: 1440; 13: 5; 14: 7200 | P
198 | 87 | 164 | SOTC199 | SWR PVC pipes (Prince/ Sudhakar/ Kisan/ Supreme or any ISI brand) 4 Kg/Sq.cm. - 75mmdia | Rmt | 450 | 145 | 65250 |  | 0 | 145 | 65250 | 84 | 37800 | P
P
199 | 87 | 165 | SOTC200 | SWR PVC pipes (Prince/ Sudhakar/ Kisan/ Supreme or any ISI brand) 4 Kg/Sq.cm. -110mmdia | Rmt | 540 | 145 | 78300 |  | 0 | 145 | 78300 | 68.25 | 36855 | P
P
200 | 90 | 226 | SOTC201 | Supplying and fixing15 mm nominal size 152.0 mm CP finish iron body shower rose 1st quality including cost and conveyance of all materials, labour charges , overheads & contractors profit for finished item of work in all floors. | Nos | 630 | 5 | 3150 |  | 0 | 5 | 3150 | 5 | 3150 | P
|  | 4: AE; 6: 630; 13: 1; 14: 630 | P
201 | 87 D | 166 | SOTC202 | Supply and Fixing of white glazed flat back bowl urinals | Nos | 2700 | 4 | 10800 |  | 0 | 4 | 10800 | 0 | 0 | P
P
202 | 87 E | 227 | SOTC203 | Supply and fixing of 16mm to 20 mm thick ploished marbles slab partitions of size 4'0"*2'0" | Nos | 3600 | 10 | 36000 |  | 0 | 10 | 36000 | 0 | 0 | P
P
[10 empty] | PART-A |  | SUB TOTAL |  | 499157.52
Medical Gas Pipe Line
203 | 88.1 | 167 | SOTC204 | 28 mm dia. and 0.90 mm thick Copper Pipe Lines for Main lines | Rmt | 1750 | 700 | 1225000 |  | 0 | 700 | 1225000 | 700 | 1225000 | G
|  | 4: AE; 6: 1750; 13: 133; 14: 232750 | G
204 | 88.1 | 168 | SOTC205 | 42 mm dia. and 1.20 mm thick Copper Pipe Lines for Main lines | Rmt | 2250 | 200 | 450000 |  | 0 | 200 | 450000 | 200 | 450000 | G
|  | 4: AE; 6: 2250; 13: 27; 14: 60750 | G
205 | 88.1 | 169 | SOTC206 | 54 mm dia. and 1.20 mm thick Copper Pipe Lines for Main lines | Rmt | 2950 | 550 | 1622500 |  | 0 | 550 | 1622500 | 550 | 1622500 | G
|  | 4: AE; 6: 2950; 13: 14; 14: 41300 | G
206 | 88.1 | 170 | SOTC207 | 12 mm dia. and 0.70 mm thick Copper Pipe Lines for distribution lines | Rmt | 650 | 320 | 208000 |  | 0 | 320 | 208000 | 320 | 208000 | G
|  | 4: AE; 6: 650; 13: 224; 14: 145600 | G
207 | 88.1 | 171 | SOTC208 | 15 mm dia. and 0.90 mm thick Copper Pipe Lines for distribution lines | Rmt | 950 | 525 | 498750 |  | 0 | 525 | 498750 | 525 | 498750 | G
|  | 4: AE; 6: 950; 13: 232; 14: 220400 | G
208 | 88.1 | 172 | SOTC209 | 22 mm dia. and 0.90 mm thick Copper Pipe Lines for distribution lines | Rmt | 1450 | 530 | 768500 |  | 0 | 530 | 768500 | 530 | 768500 | G
|  | 4: AE; 6: 1450; 13: 65; 14: 94250 | G
209 | 88.2 | 228 | SOTC210 | 15 mm (1/2") Isolation Valves | Nos | 1500 | 40 | 60000 |  | 0 | 40 | 60000 | 31 | 46500 | G
G
210 | 88.2 | 229 | SOTC211 | 22 mm (3/4") Isolation Valves | Nos | 2500 | 15 | 37500 |  | 0 | 15 | 37500 | 14 | 35000 | G
G
211 | 88.2 | 173 | SOTC212 | 28 mm Isolation Valves | Nos | 3500 | 3 | 10500 | 2 | 7000 | 5 | 17500 | 5 | 17500 | G
|  | 4: AE; 6: 3500; 13: 4; 14: 14000 | G
212 | 88.2 | 174 | SOTC213 | 42 mm Isolation Valves | Nos | 4500 | 2 | 9000 | 3 | 13500 | 5 | 22500 | 4 | 18000 | G
G
213 | 88.2 | 175 | SOTC214 | 54 mm Isolation Valves | Nos | 5500 | 2 | 11000 | 1 | 5500 | 3 | 16500 | 3 | 16500 | G
|  | 4: AE; 6: 5500; 13: 7; 14: 38500 | G
214 | 88.3 | 176 | SOTC215 | Gas Outlet Points with probes for Oxygen with S Brackets | Nos | 2850 | 189 | 538650 |  | 0 | 189 | 538650 | 189 | 538650 | G
|  | 4: AE; 6: 2850; 13: 17; 14: 48450 | G
215 | 88.4 | 177 | SOTC216 | 2 Gas Digital Area Alarm Panels | Nos | 25000 | 2 | 50000 |  | 0 | 2 | 50000 | 0 | 0 | G
G
216 | 88.4 | 178 | SOTC217 | 3 Gas Digital Area Alarm Panels | Nos | 30000 | 4 | 120000 |  | 0 | 4 | 120000 | 4 | 120000 | G
|  | 4: AE; 6: 30000; 13: 1; 14: 30000 | G
217 | 88.4 | 179 | SOTC218 | 5 Gas Digital Area Alarm Panels | Nos | 40000 | 5 | 200000 | 1 | 40000 | 6 | 240000 | 0 | 0 | G
G
218 | 88.4 | 180 | SOTC219 | Master Digital Alarm Panels | Nos | 50000 | 1 | 50000 |  | 0 | 1 | 50000 | 1 | 50000 | G
G
219 | 88.5 | 181 | SOTC220 | BPC Flow meter with Humidifier bottle and L adapter | Nos | 2250 | 27 | 60750 |  | 0 | 27 | 60750 | 27 | 60750 | G
|  | 4: AE; 6: 2250; 13: 16; 14: 36000 | G
220 | 88.5 | 182 | SOTC221 | L Type Adapter for Oxygen Flow meters | Nos | 1250 | 27 | 33750 |  | 0 | 27 | 33750 | 27 | 33750 | G
G
221 | 88.5 | 183 | SOTC222 | Kit for conversion of Oxygen | Nos | 1650 | 27 | 44550 |  | 0 | 27 | 44550 | 18 | 29700 | G
G
222 | 88.5 | 184 | SOTC223 | Suction Jars of 600 ml capacity | Nos | 3450 | 27 | 93150 |  | 0 | 27 | 93150 | 27 | 93150 | G
|  | 4: AE; 6: 3450; 13: 19; 14: 65550 | G
223 | 88.5 | 185 | SOTC224 | Adapters for Vacuum | Nos | 750 | 27 | 20250 |  | 0 | 27 | 20250 | 27 | 20250 | G
G
224 | 88.5 | 186 | SOTC225 | Adapters for Air | Nos | 750 | 27 | 20250 |  | 0 | 27 | 20250 | 27 | 20250 | G
G
225 | 88.5 | 187 | SOTC226 | Adapters for Nitrous Oxide | Nos | 750 | 15 | 11250 |  | 0 | 15 | 11250 | 15 | 11250 | G
G
226 | 88.5 | 188 | SOTC227 | Vacuum Tube | Nos | 550 | 27 | 14850 | 58 | 31900 | 85 | 46750 | 85 | 46750 | G
|  | 4: AE; 6: 550; 13: 30; 14: 16500 | G
227 | 88.6 | 189 | SOTC228 | Bed Head wall panel horizontal 1500 mm long single railing | Nos | 35000 | 27 | 945000 |  | 0 | 27 | 945000 | 27 | 945000 | G
|  | 4: AE; 6: 35000; 13: 4; 14: 140000 | G
228 | 88.7 b | 190 | SOTC229 | Valve box -2 services | Nos | 9500 | 1 | 9500 |  | 0 | 1 | 9500 | 0 | 0 | G
G
229 | 88.7 b | 191 | SOTC230 | Valve box -3 services | Nos | 14500 | 3 | 43500 |  | 0 | 3 | 43500 | 3 | 43500 | G
|  | 4: AE; 6: 14500; 13: 2; 14: 29000 | G
230 | 88.7 b | 192 | SOTC231 | Valve box -6 services | Nos | 22500 | 1 | 22500 | 5 | 112500 | 6 | 135000 | 6 | 135000 | G
G
231 | 88.8 a | 193 | SOTC232 | 4 + 4 size of CO2 manifold System | Job | 40000 | 1 | 40000 | 1 | 40000 | 2 | 80000 | 2 | 80000 | G
|  | 4: AE; 6: 40000; 13: 1; 14: 40000 | G
232 | 88.8 b | 194 | SOTC233 | 2 cylinder emergency manifold CO2 | Job | 14500 | 1 | 14500 | 1 | 14500 | 2 | 29000 | 2 | 29000 | G
G
233 | 88.8 c | 195 | SOTC234 | Fully Automatic CO2 Control System | Job | 185000 | 1 | 185000 | 1 | 185000 | 2 | 370000 | 2 | 370000 | G
G
234 | 88.9 | 237 | SOTC235 | Aneste Iwata Make TFS 150 C9 Model, Compresso Two stage, Motor 15 HP & 57.18 CFM, 60 CFM Air Dryer with 2000 Ltrs Receiver Twin System (For Air4, Air7) | Job | 1895000 | 1 | 1895000 |  | 0 | 1 | 1895000 | 1 | 1895000 | G
G
235 | 88.1 | 196 | SOTC236 | Supporting structure for MGPS lines with Ismb Columns, beams, MS angles, Flats and square rods | Job | 795000 | 1 | 795000 |  | 0 | 1 | 795000 | 1 | 795000 | G
G
236 | 88.11 | 197 | SOTC237 | 2x20 Oxygen Main manifold System | Job | 95000 | 1 | 95000 |  | 0 | 1 | 95000 | 1 | 95000 | G
G
237 | 88.12 | 198 | SOTC238 | Electrical Control Panel for MGPS | Job | 145000 | 1 | 145000 |  | 0 | 1 | 145000 | 1 | 145000 | G
G
238 | 88.13 | 238 | SOTC239 | Vaccum system Ingersoll Rand Make Model 15V x 10 Model with 5 HP Motor with 1000 Liters Reciever, Filters, Electricals, Etc Secretion Trap and Bacteria Filter | Job | 1495000 | 2 | 2990000 |  | 0 | 2 | 2990000 | 2 | 2990000 | G
G
239 |  | 235 | SOTC240 | Validation By Third Party Agency Charges per Each MOT | Each | 100000 | 4 | 400000 |  | 0 | 4 | 400000 | 4 | 400000 | G
|  | 4: AE; 6: 100000; 13: 5; 14: 500000 | G
240 |  | 236 | SOTC241 | Anesthetic Gas Scavenging System (AGSS) | Job | 1213000 | 1 | 1213000 |  | 0 | 1 | 1213000 | 1 | 1213000 | G
[10 empty] | PART-A |  | SUB TOTAL |  | 16819300
241 |  |  |  | Electrical connections for 2 UPS | Job | 100000 |  |  | 1 | 100000 | 1 | 100000 | 0 |  | E
242 |  |  |  | Double Arm Surgical Pendant | Nos | 1195000 | 0 | 0 | 6 | 7170000 | 6 | 7170000 | 6 | 7170000 | EQP
|  | 6: TOTAL; 8: 175773220.8; 10: 39541980; 12: 215315200.8; 14: 223646437.961 |  |  | 8331237.161
Sl.No |  |  |  | Item Description | UOM | Unit Rate (Rs.) | QTY | Amount (Rs.) |  |  | QTY | Amount (Rs.) | QTY | Amount (Rs.)
Civil Supplementary
1 |  | 4: Supply and installation of Under-deck Thermocol insulation sheets of 40 mm thick having more than 30 Kg/m3 density to ceiling by brush application of bituminous adhesive to the sheets and secured with screw along with washer at the centre of the sheet supported with GI wire running diagonally to the sheet of 2mm dia. (in ICUs & MOTs Integration Room); 5: Sqm; 6: 1014; 13: 262.74; 14: 266418.36 | CS
2 |  | 4: Supply and placing of the Design Mix Plain Cement Concrete of M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Concrete Batching Plant with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials. (in 6 OTs); 5: Cum; 6: 11740; 13: 28.01; 14: 328837.4 | CS
3 |  | 4: Supply and Laying of Floor leveller compund (self smoothing mortar) to level the surface, having bulk density not less than 2 Kg/l for a fresh mortor, compressive strength not less than 20 N/mm2, initial setting time not more than 40 minutes and offer a 25 minutes working time, The surface should be walkabe after 30 min of laying. (all rooms & corridors except OTs, TIRs and Sterile corridor); 5: Sqm; 6: 1460; 13: 882.44; 14: 1288362.4 | CS
4 |  | 4: Providing dadooing to walls with glazed full body ceramic wall tiles of size 800 x 1600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. (at Entrance); 5: Sqm; 6: 4665; 13: 119.385; 14: 556931.025 | CS
5 |  | 4: Providing (1500 X 2100) single sliding door operated by elbow switches / foot switch as well as touchless sensor of 10mm thick toughened glass (Saint Gobin / Modi Guard) fixed in SS 304 grade 2 Track top channel of 45 mm (one track to hold fixed glass partition in position and second track with top rollers suitably angled to reduce resistance to movement to facilitate smooth sliding movement of the door). Single track bottom channel to be provided for fixed glass partition. Floor guide to be provided for smooth sliding of the door. Concealed door handle of (150 mm) to be provided in cutout on the sliding door for manual operation when required. All fittings provided should be of Titon /Ozone / Enox make in SS 304 - In TIRs; 5: Nos; 6: 270276; 13: 2; 14: 540552 | CS
6 |  | 4: V-Board Partitions on top of false ceiling for partitioning of sterile corridor and non-sterile corridor (for dividing corridors into zones above ceiling); 5: Sqm; 6: 3640; 13: 16; 14: 58240 | CS
7 |  | 4: GI Powder Coated Sliding Doors (0.8mm shutter sheet thk & 1.2mm frame sheet thk with Single Rebate and Honeycomb Infill) Double Leaf Door 1200 x 2100mm with Accessories (Sliding Track for Double Door, Sliding Dead Lock Enox, Concealed Handles 100mm Ahlada, Flush Bolt 300mm Ahlada, SS304 Kick Plate upto 350mm ht, DG Clear Float Glass 350x750x6mm with Adhesive Tape & Silicon Sealant) (for change rooms to corridor entrance); 5: Nos; 6: 84133; 13: 1; 14: 84133 | CS
8 |  | 4: Supply and installation of 50mm thick double skin modular wall Panels made of 0.8 mm thick powder coated GI on both the sides, with 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, flush on both sides with maximum allowable gap of 3- 4mm filled with food grade silicon sealant and placed on cold rolled galvanised bottom tracks with a recess to provide floor to wall coving flush with the wall panel. This includes all required harware for completion Panels to be covered with a protective film to avoid any damages during transportation and installation; 5: Sqm; 6: 7450; 13: 297.52; 14: 2216524 | CS
9 |  | 4: Supply and installation of 50mm thick double skin ceiling system made of 0.8 mm thick Powder Coated GI sheets on both sides, 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, panels flush towards room side with maximum allowable gap of 3-4mm at panel to panel joints filled with silicon sealant. Ceiling panels are suspended from the RCC slab by using concealed AL ceiling grid with tie rod and adjustable turn buckle arrangement etc. This includes all required hardware for completion. Panels to be covered with a protective film to avoid any damages during transportation and installation; 5: Sqm; 6: 7450; 13: 163.08; 14: 1214946 | CS
10 |  | 4: Acoustic Wall Panelling with framework consisting of 25mm high GI wall channels with fully knurled surface of 0.55mm thick bottom wedge of 80mm width, having two equal flanges of 26mm is anchored to GI studs of 50mm high. GI studs of 50mm High to be fixed to wall at 600mm centres, 25mm thick channels are then fixed perpendicular to the GI studs and suitable fixing channel is fixed to the cross channel to fix the panel to achieve overall air gap of 75mm from the wall and GI Clips for inside panel and Clips for border panel of 18mm to be fixed to the GI wall channel to achieve required shape. Secured arranging of polyester wool of – thickness/density, Prelam Board to be installed. 15mm thick Prelam perforated Wooden slat of required dia perforation & pitch is to be customised and then fixed to GI frame rigidly by using fixing channel fastened perpendicular to the cross channel with GI brackets. The boards shall be fixed to the GI frame with special cleats. (MOTs Integration Room); 5: Sqm; 6: 6350; 13: 110; 14: 698500 | CS
11 |  | 4: Accooustic Ceiling Paneling with Perforated board Fine line Grid false ceiling using 11mm thick Perforated Board sheet tiles of size 595mm x 595mm fixing to steel precoated GI wall angle of size 25mm x 25mm x 0.70mm thick along the perimeter of ceiling screw fixed to brick work / partition at 610mm center to center and suspending the frame work using precoated GI Tee section (24mm x 38mm x 0.7mm) from soffit at 1220mm center to center fixed with GI Soffit Cleat, rawl plugs and steel expansion fasteners & connecting clip to the GI Tee section with 4mm dia GI rod with galvanised spring steel level clip of PVC unversal holding clips system at 1200mm center to center and Secured arranging of polyester wool of 50mm thick 1000 GSM, Prelam Board to be installed. 15mm thick Prelam perforated Wooden slat of required dia perforation & pitch is to be customised and then fixed to GI frame rigidly by using fixing channel fastened perpendicular to the cross channel with GI brackets. The boards shall be fixed to the GI frame with special cleats. (MOTs Integration Room); 5: Sqm; 6: 5700; 13: 62; 14: 353400 | CS
12 |  | 4: Wooden Flooring with Engineered wood planks of 14mm thick (MOTs Integration Room); 5: Sqm; 6: 7300; 13: 65; 14: 474500 | CS
13 |  | 4: Skirting for Wooden Flooring with Engineered wood planks of 14mm thick (MOTs Integration Room); 5: Rmt; 6: 900; 13: 40; 14: 36000 | CS
14 |  | 4: 80% blockout Ruler Blinds for MOTs Integration Room Windows; 5: Nos; 6: 12000; 13: 3; 14: 36000 | CS
15 |  | 4: Supply and installation of double pass RO system having 2 nos feed pumps of 1.5 HP with max flow of 4000 ltr/hr including construction of sand filter of dimensions (H=1650 mm, D=325 mm) with filter media as Quartz sand of SS vessel construction and Activated Carbon filter of dimensions (H= 1650mm) with filter media as Activated carbon (IV-600) of SS vessel construction, with 4 nos of spiral wound RO membrane of size 4 inch dia x 1 m length of make ION EXCHANGE (HYDROMEN) (or) equal, 2 nos UV system with service flow of 1000 ltr/hr (Before 2nd filter and after SS tank out-let) with PEX pipeline recirculation loop to avoid contamination in pipe to supply for 10 beds in Post ICU, 4 beds in Transplant ICU and 1 for each TIR.) Drinage outlet to be provided near each RO outlet.; 5: Job; 6: 6240000; 13: 1; 14: 6240000 | CS
16 |  | 4: Water Proofing of roof and peripheral walls of south west block, 8th floor, Gandhi Hospital which includes Dismantling of existing screed and lifting of debris to ground floor, Surface preparation and cracks treatment, Providing Angle fillet/taper of 75mm X 75mm with polymer modified mortor in the ratio of cement:sand:admixture (1:1.5:1.5) (Forsoc Nitobond SBR/M-Crete PC Bond @ 10% by weight of cement), Applying 1 coat of Forsoc Nitoproof WB Primer, Application of 2 coats of pitch free based liquid applied single component elastomeric waterproofing membrane (Forsoc Nito proof 600PF/BASF HLM5000), Laying 200 GSM Geotextile Fabric, Laying of 125mm Fiber Reinforced M20 grade protective concrete screed on terrace, Control joints treatment and External walls repair with window Frame-walls joints/Gaps treatment.; 5: Job; 6: 12611958; 13: 1; 14: 12611958 | CS
17 |  | 4: Supply of Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs with borders and design as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM (1:8) prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab , including neat cement slurry of honey like consistancy spread @ 3.3 kgs per Sqm. and jointed neately with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site (excluding cost of C.C. bed) including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in-charge etc.,and overheads & contractors profit complete for finished item of work. (APSS No.701 & 707).; 5: Sqm; 6: 2550; 13: 342; 14: 872100 | CS
18 |  | 4: Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707); 5: Rmt; 6: 250; 13: 120; 14: 30000 | CS
[10 empty] | SUBTOTAL |  | PART-B |  | 27907402.185
MGPS Supplementary items
19 |  | 4: 4 Gas Digital Alarm Panels : 4 Gas Digital Alarm Panel consisting of atl necessary accessories ie Pressure sensors,reguIators,hand valves ,pressure gauges ecL(Oxygen, Nitrous oxide, Medical Air, Vacuum) (for TIRs); 5: Nos; 6: 42150; 13: 2; 14: 84300 | GS
20 |  | 4: 6 Gas Digital Alarm Panele : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. (for OTs); 5: Nos; 6: 60008; 13: 6; 14: 360048 | GS
21 |  | 4: Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. (for TIRs); 5: Nos; 6: 22201; 13: 2; 14: 44402 | GS
22 |  | 4: 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen.; 5: Job; 6: 48103; 13: 1; 14: 48103 | GS
23 |  | 4: Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED.; 5: Job; 6: 222013; 13: 1; 14: 222013 | GS
24 |  | 4: 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide.; 5: Job; 6: 48103; 13: 1; 14: 48103 | GS
25 |  | 4: 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide.; 5: Job; 6: 17401; 13: 1; 14: 17401 | GS
26 |  | 4: Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041 C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED; 5: Job; 6: 222013; 13: 1; 14: 222013 | GS
[10 empty] | SUBTOTAL |  | PART-B |  | 1046383
ELV Supplementary Items
27 |  | 4: Recording in counselling room; 5: Job; 6: 155378; 13: 1; 14: 155378 | ELVS
28 |  | 4: Local Area Network (LAN) System; 5: Job; 6: 460242; 13: 1; 14: 460242 | ELVS
[10 empty] | SUBTOTAL |  | PART-B |  | 615620
Electrical Supplementary
29 |  | 4: Supply, Transportation and installation of 20KVA / 312V DC on line UPS system (for emergency lighting in all rooms & Corridor except OTs & TIRs); 5: Nos; 6: 629358; 13: 2; 14: 1258716 | ES
30 |  | 4: 800 KVA Transformer OLTC for transformers with RTCC: Supply, Transportation, Installation, Testing and Commissioning of 800 KVA TRANSFORMER with all test reports. The Transformer shall be designed and manufactured as per IS:1180 OLTC with level-II with initial filling of oil as per IS 335-1993. 1000 A LT Breaker Kiosk - 01 No.The basic details of the Transformer are as under. Makes: Kirloskar / PETE / Esennar / Voltamp / Crompton / ABB / Schneider.; 5: Nos; 6: 4814994; 13: 1; 14: 4814994 | ES
31 |  | 4: 750 KVA Generator Set with AMF Control Panel Supply, Transportation, erection and commissioning (Excluding Foundation) of 3 Phase, 415, 50Hz, water cooled multi cylinder diesel generator set with alternator of 750 KVA output continuous rating directly coupled Engine and Alternator 750 KVA, 415 Volts with guard and mounted on a common base plate of Robust construction and complete with AMF panel having IP-52 protection, Acoustic Enclosure as per CPCB norms , sound absorbing material, t to restrict sound level up to 75 dB up to 1 Mtr distance and as per CPCB norms etc.; 5: Nos; 6: 9540000; 13: 1; 14: 9540000 | ES
[10 empty] | SUBTOTAL |  | PART-B |  | 15613710
Medical Equipment Supplementary
32 |  | 4: Monitor Stand beside Bed in ICUs & TIRs; 5: Nos; 6: 6176; 13: 31; 14: 191456 | EQPS
[10 empty] | SUBTOTAL |  | PART-B |  | 191456
[10 empty] | TOTAL |  | PART-B |  | 45374571.185
|  |  |  | GRAND TOTAL |  | PART (A+B) |  | 175773220.8 |  | 39541980 |  | 215315200.8 |  | 269021009.146
[12 empty] | TOTAL EXCESS |  | 53705808.346
[12 empty] | TCV Incl GST |  | 269021009.146
[12 empty] | BASIC VALUE |  | 227983906.0559

## CIVIL1 (hidden)
REVISED ESTIMATE OF SOTC 8TH FLOOR, SOUTH-WEST BLOCK, GANDHI HOSPITAL
S.No of RE | Tech. Spec Cl. No in TED | Item S.No | Item Code | Item Name |  |  | As Per Agreement (with 4 Ots) |  | Additional Sanction fot 2 Ots |  | Total (6 Ots) |  | As Per Work Done/To Be Done
[5 empty] | UOM | Unit Rate (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.)
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
1 | 1 | 1 | SOTC001 | Stainless Steel Pre-fabricated Wall panels. (MOTs & MOT Corridor) - Wall panels | Sqm | 15010 | 400 | 6004000 | 350 | 5253500 | 750 | 11257500 | 491.9486 | 7384148.486
2 | 1 | 199 | SOTC002 | Stainless Steel Pre-fabricated Ceiling panels In MOTs & MOTs Corridor | Sqm | 15010 | 385 | 5778850 | 78 | 1170780 | 463 | 6949630 | 263.165 | 3950106.65
4 | 2.1 | 3 | SOTC004 | Electro conductive Flooring inside MOTs | Sqm | 4035 | 160 | 645600 | 80 | 322800 | 240 | 968400 | 217.7802 | 878743.107
5 | 2.2 | 4 | SOTC005 | Flooring with Vinyl Sheets In MOT Corridor | Sqm | 3750 | 175 | 656250 | 50 | 187500 | 225 | 843750 | 87.0329 | 326373.525
17 | 8 | 15 | SOTC017 | Hermetically Sealed Doors (1.80mt x 2.10 mt) | Nos | 115000 | 4 | 460000 | 2 | 230000 | 6 | 690000 | 6 | 690000
|  |  |  | AE |  | 115000 | [6 empty] | 3 | 345000
18 | 8 | 240 | SOTC018 | (1.50mt x 2.10 mt) Sliding Automatic Sliding Doors with View Windoy of 1 Mt x 1 Mt | Nos | 525000 | 2 | 1050000 |  | 0 | 2 | 1050000 | 2 | 1050000
19 | 10 | 16 | SOTC019 | Storage Units | Nos | 75000 | 4 | 300000 | 2 | 150000 | 6 | 450000 | 6 | 450000
20 | 11 | 17 | SOTC020 | Writing Board (List Board) | Nos | 18750 | 4 | 75000 | 2 | 37500 | 6 | 112500 | 6 | 112500
39 | 1 | 34 | SOTC039 | Stainless Steel Pre-fabricated Wall panels in TIRs & TIR Corridor | Sqm | 15010 | 202 | 3032020 | 0 | 0 | 202 | 3032020 | 202 | 3032020
|  |  |  | AE |  | 15010 | [6 empty] | 136.9318 | 2055346.318
40 | 1 | 35 | SOTC040 | Stainless Steel Pre-fabricated Ceiling panels in TIRs and TIR Corridor | Sqm | 15010 | 146 | 2191460 | 0 | 0 | 146 | 2191460 | 146 | 2191460
|  |  |  | AE |  | 15010 | [6 empty] | 33.22 | 498632.2
41 | 2.1 | 202 | SOTC041 | Electro conductive Flooring inside TIRs | Sqm | 4035 | 146 | 589110 |  | 0 | 146 | 589110 | 73.6644 | 297235.854
42 | 2.2 | 36 | SOTC042 | Flooring with Vinyl Sheets In TIR Corridor | Sqm | 3750 | 61 | 228750 |  | 0 | 61 | 228750 | 61 | 228750
|  |  |  | AE |  | 3750 | [6 empty] | 70.4074 | 264027.75
48 | 8 | 42 | SOTC049 | Hermetically Sealed Doors (1.80mt x 2.10 mt) | Nos | 525000 | 3 | 1575000 |  | 0 | 3 | 1575000 | 3 | 1575000
49 | 15 | 43 | SOTC050 | 12mm thick glazed Glass partition walls in TIRs | Sqm | 650 | 40 | 26000 |  | 0 | 40 | 26000 | 40 | 26000
54 | 11 | 48 | SOTC055 | WRITING BOARDS FOR ICUS, PRE OPP | Nos | 18750 | 5 | 93750 |  | 0 | 5 | 93750 | 5 | 93750
|  |  |  | AE |  | 18750 | [6 empty] | 1 | 18750
144 |  | 116 | SOTC145 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Reinforced cement concrete) | Cum | 5400 | 10 | 54000 |  | 0 | 10 | 54000 | 10 | 54000
145 |  | 117 | SOTC146 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Unreinforced cement concrete) | Cum | 4500 | 1.5 | 6750 |  | 0 | 1.5 | 6750 | 1.5 | 6750
|  |  |  | AE |  | 4500 | [6 empty] | 50.4015 | 226806.75
146 |  | 118 | SOTC147 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Brick Masonary) | Cum | 900 | 118 | 106200 |  | 0 | 118 | 106200 | 118 | 106200
|  |  |  | AE |  | 900 | [6 empty] | 34.691 | 31221.9
147 |  | 119 | SOTC148 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Kadapa slabs or shahabad stone slabs on sand bed) | Sqm | 630 | 25 | 15750 |  | 0 | 25 | 15750 | 25 | 15750
|  |  |  | AE |  | 630 | [6 empty] | 667.9265 | 420793.695
148 |  | 120 | SOTC149 | Dismantling doors, windows and clear storey windows, Ventilators etc., (wood or steel) shutters including Chowkhats, architraves,hold fasts and other attachments etc., and stacking them within 100m lead including charge etc., complete for finished item of work. (Not exceeding 3 sqm in area) | Nos | 1800 | 57 | 102600 |  | 0 | 57 | 102600 | 57 | 102600
|  |  |  | AE |  | 1800 | [6 empty] | 146 | 262800
149 |  | 121 | SOTC150 | Conveyance of un-useful excavated earth to a distance of 16 KM for disposal including hire charges of T and P, labour charges etc., complete for finished item of work. | Cum | 900 | 250 | 225000 |  | 0 | 250 | 225000 | 250 | 225000
|  |  |  | AE |  | 900 | [6 empty] | 64.769 | 58292.1
150 | 40 | 122 | SOTC151 | RCC M 25 grade design mix (For lintels) | Cum | 18900 | 3 | 56700 |  | 0 | 3 | 56700 | 3 | 56700
|  |  |  | AE |  | 18900 | [6 empty] | 0.17 | 3213
151 | 41 | 123 | SOTC152 | RCC M 20 grade design mix (50mm thick platforms) | Sqm | 1170 | 12 | 14040 |  | 0 | 12 | 14040 | 0 | 0
152 | 41 | 124 | SOTC153 | RCC M 20 grade design mix (25 mm thick Shelves) | Sqm | 900 | 12 | 10800 |  | 0 | 12 | 10800 | 0 | 0
153 | 42 | 125 | SOTC154 | Brick Masonry work in CM (1:6) prop in superstructure | Cum | 15300 | 3 | 45900 |  | 0 | 3 | 45900 | 3 | 45900
|  |  |  | AE |  | 15300 | [6 empty] | 108.951 | 1666950.3
154 | 43 | 126 | SOTC155 | Reinforced Masonry for partition walls (100 mm thick) in CM (1:4) | Sqm | 2700 | 500 | 1350000 |  | 0 | 500 | 1350000 | 404.9325 | 1093317.75
155 | 44 | 127 | SOTC156 | PCC (1:3:6) nominal mix using 20mm size graded m/c (For bed blocks and hold fasts) (OTs screed) | Cum | 9000 | 1.5 | 13500 |  | 0 | 1.5 | 13500 | 0 | 0
156 | 45 | 128 | SOTC157 | Filling with light weight concrete in Cement Concrete (1:5:10) proportion using brick jelly for low roofs | Cum | 7200 | 23 | 165600 |  | 0 | 23 | 165600 | 16.8651 | 121428.72
157 | 46 | 129 | SOTC158 | Thermo Mechanically Treated (Fe -500/500D/550D) for RCC works | MT | 126000 | 1.25 | 157500 |  | 0 | 1.25 | 157500 | 0.7686 | 96843.6
158 | 49 | 130 | SOTC159 | Plastering 12mm thick in two coats with base coat of 8mm thick in CM (1:6) and top coat of 4mm thick in CM (1:4). for Internal walls. | Sqm | 1224 | 1600 | 1958400 |  | 0 | 1600 | 1958400 | 1600 | 1958400
|  |  |  | AE |  | 1224 | [6 empty] | 548.804 | 671736.096
159 | 51 | 131 | SOTC160 | Impervious coat to exposed RCC roof slab surfaces (APSS No. 901 and 903) For Toilets | Sqm | 360 | 77.78 | 28000.8 |  | 0 | 77.78 | 28000.8 | 43.05 | 15498
160 | 92 | 222 | SOTC161 | Providing and applying Wall putty of White Cement or Polymer or Cement based of average 1 to 2 mm thickness over plastered surface to prepare the surface even and smooth after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, applying emery paper, Sand the surface, clean & wipe off loose dust, applying knifing paste filler by putty knife / muslin pad, air dry for 2 - 3 | Sqm | 270 | 4447 | 1200690 |  | 0 | 4447 | 1200690 | 1811.5335 | 489114.045
161 | 53 | 132 | SOTC162 | Flooring with non-skid full body ceramic floor tiles | Sqm | 1710 | 85 | 145350 |  | 0 | 85 | 145350 | 85 | 145350
|  |  |  | AE |  | 1710 | [6 empty] | 13.0805 | 22367.655
162 | 55 | 133 | SOTC163 | Dadooing to walls with glazed full body Porcelain wall tiles | Sqm | 1440 | 225 | 324000 |  | 0 | 225 | 324000 | 225 | 324000
|  |  |  | AE |  | 1440 | [6 empty] | 115 | 165600
163 | 56 | 134 | SOTC164 | Dadooing to walls with glazed full body Ceramic tiles | Sqm | 1440 | 350 | 504000 |  | 0 | 350 | 504000 | 270.2175 | 389113.2
164 | 57 | 135 | SOTC165 | Painting one coat water based cement primer of interior grade I and two coats of acrylic emulsion paint for ceiling and Walls | Sqm | 360 | 4447 | 1600920 |  | 0 | 4447 | 1600920 | 1372.014 | 493925.04
165 | 59 | 136 | SOTC166 | Painting to new wood work | Sqm | 360 | 313 | 112680 |  | 0 | 313 | 112680 | 75 | 27000
166 | 60 | 137 | SOTC167 | Painting to new iron work | Sqm | 270 | 88 | 23760 |  | 0 | 88 | 23760 | 88 | 23760
|  |  |  | AE |  | 270 | [6 empty] | 38.42 | 10373.4
167 | 61 | 138 | SOTC168 | Two shutter cupboards | Sqm | 9000 | 100 | 900000 |  | 0 | 100 | 900000 | 0 | 0
168 | 64 | 139 | SOTC169 | UPVC Fixed Louvered Ventilator | Sqm | 12000 | 7 | 84000 |  | 0 | 7 | 84000 | 7 | 84000
|  |  |  | AE |  | 12000 | [6 empty] | 9.5165 | 114198
169 |  | 140 | SOTC170 | UPVC 3 track Sliding Windows | Sqm | 9000 | 15 | 135000 |  | 0 | 15 | 135000 | 15 | 135000
|  |  |  | AE |  | 9000 | [6 empty] | 30.276 | 272484
170 |  | 141 | SOTC171 | MS Grills to Windows | Sqm | 1800 | 150 | 270000 |  | 0 | 150 | 270000 | 126.42 | 227556
171 | 66 | 142 | SOTC172 | Flooring with 16 to 18 mm thick high polished granite stone slabs black colour for platforms (S.S.701 and special) | Sqm | 6300 | 50 | 315000 |  | 0 | 50 | 315000 | 50 | 315000
0
172 | 67 | 143 | SOTC173 | Doors as per approved drawings with medium teak wood frame (1500mm x 2600mm) | Sqm | 6300 | 50 | 315000 |  | 0 | 50 | 315000 | 15.4 | 97020
173 | 68 | 144 | SOTC174 | Doors as per approved drawings with medium teak wood frame (1000mm x 2100mm) | Sqm | 7400 | 45 | 333000 |  | 0 | 45 | 333000 | 17.2 | 127280
174 | 69 | 145 | SOTC175 | Doors Shutters WPC(800mm x 2100mm) | Sqm | 5400 | 40 | 216000 |  | 0 | 40 | 216000 | 33.3795 | 180249.3
175 | 70 | 146 | SOTC176 | Scientific Doors with metal door frames and door shutters made of galvanize steel | Sqm | 18000 | 45 | 810000 |  | 0 | 45 | 810000 | 45 | 810000
|  |  |  | AE |  | 18000 | [6 empty] | 24.3 | 437400
176 | 71 | 147 | SOTC177 | False ceiling as per Technical specification | Sqm | 1800 | 1400 | 2520000 |  | 0 | 1400 | 2520000 | 750 | 1350000
177 | 72 | 148 | SOTC178 | Vinyl flooring | Sqm | 3000 | 500 | 1500000 |  | 0 | 500 | 1500000 | 500 | 1500000
|  |  |  | AE |  | 3000 | [6 empty] | 164 | 492000
178 | 74 | 149 | SOTC179 | Impervious coat to exposed RCC roof slab surfacesof 20mm thick (APSS No. 901 and 903) | Sqm | 1260 | 350 | 441000 |  | 0 | 350 | 441000 | 0 | 0
179 | 63 | 233 | SOTC180 | Fixed Glass Window – 1200 x 1200 | Sqm | 5400 | 53.55 | 289170 |  | 0 | 53.55 | 289170 | 53.55 | 289170
|  |  |  | AE |  | 5400 | [6 empty] | 7.46 | 40284
180 | 95 | 223 | SOTC181 | Grouting the holes with neat cement slurry of 20mm dia with all required accessories of all materials etc., including cost & Conveyance of all labour Charges etc., complete finished item of work (*As per SSR2021-22 of S.NO:-8) | Nos | 180 | 500 | 90000 |  | 0 | 500 | 90000 | 0 | 0
181 | 96 | 224 | SOTC182 | Pressure grouting the drilled holes with neat cement slurry or with approved grout admixture using pump - excluding cost of drilling holes after fixing nozzles as technical specification approved by the department etc., including cost & Conveyance of all labour charges etc., complete finished item of work | Nos | 630 | 500 | 315000 |  | 0 | 500 | 315000 | 500 | 315000
|  |  |  | AE |  | 630 | [6 empty] | 632 | 398160
182 | 87 A | 234 | SOTC183 | Supply and fabricating,erecting and fixing inposition trusses of approved design with structural steel other than MS. | Kgs | 180 | 6500 | 1170000 |  | 0 | 6500 | 1170000 | 6500 | 1170000
183 | 87 B | 150 | SOTC184 | Supply and fixing of pre painted Galvalume Trapezoidal Profile Roofing with 0.50mm Thickness. | Sqm | 1080 | 65 | 70200 |  | 0 | 65 | 70200 | 65 | 70200
[12 empty] | Total |  | 43223650.441

## ELE1 (hidden)
REVISED ESTIMATE OF SOTC 8TH FLOOR, SOUTH-WEST BLOCK, GANDHI HOSPITAL
S.No | Tech. Spec Cl. No in TED | Item S.No | Item Code | Item Name |  |  | As Per Agreement (with 4 Ots) |  | Additional Sanction fot 2 Ots |  | Total (6 Ots) |  | As Per Work Done/To Be Done
[5 empty] | UOM | Unit Rate (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.)
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
14 | 91 | 13 | SOTC014 | Ceiling/Wall mounted CCTV Room Camera | Nos | 22500 | 4 | 90000 | 2 | 45000 | 6 | 135000 | 6 | 135000
15 | 6 | 14 | SOTC015 | LED Peripheral Lights cum clean room (OT) luminaries | Nos | 18750 | 62 | 1162500 | 40 | 750000 | 102 | 1912500 | 102 | 1912500
|  |  |  | AE |  | 18750 | [6 empty] | 5 | 93750
27 | 16.3 & 16.4 | 24 | SOTC027 | Cable connections for integration within MOTs and with Workshop Projector Hall, Networks with OFC Cable | Job | 997500 | 4 | 3990000 | 2 | 1995000 | 6 | 5985000 | 6 | 5985000
38 | 19 | 201 | SOTC038 | Electrical Installations in MOTs & TIRs | Job | 195000 | 7 | 1365000 | 2 | 390000 | 9 | 1755000 | 9 | 1755000
51 | 91 | 45 | SOTC052 | Ceiling/Wall mounted CCTV Room Camera | Nos | 12000 | 3 | 36000 |  | 0 | 3 | 36000 | 3 | 36000
55 | 91 | 49 | SOTC056 | CCTV CEILING CAMERA | Nos | 9500 | 10 | 95000 |  | 0 | 10 | 95000 | 10 | 95000
56 | 22 a | 50 | SOTC057 | Supply and Fixing of 25mm dia Conduit Pipes surface on wall. | Rmt | 110 | 10000 | 1100000 |  | 0 | 10000 | 1100000 | 10000 | 1100000
57 | 22 b | 51 | SOTC058 | Supply and Fixing of 25mm dia Conduit Pipes Concealed on wall. | Rmt | 115 | 4000 | 460000 |  | 0 | 4000 | 460000 | 4000 | 460000
58 | 23 a | 52 | SOTC059 | Wiring with run of 2 of 1.5 Sqmm Copper cable for points wiring. | Pts | 1525 | 570 | 869250 |  | 0 | 570 | 869250 | 570 | 869250
59 | 23 b | 53 | SOTC060 | Wiring with run of 2 of 1.5 Sqmm Copper cable for stairecase points wiring. | Pts | 1100 | 10 | 11000 |  | 0 | 10 | 11000 | 10 | 11000
60 | 23 c | 54 | SOTC061 | Supply and fixing of 6A/10A ISI Mark 3/2 pin Modular socket Common switch board | Pts | 900 | 25 | 22500 |  | 0 | 25 | 22500 | 25 | 22500
61 | 23 d | 55 | SOTC062 | Wiring with 3 of 1.5 sq.mm with 6A switch and 6A, 3/2 pin socket Modular type with 6A switch control fixing on separate board. | Pts | 2800 | 50 | 140000 |  | 0 | 50 | 140000 | 50 | 140000
62 | 23 e | 56 | SOTC063 | Supply and fixing of 6A switchs - 2 Nos and 6A 3/2 pin socket - 3 Nos Modular type with cover plate | Pts | 1400 | 200 | 280000 |  | 0 | 200 | 280000 | 200 | 280000
63 | 23 f | 203 | SOTC064 | Supply & fixing of 16A/6A, 2 in one socket with 16A switch control modular type | Nos | 900 | 200 | 180000 |  | 0 | 200 | 180000 | 200 | 180000
64 | 23 g | 204 | SOTC065 | Supply & fixing of 32A, socket with switch control modular | Nos | 1600 | 18 | 28800 |  | 0 | 18 | 28800 | 18 | 28800
65 | 23 h | 205 | SOTC066 | Supply & fixing of 64A, socket with 64A switch control modular type | Nos | 18000 | 4 | 72000 |  | 0 | 4 | 72000 | 4 | 72000
66 | 24 a | 57 | SOTC067 | Supply and Run of 1 of 1.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 36 | 2000 | 72000 |  | 0 | 2000 | 72000 | 2000 | 72000
67 | 24 b | 58 | SOTC068 | Supply and Run of 3 of 1.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable . | Rmt | 100 | 2000 | 200000 |  | 0 | 2000 | 200000 | 2000 | 200000
68 | 24 c | 59 | SOTC069 | Supply and Run of 3 of 2.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 145 | 8000 | 1160000 |  | 0 | 8000 | 1160000 | 8000 | 1160000
69 | 24 d | 60 | SOTC070 | Supply and Run of 3 runs of 4.0 sq mm (phase neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 230 | 5000 | 1150000 |  | 0 | 5000 | 1150000 | 5000 | 1150000
70 | 24 e | 61 | SOTC071 | Supply and Run of 3 of 6.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 325 | 300 | 97500 |  | 0 | 300 | 97500 | 300 | 97500
71 | 24 f | 62 | SOTC072 | Supply and Run of 5 of 6.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 545 | 300 | 163500 |  | 0 | 300 | 163500 | 300 | 163500
72 | 24 g | 63 | SOTC073 | Supply and Run of 5 of 10.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 850 | 500 | 425000 |  | 0 | 500 | 425000 | 500 | 425000
73 | 25 a | 64 | SOTC074 | Supply and fixing of DP Metal Enclosure with IP 20 Protection DB Make with 1 No 20A, 10 KA DP MCB | Nos | 1800 | 8 | 14400 |  | 0 | 8 | 14400 | 8 | 14400
74 | 25 b | 65 | SOTC075 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 (For Lighting DBs) | Nos | 13000 | 10 | 130000 |  | 0 | 10 | 130000 | 10 | 130000
75 | 25 c | 230 | SOTC076 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 (For Power DB's) | Nos | 13000 | 14 | 182000 |  | 0 | 14 | 182000 | 14 | 182000
76 | 25 d | 66 | SOTC077 | Supply and fixing of 8 Way VTPN DB with IP 43 Protection as per IS:13032 | Nos | 50000 | 5 | 250000 |  | 0 | 5 | 250000 | 5 | 250000
77 | 25 e | 67 | SOTC078 | Supply and fixing of cable adopteres box with cover for DBs including, massanory work etc., complete., | Nos | 6000 | 10 | 60000 |  | 0 | 10 | 60000 | 10 | 60000
78 | 26 a | 206 | SOTC079 | Providing independent earthing for Important equipment with 40mm dia 'B' class 2.5m long G.I pipe (GI Earthing) | Nos | 22500 | 18 | 405000 |  | 0 | 18 | 405000 | 18 | 405000
79 | 26 b | 68 | SOTC080 | Providing independent earthing by exacavating a pit to a depth of 2.25Mtr in all soils as per size specified in the data for Sophisticated Electronic equipment (Copper Earthing) | Nos | 54000 | 18 | 972000 |  | 0 | 18 | 972000 | 18 | 972000
80 | 26 b 1 | 69 | SOTC081 | Providing independent earthing for Important equipment with 100mm dia Heavy gauge C.I Earthing | Nos | 25000 | 6 | 150000 |  | 0 | 6 | 150000 | 6 | 150000
81 | 26 c | 70 | SOTC082 | Supply and Run of 50mm x 6mm G.I Strip | Rmt | 450 | 400 | 180000 |  | 0 | 400 | 180000 | 400 | 180000
82 | 26 d | 71 | SOTC083 | Supply and Run of 25mm x 3mm copper strip | Rmt | 300 | 400 | 120000 |  | 0 | 400 | 120000 | 400 | 120000
83 | 27 a | 207 | SOTC084 | Supply, transportation and fixing of 22W +/ 10% , >/ 2300 lumens, 1200mm length LED light | Nos | 4800 | 20 | 96000 |  | 0 | 20 | 96000 | 20 | 96000
84 | 27 b | 208 | SOTC085 | Supply, transportation and fixing 32-36W (>=3600 Lumens), 2' x2' (600mm x 600mm) slim panel LED luminaire | Nos | 4000 | 60 | 240000 |  | 0 | 60 | 240000 | 60 | 240000
85 | 27 c | 209 | SOTC086 | Supply, transportation and fixing 12 W +/-10% (>= 1200 Lumens) Down lighter back lit LED Down Light Recessed / Surface | Nos | 1400 | 215 | 301000 |  | 0 | 215 | 301000 | 215 | 301000
86 | 27 d | 210 | SOTC087 | Supply, transportation and fixing 18 W +/-10% (>= 1800 Lumens) Down lighter back lit LED Down Light | Nos | 1800 | 95 | 171000 |  | 0 | 95 | 171000 | 95 | 171000
87 | 27 e | 72 | SOTC088 | Supply, transportation and fixing ISI mark batten holder / slanting holder | Nos | 160 | 8 | 1280 |  | 0 | 8 | 1280 | 8 | 1280
88 | 27 f | 231 | SOTC089 | Supply, Transportation of energy efficient fan, 1200 mm sweep, aluminium body, consuming 28 W, BEE 5 star rated, ceiling fan | Nos | 3700 | 40 | 148000 |  | 0 | 40 | 148000 | 40 | 148000
89 | 27 f 1 | 73 | SOTC090 | Supply and fixing of Modular type Stepped electronic regulator. | Nos | 1000 | 40 | 40000 |  | 0 | 40 | 40000 | 40 | 40000
90 | 27 f 2 | 74 | SOTC091 | Labour charges for fixing of ceiling fan and regulator | Nos | 210 | 40 | 8400 |  | 0 | 40 | 8400 | 40 | 8400
91 | 27 f 3 | 75 | SOTC092 | Supply and erecting 19/20mm steel tube down rod of one meter length | Nos | 600 | 40 | 24000 |  | 0 | 40 | 24000 | 40 | 24000
92 | 27 g | 211 | SOTC093 | Supply of 12" (300mm) Light duty exhaust fan | Nos | 3000 | 5 | 15000 |  | 0 | 5 | 15000 | 5 | 15000
93 | 27 h | 212 | SOTC094 | Supply,Transportation of 12" (300mm) ISI, 900 RPM Heavy duty exhaust fan | Nos | 4900 | 10 | 49000 |  | 0 | 10 | 49000 | 10 | 49000
94 | 27 i | 76 | SOTC095 | Labour charges for fixing the exhaust fan in wall with necessary connections | Nos | 900 | 15 | 13500 |  | 0 | 15 | 13500 | 15 | 13500
95 | 27 j | 77 | SOTC096 | Supply and fixing of GI louver shutter including GI mesh | Nos | 3200 | 15 | 48000 |  | 0 | 15 | 48000 | 15 | 48000
96 | 28 a | 213 | SOTC097 | Main Power Panel with 1000A 4 Pole ACB as incomer - 1 No and out goings 800 A 4P MCCB - 1 No., 630 A 4P MCCB - 1 No., 400A 4P MCCB - 4 Nos & 250A 4P MCCB - 3 No's with required Digital Ammeter and Voltmer, LED Indicators | Nos | 1315000 | 1 | 1315000 |  | 0 | 1 | 1315000 | 1 | 1315000
97 | 28 b | 214 | SOTC098 | Floor Power Panel : Incomer: 630A 4 Pole MCCB,- 1 No Outgoings 250 A 4P MCCB - 4 No's 125 A 4P MCCB - 10 No's, 63 A 4P MCCB - 4 No's with required Digital Ammeter and Voltmer, LED Indicators | Nos | 875000 | 1 | 875000 |  | 0 | 1 | 875000 | 1 | 875000
98 | 28 c | 215 | SOTC099 | Electrical Lighting Panels : Incomer: 250 A 4 Pole MCCB - 1 No, Out Goings 125 A 4P MCCB - 4 No's 63 A 4P MCCB - 3 No's with required Digital Ammeter and Voltmer, LED Indicators | Nos | 370000 | 2 | 740000 |  | 0 | 2 | 740000 | 2 | 740000
99 | 29 d | 78 | SOTC100 | 130KVAR Out Door Capacitor panel : Incomer: 250A FP MCCB - 1 No, 63A 10KA TP MCB - 9 Nos. 20 KVAR Capacitor Duty contactors - 5 Nos., 10 KVAR Capacitor Duty contactors - 2 Nos, .5 KVAR Capacitor Duty contactors - 2 Nos. 12 stage APFC Relay - 1 No | Nos | 450000 | 1 | 450000 |  | 0 | 1 | 450000 | 1 | 450000
100 |  | 232 | SOTC101 | 630 KVA Transformer OLTC for transformers with RTCC: Supply, Transportation, Installation, Testing and Commissioning of 630 KVA TRANSFORMER with all test reports. The Transformer shall be designed and manufactured as per IS:1180 OLTC with level-II with initial filling of oil as per IS 335-1993. 1000 A LT Breaker Kiosk - 01 No.The basic details of the Transformer are as under. Makes: Kirloskar / PETE / Esennar / Voltamp / Crompton / ABB / Schneider. | Nos | 4000000 | 1 | 4000000 |  | 0 | 1 | 4000000 | 0 | 0
101 | 30 a | 79 | SOTC102 | Supply of 25 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 300 | 200 | 60000 |  | 0 | 200 | 60000 | 200 | 60000
102 | 30 b | 80 | SOTC103 | Supply of 50 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 560 | 200 | 112000 |  | 0 | 200 | 112000 | 200 | 112000
103 | 30 c | 81 | SOTC104 | Supply of 70 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 750 | 75 | 56250 |  | 0 | 75 | 56250 | 75 | 56250
104 | 30 d | 82 | SOTC105 | Supply of 120 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 1050 | 50 | 52500 |  | 0 | 50 | 52500 | 50 | 52500
105 | 30 e | 83 | SOTC106 | Supply of 185 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 1500 | 50 | 75000 |  | 0 | 50 | 75000 | 50 | 75000
106 | 30 f | 84 | SOTC107 | Supply of 240 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 1900 | 100 | 190000 |  | 0 | 100 | 190000 | 100 | 190000
107 | 30 g | 85 | SOTC108 | Supply of 300 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 2400 | 500 | 1200000 |  | 0 | 500 | 1200000 | 500 | 1200000
108 | 31 a | 86 | SOTC109 | Termination of UG cables of 3.5 core 25 Sq.mm | Nos | 850 | 8 | 6800 |  | 0 | 8 | 6800 | 8 | 6800
109 | 31 b | 87 | SOTC110 | Termination of UG cables of 3.5 core 50 Sq.mm | Nos | 1200 | 8 | 9600 |  | 0 | 8 | 9600 | 8 | 9600
110 | 31 c | 88 | SOTC111 | Termination of UG cables of 3.5 core 70 Sq.mm | Nos | 1500 | 8 | 12000 |  | 0 | 8 | 12000 | 8 | 12000
111 | 31 d | 89 | SOTC112 | Termination of UG cables of 3.5 core 120 Sq.mm | Nos | 1900 | 4 | 7600 |  | 0 | 4 | 7600 | 4 | 7600
112 | 31 e | 90 | SOTC113 | Termination of UG cables of 3.5 core 185 Sq.mm | Nos | 2500 | 4 | 10000 |  | 0 | 4 | 10000 | 4 | 10000
113 | 31 f | 91 | SOTC114 | Termination of UG cables of 3.5 core 240 Sq.mm | Nos | 3500 | 4 | 14000 |  | 0 | 4 | 14000 | 4 | 14000
114 | 31 g | 92 | SOTC115 | Termination of UG cables of 3.5 core 300 Sq.mm | Nos | 4000 | 12 | 48000 |  | 0 | 12 | 48000 | 12 | 48000
115 | 31 h | 93 | SOTC116 | Earth work excavation of Trench laying of U.G cables up to 70 sqmm | Rmt | 1100 | 100 | 110000 |  | 0 | 100 | 110000 | 100 | 110000
116 | 31 i | 94 | SOTC117 | Earth work excavation of Trench laying of U.G cables from 95 Sqmm | Rmt | 1150 | 100 | 115000 |  | 0 | 100 | 115000 | 100 | 115000
117 | 31 j | 95 | SOTC118 | Laying of PVC armoured under ground cable up to 95 Sqmm on wall | Rmt | 125 | 200 | 25000 |  | 0 | 200 | 25000 | 200 | 25000
118 | 31 k | 96 | SOTC119 | Laying of PVC armoured under ground cable from 120 Sq.mm to 400 Sqmm saddles on wall | Rmt | 270 | 700 | 189000 |  | 0 | 700 | 189000 | 700 | 189000
119 | 32 a | 97 | SOTC120 | Supply, Transportation and Installation of 150mm x 50mm x 2mm thick hot dip GI perforated cable tray | Rmt | 1295 | 200 | 259000 |  | 0 | 200 | 259000 | 200 | 259000
120 | 32 b | 98 | SOTC121 | Supply, Transportation and Installation of 300mm x 50mm x 2mm thick thick hot dip GI perforated cable tray | Rmt | 4500 | 100 | 450000 |  | 0 | 100 | 450000 | 100 | 450000
121 | 33 a | 99 | SOTC122 | Supply, Transportation and installation of 10KVA / 312V DC on line UPS system | Nos | 400000 | 7 | 2800000 | 2 | 800000 | 9 | 3600000 | 9 | 3600000
122 | 33 b | 100 | SOTC123 | Supply and fixing of 12V, 150 AH MF battery | Nos | 25000 | 182 | 4550000 | 52 | 1300000 | 234 | 5850000 | 234 | 5850000
|  |  |  | AE |  | 25000 | [6 empty] | 118 | 2950000
123 | 33 c | 101 | SOTC124 | Supply and providing of UPS cum battery rack 20 batteries | Nos | 30000 | 7 | 210000 | 2 | 60000 | 9 | 270000 | 9 | 270000
|  |  |  | AE |  | 30000 | [6 empty] | 2 | 60000
124 | 33 d | 102 | SOTC125 | Supply, Transportation, Installation, Testing and commissioning of storage / Pressure type 5 Star rated water heater with ABS plastic body of 15 Ltrs | Nos | 16000 | 7 | 112000 |  | 0 | 7 | 112000 | 7 | 112000
|  |  |  | AE |  | 16000 | [6 empty] | 4 | 64000
125 | 34 | 103 | SOTC126 | 26 persons ICU bed cum passenger lift (1768 Kgs) G+8 Floors, 9 stops,9 Openings (Cost Includes amount for Construction of Shaft / Cladding from Ground to 8th Floor) | Nos | 10495000 | 1 | 10495000 |  | 0 | 1 | 10495000 | 1 | 10495000
241 |  |  |  | Electrical connections for 2 UPS | Job | 100000 |  |  | 1 | 100000 | 1 | 100000 | 0
[12 empty] | TOTAL |  | 49845130

## ELV1 (hidden)
REVISED ESTIMATE OF SOTC 8TH FLOOR, SOUTH-WEST BLOCK, GANDHI HOSPITAL
S.No | Tech. Spec Cl. No in TED | Item S.No | Item Code | Item Name |  |  | As Per Agreement (with 4 Ots) |  | Additional Sanction fot 2 Ots |  | Total (6 Ots) |  | As Per Work Done/To Be Done
[5 empty] | UOM | Unit Rate (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.)
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
141 | 37 | 221 | SOTC142 | Telephone & EPABX System | Job | 1000000 | 1 | 1000000 |  | 0 | 1 | 1000000 | 1 | 1000000
142 | 38 | 114 | SOTC143 | Local Area Network (LAN) System | Job | 1250000 | 1 | 1250000 |  | 0 | 1 | 1250000 | 1 | 1250000
143 | 39 | 115 | SOTC144 | Biometric Access Control System | Nos | 300000 | 2 | 600000 |  | 0 | 2 | 600000 | 2 | 600000
|  |  |  | AE |  | 300000 | [6 empty] | 1 | 300000
[12 empty] | TOTAL |  | 3150000

## FF (hidden)
REVISED ESTIMATE OF SOTC 8TH FLOOR, SOUTH-WEST BLOCK, GANDHI HOSPITAL
S.No | Tech. Spec Cl. No in TED | Item S.No | Item Code | Item Name |  |  | As Per Agreement (with 4 Ots) |  | Additional Sanction fot 2 Ots |  | Total (6 Ots) |  | As Per Work Done/To Be Done
[5 empty] | UOM | Unit Rate (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.)
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
133 | 36.2 | 108 | SOTC134 | Automatic Smoke Detection System | Job | 1425000 | 1 | 1425000 |  | 0 | 1 | 1425000 | 1 | 1425000
134 | 36.3 | 109 | SOTC135 | Automatic Fire Alarm System | Job | 1400000 | 1 | 1400000 |  | 0 | 1 | 1400000 | 1 | 1400000
135 | 36.4 | 219 | SOTC136 | Supply & Fixing of 4.5Kg, CO2 Type Fire Extinguisher. | Nos | 27000 | 6 | 162000 |  | 0 | 6 | 162000 | 6 | 162000
136 | 36.5 | 110 | SOTC137 | Supply and fixing of ABC stored pressure squeeze grip type fire extinguishers, 9 kg capacity. | Nos | 16000 | 6 | 96000 |  | 0 | 6 | 96000 | 6 | 96000
137 | 36.6 | 111 | SOTC138 | Supply and fixing of ABC Powder MAP 4 Kg Fire extinguisher | Nos | 11000 | 10 | 110000 |  | 0 | 10 | 110000 | 10 | 110000
138 | 36.7 | 112 | SOTC139 | Supply and fixing of 2 Kg Fire extinguisher Clean Agent | Nos | 22500 | 10 | 225000 |  | 0 | 10 | 225000 | 10 | 225000
139 | 36.8 | 113 | SOTC140 | Supply and fixing of Escape signage boards in Rigid Photo luminescent based glow | Nos | 2000 | 150 | 300000 |  | 0 | 150 | 300000 | 150 | 300000
140 | 36.9 | 220 | SOTC141 | Supply & Fixing of Powder Coated Fire Rated doors. | Sqm | 29000 | 6 | 174000 |  | 0 | 6 | 174000 | 6 | 174000
|  |  |  | AE |  | 29000 | [6 empty] | 7.8 | 226200
[12 empty] | TOTAL |  | 4118200

## EQP1 (hidden)
REVISED ESTIMATE OF SOTC 8TH FLOOR, SOUTH-WEST BLOCK, GANDHI HOSPITAL
S.No | Tech. Spec Cl. No in TED | Item S.No | Item Code | Item Name |  |  | As Per Agreement (with 4 Ots) |  | Additional Sanction fot 2 Ots |  | Total (6 Ots) |  | As Per Work Done/To Be Done
[5 empty] | UOM | Unit Rate (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.)
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
3 | 1.5 | 2 | SOTC003 | Dynamic Hatch Box | Nos | 295000 | 2 | 590000 | 1 | 295000 | 3 | 885000 | 0 | 0
9 | 4 | 8 | SOTC009 | Pressure Relief Dampers | Nos | 22500 | 4 | 90000 | 2 | 45000 | 6 | 135000 | 6 | 135000
10 | 5.1 | 9 | SOTC010 | Single arm Anesthesia Pendants (Imported) | Nos | 1195000 | 4 | 4780000 | 2 | 2390000 | 6 | 7170000 | 6 | 7170000
11 | 5.2 | 10 | SOTC011 | Triple Dome Ceiling OT LED Lights (Imported) | Nos | 4750000 | 2 | 9500000 |  | 0 | 2 | 9500000 | 2 | 9500000
|  |  |  | AE |  | 4750000 | [6 empty] | 1 | 4750000
12 | 5.3 | 11 | SOTC012 | Double Dome Ceiling OT LED Lights (Imported) | Nos | 3550000 | 2 | 7100000 | 2 | 7100000 | 4 | 14200000 | 3 | 10650000
13 | 5.4 | 12 | SOTC013 | Detachable Hi Definition Cameras in Triple Dome Ceiling OT Lights | Nos | 995000 | 2 | 1990000 | 1 | 995000 | 3 | 2985000 | 3 | 2985000
0
16 | 7 | 239 | SOTC016 | View Window with Motorised Blinds of 1 Mt Length & 1 Mt Height | Nos | 115000 | 7 | 805000 | 2 | 230000 | 9 | 1035000 | 9 | 1035000
|  |  |  | AE |  | 115000 | [6 empty] | 5 | 575000
21 | 12 | 18 | SOTC021 | X-Ray CT Scan LED viewing Screen | Nos | 37500 | 4 | 150000 | 2 | 75000 | 6 | 225000 | 6 | 225000
22 | 13 | 19 | SOTC022 | Touch Screen Surgeon Control Panels | Nos | 385000 | 4 | 1540000 | 2 | 770000 | 6 | 2310000 | 6 | 2310000
|  |  |  | AE |  | 385000 | [6 empty] | 3 | 1155000
23 | 14 | 20 | SOTC023 | 3-Bay Scrub Stations/Sinks | Nos | 368750 | 2 | 737500 |  | 0 | 2 | 737500 | 2 | 737500
|  |  |  | AE |  | 368750 | [6 empty] | 1 | 368750
24 | 16 | 21 | SOTC024 | Video and Image Management system | Nos | 8000000 | 1 | 8000000 |  | 0 | 1 | 8000000 | 1 | 8000000
25 | 16.1 | 22 | SOTC025 | Medical Grade Monitors 32 inch 4 K Resolution | Nos | 1295000 | 4 | 5180000 | 2 | 2590000 | 6 | 7770000 | 6 | 7770000
26 | 16.2 | 23 | SOTC026 | Wall mounted large screen display 55 inch (Commercial Grade) | Nos | 495000 | 2 | 990000 |  | 0 | 2 | 990000 | 2 | 990000
28 | 16.5 | 25 | SOTC028 | Wireless Microphone | Nos | 255000 | 1 | 255000 |  | 0 | 1 | 255000 | 1 | 255000
29 | 16.6 | 26 | SOTC029 | Digital mixer Amplifier | Nos | 245000 | 1 | 245000 |  | 0 | 1 | 245000 | 1 | 245000
30 | 16.7 | 27 | SOTC030 | Ceiling Mounted Speakers | Nos | 15000 | 4 | 60000 | 2 | 30000 | 6 | 90000 | 6 | 90000
31 | 16.8 | 28 | SOTC031 | Video Conferencing System | Nos | 1195000 | 1 | 1195000 |  | 0 | 1 | 1195000 | 1 | 1195000
32 | 17.1 | 29 | SOTC032 | Home Theatre Power Conditioner, 230 V | Nos | 145000 | 1 | 145000 |  | 0 | 1 | 145000 | 1 | 145000
33 | 17.2 | 30 | SOTC033 | Amplifier (8 Channel) | Nos | 245000 | 1 | 245000 |  | 0 | 1 | 245000 | 1 | 245000
34 | 17.3 | 31 | SOTC034 | HiFi Active Sub Woofer | Nos | 50000 | 1 | 50000 |  | 0 | 1 | 50000 | 1 | 50000
35 | 17.5 | 32 | SOTC035 | 4K Laser Projection TV | Nos | 1495000 | 1 | 1495000 |  | 0 | 1 | 1495000 | 1 | 1495000
36 | 17.6 & 17.7 | 200 | SOTC036 | Equalization & Loud Speaker Control System | Nos | 40000 | 1 | 40000 |  | 0 | 1 | 40000 | 1 | 40000
37 | 17.8 | 33 | SOTC037 | Sound Analog Mixer | Nos | 245000 | 1 | 245000 |  | 0 | 1 | 245000 | 1 | 245000
47 | 4 | 41 | SOTC047 | Pressure Relief Dampers | Nos | 22500 | 3 | 67500 |  | 0 | 3 | 67500 | 3 | 67500
50 | 15 | 44 | SOTC051 | Wall mounted LED TV43 inchesFull HD | Nos | 165000 | 3 | 495000 |  | 0 | 3 | 495000 | 3 | 495000
53 | 12 | 47 | SOTC054 | X-RAY VIEWERS FOR ALL ICUS AND PRE OPP AREAS AND DOCTORS ROOMS | Nos | 37500 | 5 | 187500 |  | 0 | 5 | 187500 | 5 | 187500
|  |  |  | AE | [8 empty] | 1 | 37500
242 |  |  |  | Double Arm Surgical Pendant | Nos | 1195000 | 0 | 0 | 6 | 7170000 | 6 | 7170000 | 6 | 7170000
[12 empty] | TOTAL |  | 70318750

## AC (hidden)
REVISED ESTIMATE OF SOTC 8TH FLOOR, SOUTH-WEST BLOCK, GANDHI HOSPITAL
S.No | Tech. Spec Cl. No in TED | Item S.No | Item Code | Item Name |  |  | As Per Agreement (with 4 Ots) |  | Additional Sanction fot 2 Ots |  | Total (6 Ots) |  | As Per Work Done/To Be Done
[5 empty] | UOM | Unit Rate (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.)
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
6 | 3 | 5 | SOTC006 | Uni Directional Ceiling Laminar Airflow Systems | Nos | 465000 | 4 | 1860000 | 2 | 930000 | 6 | 2790000 | 6 | 2790000
7 | 3.1 | 6 | SOTC007 | Air Handling Units (AHUs) 11 TR | Nos | 1495000 | 4 | 5980000 | 2 | 2990000 | 6 | 8970000 | 6 | 8970000
8 | 3.2 | 7 | SOTC008 | Condensing Units | Nos | 345000 | 4 | 1380000 | 2 | 690000 | 6 | 2070000 | 6 | 2070000
|  |  |  | AE |  | 345000 | [6 empty] | 4 | 1380000
43 | 3 | 37 | SOTC043 | Uni Directional Ceiling Laminar Airflow Systems | Nos | 395000 | 3 | 1185000 |  | 0 | 3 | 1185000 | 3 | 1185000
44 | 3.1 | 38 | SOTC044 | Air Handling Units (AHUs) 11 TR | Nos | 1495000 | 2 | 2990000 |  | 0 | 2 | 2990000 | 2 | 2990000
45 | 3.1 | 39 | SOTC045 | Air Handling Units (AHUs) 8.5 TR | Nos | 1195000 | 1 | 1195000 |  | 0 | 1 | 1195000 | 1 | 1195000
46 | 3.2 | 40 | SOTC046 | Condensing Units | Nos | 345000 | 3 | 1035000 |  | 0 | 3 | 1035000 | 3 | 1035000
|  |  |  | AE |  | 345000 | [6 empty] | 3 | 1035000
126 | 35.1 | 104 | SOTC127 | 1.50 TR with , 18000 BTU/Hr High Wall mount Split Air Conditioners | Nos | 150000 | 6 | 900000 |  | 0 | 6 | 900000 | 6 | 900000
|  |  |  | AE |  | 150000 | [6 empty] | 1 | 150000
127 | 35.2 | 105 | SOTC128 | 2.0 TR with , 24000 BTU/Hr High Wall mount Split Air Conditioners | Nos | 210000 | 2 | 420000 |  | 0 | 2 | 420000 | 2 | 420000
|  |  |  | AE |  | 210000 | [6 empty] | 4 | 840000
128 | 35.3 | 106 | SOTC129 | Voltage stabilizer for 4 KVA maximum load | Nos | 7000 | 6 | 42000 |  | 0 | 6 | 42000 | 6 | 42000
|  |  |  | AE |  | 7000 | [6 empty] | 1 | 7000
129 | 35.4 | 107 | SOTC130 | Voltage stabilizer for 5 KVA maximum load | Nos | 8500 | 2 | 17000 |  | 0 | 2 | 17000 | 2 | 17000
|  |  |  | AE |  | 8500 | [6 empty] | 4 | 34000
130 | 35.5 | 216 | SOTC131 | Ductable Air Conditioners 11.0 TR with ISEER ≥ 4 | Nos | 1200000 | 1 | 1200000 |  | 0 | 1 | 1200000 | 1 | 1200000
131 | 35.6 | 217 | SOTC132 | Ductable Air Conditioners 8.5 TR with ISEER ≥ 4 | Nos | 1000000 | 2 | 2000000 |  | 0 | 2 | 2000000 | 2 | 2000000
|  |  |  | AE |  | 1000000 | [6 empty] | 2 | 2000000
132 | 35.7 | 218 | SOTC133 | Ductable Air Conditioners 5.5 TR with ISEER ≥ 4 | Nos | 900000 | 1 | 900000 |  | 0 | 1 | 900000 | 1 | 900000
|  |  |  | AE |  | 900000 | [6 empty] | 2 | 1800000
[12 empty] | TOTAL |  | 32960000

## P (hidden)
REVISED ESTIMATE OF SOTC 8TH FLOOR, SOUTH-WEST BLOCK, GANDHI HOSPITAL
S.No | Tech. Spec Cl. No in TED | Item S.No | Item Code | Item Name |  |  | As Per Agreement (with 4 Ots) |  | Additional Sanction fot 2 Ots |  | Total (6 Ots) |  | As Per Work Done/To Be Done
[5 empty] | UOM | Unit Rate (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.)
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
184 | 75 | 225 | SOTC185 | 4" (101.6mm) multi floor trap with jali - UPVC/SWR | Nos | 270 | 25 | 6750 |  | 0 | 25 | 6750 | 25 | 6750
|  |  |  | AE |  | 270 | [6 empty] | 19 | 5130
185 | 76 | 151 | SOTC186 | 580mm x 440mm long Orissa pan white glazed Water Closet | Nos | 5400 | 4 | 21600 |  | 0 | 4 | 21600 | 4 | 21600
186 | 77 | 152 | SOTC187 | European Water Closet of 1st quality | Nos | 6300 | 9 | 56700 |  | 0 | 9 | 56700 | 9 | 56700
187 | 78 | 153 | SOTC188 | Indian make Flat Back Wash Hand Basin 1st quality | Nos | 3600 | 16 | 57600 |  | 0 | 16 | 57600 | 15 | 54000
188 | 79 | 154 | SOTC189 | CP finish brass soap dish | Nos | 1100 | 21 | 23100 |  | 0 | 21 | 23100 | 21 | 23100
189 | 80 | 155 | SOTC190 | TV shape mirror with plastic frame of size 609.6mm x 457.2mm | Nos | 630 | 25 | 15750 |  | 0 | 25 | 15750 | 15 | 9450
190 | 81 | 156 | SOTC191 | 25.4mm dia , 609.6mm long aluminium anodized towel rods | Nos | 540 | 36 | 19440 |  | 0 | 36 | 19440 | 21 | 11340
191 | 82 | 156 | SOTC192 | 15 mm brass body CP finish bib tap of not less than 300 grams weight | Nos | 540 | 25 | 13500 |  | 0 | 25 | 13500 | 14 | 7560
192 | 87 C | 158 | SOTC193 | Self Closing Tap - Push Type | Nos | 720 | 25 | 18000 |  | 0 | 25 | 18000 | 15 | 10800
193 | 84 | 159 | SOTC194 | Chromium plated finish brass body quarter turn Bibcock cum Health Faucet | Nos | 3600 | 12 | 43200 |  | 0 | 12 | 43200 | 12 | 43200
|  |  |  | AE |  | 3600 | [6 empty] | 4 | 14400
194 | 85 | 160 | SOTC195 | Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings - 15.90mm OD pipe | Rmt | 270 | 55 | 14850 |  | 0 | 55 | 14850 | 55 | 14850
|  |  |  | AE |  | 270 | [6 empty] | 53.234 | 14373.18
195 | 85 | 161 | SOTC196 | Ashirvad/Ajay/Astral Flowguard or equivalent CPVC Pipes and Fittings - 22.20mm OD pipe | Rmt | 360 | 115 | 41400 |  | 0 | 115 | 41400 | 115 | 41400
|  |  |  | AE |  | 360 | [6 empty] | 14.7065 | 5294.34
196 | 85 | 162 | SOTC197 | Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings -28.60mm OD pipe | Rmt | 450 | 143 | 64350 |  | 0 | 143 | 64350 | 115.5 | 51975
197 | 86 | 163 | SOTC198 | Bronze Gate/ Globe valve - 25mm Nominal bore | Nos | 1440 | 15 | 21600 |  | 0 | 15 | 21600 | 15 | 21600
|  |  |  | AE |  | 1440 | [6 empty] | 5 | 7200
198 | 87 | 164 | SOTC199 | SWR PVC pipes (Prince/ Sudhakar/ Kisan/ Supreme or any ISI brand) 4 Kg/Sq.cm. - 75mmdia | Rmt | 450 | 145 | 65250 |  | 0 | 145 | 65250 | 84 | 37800
199 | 87 | 165 | SOTC200 | SWR PVC pipes (Prince/ Sudhakar/ Kisan/ Supreme or any ISI brand) 4 Kg/Sq.cm. -110mmdia | Rmt | 540 | 145 | 78300 |  | 0 | 145 | 78300 | 68.25 | 36855
200 | 90 | 226 | SOTC201 | Supplying and fixing15 mm nominal size 152.0 mm CP finish iron body shower rose 1st quality including cost and conveyance of all materials, labour charges , overheads & contractors profit for finished item of work in all floors. | Nos | 630 | 5 | 3150 |  | 0 | 5 | 3150 | 5 | 3150
|  |  |  | AE |  | 630 | [6 empty] | 1 | 630
201 | 87 D | 166 | SOTC202 | Supply and Fixing of white glazed flat back bowl urinals | Nos | 2700 | 4 | 10800 |  | 0 | 4 | 10800 | 0 | 0
202 | 87 E | 227 | SOTC203 | Supply and fixing of 16mm to 20 mm thick ploished marbles slab partitions of size 4'0"*2'0" | Nos | 3600 | 10 | 36000 |  | 0 | 10 | 36000 | 0 | 0
[12 empty] | TOTAL |  | 499157.52

## MGPS (hidden)
REVISED ESTIMATE OF SOTC 8TH FLOOR, SOUTH-WEST BLOCK, GANDHI HOSPITAL
S.No | Tech. Spec Cl. No in TED | Item S.No | Item Code | Item Name |  |  | As Per Agreement (with 4 Ots) |  | Additional Sanction fot 2 Ots |  | Total (6 Ots) |  | As Per Work Done/To Be Done
[5 empty] | UOM | Unit Rate (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.)
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
52 | 88.6 | 46 | SOTC053 | BED HEAD PANEL FOR TIR WITH DOUBLE OUTLETS AND ELECTRICAL OUTLETS | Nos | 49500 | 3 | 148500 |  | 0 | 3 | 148500 | 3 | 148500
203 | 88.1 | 167 | SOTC204 | 28 mm dia. and 0.90 mm thick Copper Pipe Lines for Main lines | Rmt | 1750 | 700 | 1225000 |  | 0 | 700 | 1225000 | 700 | 1225000
|  |  |  | AE |  | 1750 | [6 empty] | 133 | 232750
204 | 88.1 | 168 | SOTC205 | 42 mm dia. and 1.20 mm thick Copper Pipe Lines for Main lines | Rmt | 2250 | 200 | 450000 |  | 0 | 200 | 450000 | 200 | 450000
|  |  |  | AE |  | 2250 | [6 empty] | 27 | 60750
205 | 88.1 | 169 | SOTC206 | 54 mm dia. and 1.20 mm thick Copper Pipe Lines for Main lines | Rmt | 2950 | 550 | 1622500 |  | 0 | 550 | 1622500 | 550 | 1622500
|  |  |  | AE |  | 2950 | [6 empty] | 14 | 41300
206 | 88.1 | 170 | SOTC207 | 12 mm dia. and 0.70 mm thick Copper Pipe Lines for distribution lines | Rmt | 650 | 320 | 208000 |  | 0 | 320 | 208000 | 320 | 208000
|  |  |  | AE |  | 650 | [6 empty] | 224 | 145600
207 | 88.1 | 171 | SOTC208 | 15 mm dia. and 0.90 mm thick Copper Pipe Lines for distribution lines | Rmt | 950 | 525 | 498750 |  | 0 | 525 | 498750 | 525 | 498750
|  |  |  | AE |  | 950 | [6 empty] | 232 | 220400
208 | 88.1 | 172 | SOTC209 | 22 mm dia. and 0.90 mm thick Copper Pipe Lines for distribution lines | Rmt | 1450 | 530 | 768500 |  | 0 | 530 | 768500 | 530 | 768500
|  |  |  | AE |  | 1450 | [6 empty] | 65 | 94250
209 | 88.2 | 228 | SOTC210 | 15 mm (1/2") Isolation Valves | Nos | 1500 | 40 | 60000 |  | 0 | 40 | 60000 | 31 | 46500
210 | 88.2 | 229 | SOTC211 | 22 mm (3/4") Isolation Valves | Nos | 2500 | 15 | 37500 |  | 0 | 15 | 37500 | 14 | 35000
211 | 88.2 | 173 | SOTC212 | 28 mm Isolation Valves | Nos | 3500 | 3 | 10500 | 2 | 7000 | 5 | 17500 | 5 | 17500
|  |  |  | AE |  | 3500 | [6 empty] | 4 | 14000
212 | 88.2 | 174 | SOTC213 | 42 mm Isolation Valves | Nos | 4500 | 2 | 9000 | 3 | 13500 | 5 | 22500 | 4 | 18000
213 | 88.2 | 175 | SOTC214 | 54 mm Isolation Valves | Nos | 5500 | 2 | 11000 | 1 | 5500 | 3 | 16500 | 3 | 16500
|  |  |  | AE |  | 5500 | [6 empty] | 7 | 38500
214 | 88.3 | 176 | SOTC215 | Gas Outlet Points with probes for Oxygen with S Brackets | Nos | 2850 | 189 | 538650 |  | 0 | 189 | 538650 | 189 | 538650
|  |  |  | AE |  | 2850 | [6 empty] | 17 | 48450
215 | 88.4 | 177 | SOTC216 | 2 Gas Digital Area Alarm Panels | Nos | 25000 | 2 | 50000 |  | 0 | 2 | 50000 | 0 | 0
216 | 88.4 | 178 | SOTC217 | 3 Gas Digital Area Alarm Panels | Nos | 30000 | 4 | 120000 |  | 0 | 4 | 120000 | 4 | 120000
|  |  |  | AE |  | 30000 | [6 empty] | 1 | 30000
217 | 88.4 | 179 | SOTC218 | 5 Gas Digital Area Alarm Panels | Nos | 40000 | 5 | 200000 | 1 | 40000 | 6 | 240000 | 0 | 0
218 | 88.4 | 180 | SOTC219 | Master Digital Alarm Panels | Nos | 50000 | 1 | 50000 |  | 0 | 1 | 50000 | 1 | 50000
219 | 88.5 | 181 | SOTC220 | BPC Flow meter with Humidifier bottle and L adapter | Nos | 2250 | 27 | 60750 |  | 0 | 27 | 60750 | 27 | 60750
|  |  |  | AE |  | 2250 | [6 empty] | 16 | 36000
220 | 88.5 | 182 | SOTC221 | L Type Adapter for Oxygen Flow meters | Nos | 1250 | 27 | 33750 |  | 0 | 27 | 33750 | 27 | 33750
221 | 88.5 | 183 | SOTC222 | Kit for conversion of Oxygen | Nos | 1650 | 27 | 44550 |  | 0 | 27 | 44550 | 18 | 29700
222 | 88.5 | 184 | SOTC223 | Suction Jars of 600 ml capacity | Nos | 3450 | 27 | 93150 |  | 0 | 27 | 93150 | 27 | 93150
|  |  |  | AE |  | 3450 | [6 empty] | 19 | 65550
223 | 88.5 | 185 | SOTC224 | Adapters for Vacuum | Nos | 750 | 27 | 20250 |  | 0 | 27 | 20250 | 27 | 20250
224 | 88.5 | 186 | SOTC225 | Adapters for Air | Nos | 750 | 27 | 20250 |  | 0 | 27 | 20250 | 27 | 20250
225 | 88.5 | 187 | SOTC226 | Adapters for Nitrous Oxide | Nos | 750 | 15 | 11250 |  | 0 | 15 | 11250 | 15 | 11250
226 | 88.5 | 188 | SOTC227 | Vacuum Tube | Nos | 550 | 27 | 14850 | 58 | 31900 | 85 | 46750 | 85 | 46750
|  |  |  | AE |  | 550 | [6 empty] | 30 | 16500
227 | 88.6 | 189 | SOTC228 | Bed Head wall panel horizontal 1500 mm long single railing | Nos | 35000 | 27 | 945000 |  | 0 | 27 | 945000 | 27 | 945000
|  |  |  | AE |  | 35000 | [6 empty] | 4 | 140000
228 | 88.7 b | 190 | SOTC229 | Valve box -2 services | Nos | 9500 | 1 | 9500 |  | 0 | 1 | 9500 | 0 | 0
229 | 88.7 b | 191 | SOTC230 | Valve box -3 services | Nos | 14500 | 3 | 43500 |  | 0 | 3 | 43500 | 3 | 43500
|  |  |  | AE |  | 14500 | [6 empty] | 2 | 29000
230 | 88.7 b | 192 | SOTC231 | Valve box -6 services | Nos | 22500 | 1 | 22500 | 5 | 112500 | 6 | 135000 | 6 | 135000
231 | 88.8 a | 193 | SOTC232 | 4 + 4 size of CO2 manifold System | Job | 40000 | 1 | 40000 | 1 | 40000 | 2 | 80000 | 2 | 80000
|  |  |  | AE |  | 40000 | [6 empty] | 1 | 40000
232 | 88.8 b | 194 | SOTC233 | 2 cylinder emergency manifold CO2 | Job | 14500 | 1 | 14500 | 1 | 14500 | 2 | 29000 | 2 | 29000
233 | 88.8 c | 195 | SOTC234 | Fully Automatic CO2 Control System | Job | 185000 | 1 | 185000 | 1 | 185000 | 2 | 370000 | 2 | 370000
234 | 88.9 | 237 | SOTC235 | Aneste Iwata Make TFS 150 C9 Model, Compresso Two stage, Motor 15 HP & 57.18 CFM, 60 CFM Air Dryer with 2000 Ltrs Receiver Twin System (For Air4, Air7) | Job | 1895000 | 1 | 1895000 |  | 0 | 1 | 1895000 | 1 | 1895000
235 | 88.1 | 196 | SOTC236 | Supporting structure for MGPS lines with Ismb Columns, beams, MS angles, Flats and square rods | Job | 795000 | 1 | 795000 |  | 0 | 1 | 795000 | 1 | 795000
236 | 88.11 | 197 | SOTC237 | 2x20 Oxygen Main manifold System | Job | 95000 | 1 | 95000 |  | 0 | 1 | 95000 | 1 | 95000
237 | 88.12 | 198 | SOTC238 | Electrical Control Panel for MGPS | Job | 145000 | 1 | 145000 |  | 0 | 1 | 145000 | 1 | 145000
238 | 88.13 | 238 | SOTC239 | Vaccum system Ingersoll Rand Make Model 15V x 10 Model with 5 HP Motor with 1000 Liters Reciever, Filters, Electricals, Etc Secretion Trap and Bacteria Filter | Job | 1495000 | 2 | 2990000 |  | 0 | 2 | 2990000 | 2 | 2990000
239 |  | 235 | SOTC240 | Validation By Third Party Agency Charges per Each MOT | Each | 100000 | 4 | 400000 |  | 0 | 4 | 400000 | 4 | 400000
|  |  |  | AE |  | 100000 | [6 empty] | 5 | 500000
240 |  | 236 | SOTC241 | Anesthetic Gas Scavenging System (AGSS) | Job | 1213000 | 1 | 1213000 |  | 0 | 1 | 1213000 | 1 | 1213000
[12 empty] | TOTAL |  | 16967800

## CIVIL2 (hidden)
C
S.No | Tech. Spec Cl. No in TED | Item S.No | Item Code | Item Name |  |  | As Per Agreement (with 4 Ots) |  | Additional Sanction fot 2 Ots |  | Total (6 Ots) |  | As Per Work Done/To Be Done
[5 empty] | UOM | Unit Rate (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.)
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
1 |  | 4: Supply and installation of Under-deck Thermocol insulation sheets of 40 mm thick having more than 30 Kg/m3 density to ceiling by brush application of bituminous adhesive to the sheets and secured with screw along with washer at the centre of the sheet supported with GI wire running diagonally to the sheet of 2mm dia. (in ICUs & MOTs Integration Room); 5: Sqm; 6: 1014; 13: 262.74; 14: 266418.36
2 |  | 4: Supply and placing of the Design Mix Plain Cement Concrete of M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Concrete Batching Plant with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials. (in 6 OTs); 5: Cum; 6: 11740; 13: 28.01; 14: 328837.4
3 |  | 4: Supply and Laying of Floor leveller compund (self smoothing mortar) to level the surface, having bulk density not less than 2 Kg/l for a fresh mortor, compressive strength not less than 20 N/mm2, initial setting time not more than 40 minutes and offer a 25 minutes working time, The surface should be walkabe after 30 min of laying. (all rooms & corridors except OTs, TIRs and Sterile corridor); 5: Sqm; 6: 1460; 13: 882.44; 14: 1288362.4
4 |  | 4: Providing dadooing to walls with glazed full body ceramic wall tiles of size 800 x 1600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. (at Entrance); 5: Sqm; 6: 4665; 13: 119.385; 14: 556931.025
5 |  | 4: Providing (1500 X 2100) single sliding door operated by elbow switches / foot switch as well as touchless sensor of 10mm thick toughened glass (Saint Gobin / Modi Guard) fixed in SS 304 grade 2 Track top channel of 45 mm (one track to hold fixed glass partition in position and second track with top rollers suitably angled to reduce resistance to movement to facilitate smooth sliding movement of the door). Single track bottom channel to be provided for fixed glass partition. Floor guide to be provided for smooth sliding of the door. Concealed door handle of (150 mm) to be provided in cutout on the sliding door for manual operation when required. All fittings provided should be of Titon /Ozone / Enox make in SS 304 - In TIRs; 5: Nos; 6: 270276; 13: 2; 14: 540552
6 |  | 4: V-Board Partitions on top of false ceiling for partitioning of sterile corridor and non-sterile corridor (for dividing corridors into zones above ceiling); 5: Sqm; 6: 3640; 13: 16; 14: 58240
7 |  | 4: GI Powder Coated Sliding Doors (0.8mm shutter sheet thk & 1.2mm frame sheet thk with Single Rebate and Honeycomb Infill) Double Leaf Door 1200 x 2100mm with Accessories (Sliding Track for Double Door, Sliding Dead Lock Enox, Concealed Handles 100mm Ahlada, Flush Bolt 300mm Ahlada, SS304 Kick Plate upto 350mm ht, DG Clear Float Glass 350x750x6mm with Adhesive Tape & Silicon Sealant) (for change rooms to corridor entrance); 5: Nos; 6: 84133; 13: 1; 14: 84133
8 |  | 4: Supply and installation of 50mm thick double skin modular wall Panels made of 0.8 mm thick powder coated GI on both the sides, with 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, flush on both sides with maximum allowable gap of 3- 4mm filled with food grade silicon sealant and placed on cold rolled galvanised bottom tracks with a recess to provide floor to wall coving flush with the wall panel. This includes all required harware for completion Panels to be covered with a protective film to avoid any damages during transportation and installation; 5: Sqm; 6: 7450; 13: 297.52; 14: 2216524
9 |  | 4: Supply and installation of 50mm thick double skin ceiling system made of 0.8 mm thick Powder Coated GI sheets on both sides, 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, panels flush towards room side with maximum allowable gap of 3-4mm at panel to panel joints filled with silicon sealant. Ceiling panels are suspended from the RCC slab by using concealed AL ceiling grid with tie rod and adjustable turn buckle arrangement etc. This includes all required hardware for completion. Panels to be covered with a protective film to avoid any damages during transportation and installation; 5: Sqm; 6: 7450; 13: 163.08; 14: 1214946
10 |  | 4: Acoustic Wall Panelling with framework consisting of 25mm high GI wall channels with fully knurled surface of 0.55mm thick bottom wedge of 80mm width, having two equal flanges of 26mm is anchored to GI studs of 50mm high. GI studs of 50mm High to be fixed to wall at 600mm centres, 25mm thick channels are then fixed perpendicular to the GI studs and suitable fixing channel is fixed to the cross channel to fix the panel to achieve overall air gap of 75mm from the wall and GI Clips for inside panel and Clips for border panel of 18mm to be fixed to the GI wall channel to achieve required shape. Secured arranging of polyester wool of – thickness/density, Prelam Board to be installed. 15mm thick Prelam perforated Wooden slat of required dia perforation & pitch is to be customised and then fixed to GI frame rigidly by using fixing channel fastened perpendicular to the cross channel with GI brackets. The boards shall be fixed to the GI frame with special cleats. (MOTs Integration Room); 5: Sqm; 6: 6350; 13: 110; 14: 698500
11 |  | 4: Accooustic Ceiling Paneling with Perforated board Fine line Grid false ceiling using 11mm thick Perforated Board sheet tiles of size 595mm x 595mm fixing to steel precoated GI wall angle of size 25mm x 25mm x 0.70mm thick along the perimeter of ceiling screw fixed to brick work / partition at 610mm center to center and suspending the frame work using precoated GI Tee section (24mm x 38mm x 0.7mm) from soffit at 1220mm center to center fixed with GI Soffit Cleat, rawl plugs and steel expansion fasteners & connecting clip to the GI Tee section with 4mm dia GI rod with galvanised spring steel level clip of PVC unversal holding clips system at 1200mm center to center and Secured arranging of polyester wool of 50mm thick 1000 GSM, Prelam Board to be installed. 15mm thick Prelam perforated Wooden slat of required dia perforation & pitch is to be customised and then fixed to GI frame rigidly by using fixing channel fastened perpendicular to the cross channel with GI brackets. The boards shall be fixed to the GI frame with special cleats. (MOTs Integration Room); 5: Sqm; 6: 5700; 13: 62; 14: 353400
12 |  | 4: Wooden Flooring with Engineered wood planks of 14mm thick (MOTs Integration Room); 5: Sqm; 6: 7300; 13: 65; 14: 474500
13 |  | 4: Skirting for Wooden Flooring with Engineered wood planks of 14mm thick (MOTs Integration Room); 5: Rmt; 6: 900; 13: 40; 14: 36000
14 |  | 4: 80% blockout Ruler Blinds for MOTs Integration Room Windows; 5: Nos; 6: 12000; 13: 3; 14: 36000
15 |  | 4: Supply and installation of double pass RO system having 2 nos feed pumps of 1.5 HP with max flow of 4000 ltr/hr including construction of sand filter of dimensions (H=1650 mm, D=325 mm) with filter media as Quartz sand of SS vessel construction and Activated Carbon filter of dimensions (H= 1650mm) with filter media as Activated carbon (IV-600) of SS vessel construction, with 4 nos of spiral wound RO membrane of size 4 inch dia x 1 m length of make ION EXCHANGE (HYDROMEN) (or) equal, 2 nos UV system with service flow of 1000 ltr/hr (Before 2nd filter and after SS tank out-let) with PEX pipeline recirculation loop to avoid contamination in pipe to supply for 10 beds in Post ICU, 4 beds in Transplant ICU and 1 for each TIR.) Drinage outlet to be provided near each RO outlet.; 5: Job; 6: 6240000; 13: 1; 14: 6240000
16 |  | 4: Water Proofing of roof and peripheral walls of south west block, 8th floor, Gandhi Hospital which includes Dismantling of existing screed and lifting of debris to ground floor, Surface preparation and cracks treatment, Providing Angle fillet/taper of 75mm X 75mm with polymer modified mortor in the ratio of cement:sand:admixture (1:1.5:1.5) (Forsoc Nitobond SBR/M-Crete PC Bond @ 10% by weight of cement), Applying 1 coat of Forsoc Nitoproof WB Primer, Application of 2 coats of pitch free based liquid applied single component elastomeric waterproofing membrane (Forsoc Nito proof 600PF/BASF HLM5000), Laying 200 GSM Geotextile Fabric, Laying of 125mm Fiber Reinforced M20 grade protective concrete screed on terrace, Control joints treatment and External walls repair with window Frame-walls joints/Gaps treatment.; 5: Job; 6: 12611958; 13: 1; 14: 12611958
17 |  | 4: Supply of Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs with borders and design as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM (1:8) prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab , including neat cement slurry of honey like consistancy spread @ 3.3 kgs per Sqm. and jointed neately with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site (excluding cost of C.C. bed) including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in-charge etc.,and overheads & contractors profit complete for finished item of work. (APSS No.701 & 707).; 5: Sqm; 6: 2550; 13: 342; 14: 872100
18 |  | 4: Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707); 5: Rmt; 6: 250; 13: 120; 14: 30000
[12 empty] | TOTAL |  | 27907416.185

## ELE2 (hidden)
REVISED ESTIMATE OF SOTC 8TH FLOOR, SOUTH-WEST BLOCK, GANDHI HOSPITAL
S.No | Tech. Spec Cl. No in TED | Item S.No | Item Code | Item Name |  |  | As Per Agreement (with 4 Ots) |  | Additional Sanction fot 2 Ots |  | Total (6 Ots) |  | As Per Work Done/To Be Done
[5 empty] | UOM | Unit Rate (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.)
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
29 |  | 4: Supply, Transportation and installation of 20KVA / 312V DC on line UPS system (for emergency lighting in all rooms & Corridor except OTs & TIRs); 5: Nos; 6: 629358; 13: 2; 14: 1258716
30 |  | 4: 800 KVA Transformer OLTC for transformers with RTCC: Supply, Transportation, Installation, Testing and Commissioning of 800 KVA TRANSFORMER with all test reports. The Transformer shall be designed and manufactured as per IS:1180 OLTC with level-II with initial filling of oil as per IS 335-1993. 1000 A LT Breaker Kiosk - 01 No.The basic details of the Transformer are as under. Makes: Kirloskar / PETE / Esennar / Voltamp / Crompton / ABB / Schneider.; 5: Nos; 6: 4814994; 13: 1; 14: 4814994
31 |  | 4: 750 KVA Generator Set with AMF Control Panel Supply, Transportation, erection and commissioning (Excluding Foundation) of 3 Phase, 415, 50Hz, water cooled multi cylinder diesel generator set with alternator of 750 KVA output continuous rating directly coupled Engine and Alternator 750 KVA, 415 Volts with guard and mounted on a common base plate of Robust construction and complete with AMF panel having IP-52 protection, Acoustic Enclosure as per CPCB norms , sound absorbing material, t to restrict sound level up to 75 dB up to 1 Mtr distance and as per CPCB norms etc.; 5: Nos; 6: 9540000; 13: 1; 14: 9540000
[12 empty] | TOTAL |  | 15613710

## ELV2 (hidden)
REVISED ESTIMATE OF SOTC 8TH FLOOR, SOUTH-WEST BLOCK, GANDHI HOSPITAL
S.No | Tech. Spec Cl. No in TED | Item S.No | Item Code | Item Name |  |  | As Per Agreement (with 4 Ots) |  | Additional Sanction fot 2 Ots |  | Total (6 Ots) |  | As Per Work Done/To Be Done
[5 empty] | UOM | Unit Rate (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.)
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
27 |  | 4: Recording in counselling room; 5: Job; 6: 155378; 13: 1; 14: 155378
28 |  | 4: Local Area Network (LAN) System; 5: Job; 6: 460242; 13: 1; 14: 460242
[12 empty] | TOTAL |  | 615620

## EQP2 (hidden)
REVISED ESTIMATE OF SOTC 8TH FLOOR, SOUTH-WEST BLOCK, GANDHI HOSPITAL
S.No | Tech. Spec Cl. No in TED | Item S.No | Item Code | Item Name |  |  | As Per Agreement (with 4 Ots) |  | Additional Sanction fot 2 Ots |  | Total (6 Ots) |  | As Per Work Done/To Be Done
[5 empty] | UOM | Unit Rate (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.)
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
32 |  | 4: Monitor Stand beside Bed in ICUs & TIRs; 5: Nos; 6: 6176; 13: 31; 14: 191456
[12 empty] | TOTAL |  | 191456

## MGPS2 (hidden)
REVISED ESTIMATE OF SOTC 8TH FLOOR, SOUTH-WEST BLOCK, GANDHI HOSPITAL
S.No | Tech. Spec Cl. No in TED | Item S.No | Item Code | Item Name |  |  | As Per Agreement (with 4 Ots) |  | Additional Sanction fot 2 Ots |  | Total (6 Ots) |  | As Per Work Done/To Be Done
[5 empty] | UOM | Unit Rate (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.)
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
19 |  | 4: 4 Gas Digital Alarm Panels : 4 Gas Digital Alarm Panel consisting of atl necessary accessories ie Pressure sensors,reguIators,hand valves ,pressure gauges ecL(Oxygen, Nitrous oxide, Medical Air, Vacuum) (for TIRs); 5: Nos; 6: 42150; 13: 2; 14: 84300
20 |  | 4: 6 Gas Digital Alarm Panele : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. (for OTs); 5: Nos; 6: 60008; 13: 6; 14: 360048
21 |  | 4: Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. (for TIRs); 5: Nos; 6: 22201; 13: 2; 14: 44402
22 |  | 4: 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen.; 5: Job; 6: 48103; 13: 1; 14: 48103
23 |  | 4: Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED.; 5: Job; 6: 222013; 13: 1; 14: 222013
24 |  | 4: 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide.; 5: Job; 6: 48103; 13: 1; 14: 48103
25 |  | 4: 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide.; 5: Job; 6: 17401; 13: 1; 14: 17401
26 |  | 4: Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041 C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED; 5: Job; 6: 222013; 13: 1; 14: 222013
[12 empty] | TOTAL |  | 1046383

## Print (2) (hidden)
REVISED ESTIMATE OF SOTC 8TH FLOOR, SOUTH-WEST BLOCK, GANDHI HOSPITAL
S.No of RE | Tech. Spec Cl. No in TED | Item S.No | Item Code | Item Name |  |  | As Per Agreement (with 4 Ots) |  | Additional Sanction fot 2 Ots |  | Total (6 Ots) |  | As Per Work Done/To Be Done |  | CAMC Unit Rate (As per Price bid) | Total CAMC
[5 empty] | UOM | Unit Rate (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.)
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
CIVIL WORKS
1 | 1 | 1 | SOTC001 | Stainless Steel Pre-fabricated Wall panels. (MOTs & MOT Corridor) - Wall panels | Sqm | 15010 | 400 | 6004000 | 350 | 5253500 | 750 | 11257500 | 491.9486 | 7384148.486 | 5253.5 | 2584451.9701 |  | AE | AUTHORIZED EXTRAS | 30868378.288 | 62
2 | 1 | 199 | SOTC002 | Stainless Steel Pre-fabricated Ceiling panels In MOTs & MOTs Corridor | Sqm | 15010 | 385 | 5778850 | 78 | 1170780 | 463 | 6949630 | 263.165 | 3950106.65 | 5253.5 | 1382537.3275 |  | SI | SUPPLEMENTAL ITEMS | 45374571.185 | 32
4 | 2.1 | 3 | SOTC004 | Electro conductive Flooring inside MOTs | Sqm | 4035 | 160 | 645600 | 80 | 322800 | 240 | 968400 | 217.7802 | 878743.107 | 1412.25 | 307560.0874 |  |  |  | 76242949.473 | 94
5 | 2.2 | 4 | SOTC005 | Flooring with Vinyl Sheets In MOT Corridor | Sqm | 3750 | 175 | 656250 | 50 | 187500 | 225 | 843750 | 87.0329 | 326373.525 | 1312.5 | 114230.7338
17 | 8 | 15 | SOTC017 | Hermetically Sealed Doors (1.80mt x 2.10 mt) | Nos | 115000 | 4 | 460000 | 2 | 230000 | 6 | 690000 | 6 | 690000 | 40250 | 241500
|  | 4: AE; 6: 115000; 13: 3; 14: 345000; 15: 40250; 16: 120750 | AE
18 | 8 | 240 | SOTC018 | (1.50mt x 2.10 mt) Sliding Automatic Sliding Doors with View Windoy of 1 Mt x 1 Mt | Nos | 525000 | 2 | 1050000 |  | 0 | 2 | 1050000 | 2 | 1050000 | 183750 | 367500
19 | 10 | 16 | SOTC019 | Storage Units | Nos | 75000 | 4 | 300000 | 2 | 150000 | 6 | 450000 | 6 | 450000 | 26250 | 157500
20 | 11 | 17 | SOTC020 | Writing Board (List Board) | Nos | 18750 | 4 | 75000 | 2 | 37500 | 6 | 112500 | 6 | 112500 | 6562.5 | 39375
39 | 1 | 34 | SOTC039 | Stainless Steel Pre-fabricated Wall panels in TIRs & TIR Corridor | Sqm | 15010 | 202 | 3032020 | 0 | 0 | 202 | 3032020 | 202 | 3032020 | 5253.5 | 1061207
|  | 4: AE; 6: 15010; 13: 136.9318; 14: 2055346.318; 15: 5253.5; 16: 719371.2113 | AE
40 | 1 | 35 | SOTC040 | Stainless Steel Pre-fabricated Ceiling panels in TIRs and TIR Corridor | Sqm | 15010 | 146 | 2191460 | 0 | 0 | 146 | 2191460 | 146 | 2191460 | 5253.5 | 767011
|  | 4: AE; 6: 15010; 13: 33.22; 14: 498632.2; 15: 5253.5; 16: 174521.27 | AE
41 | 2.1 | 202 | SOTC041 | Electro conductive Flooring inside TIRs | Sqm | 4035 | 146 | 589110 |  | 0 | 146 | 589110 | 73.6644 | 297235.854 | 1412.25 | 104032.5489
42 | 2.2 | 36 | SOTC042 | Flooring with Vinyl Sheets In TIR Corridor | Sqm | 3750 | 61 | 228750 |  | 0 | 61 | 228750 | 61 | 228750 | 1312.5 | 80062.5
|  | 4: AE; 6: 3750; 13: 70.4074; 14: 264027.75; 15: 1312.5; 16: 92409.7125 | AE
48 | 8 | 42 | SOTC049 | Hermetically Sealed Doors (1.80mt x 2.10 mt) | Nos | 525000 | 3 | 1575000 |  | 0 | 3 | 1575000 | 3 | 1575000 | 183750 | 551250
49 | 15 | 43 | SOTC050 | 12mm thick glazed Glass partition walls in TIRs | Sqm | 650 | 40 | 26000 |  | 0 | 40 | 26000 | 40 | 26000 | 227.5 | 9100
54 | 11 | 48 | SOTC055 | WRITING BOARDS FOR ICUS, PRE OPP | Nos | 18750 | 5 | 93750 |  | 0 | 5 | 93750 | 5 | 93750 | 6562.5 | 32812.5
|  | 4: AE; 6: 18750; 13: 1; 14: 18750; 15: 6562.5; 16: 6562.5 | AE
144 |  | 116 | SOTC145 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Reinforced cement concrete) | Cum | 5400 | 10 | 54000 |  | 0 | 10 | 54000 | 10 | 54000 | 1890 | 18900
145 |  | 117 | SOTC146 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Unreinforced cement concrete) | Cum | 4500 | 1.5 | 6750 |  | 0 | 1.5 | 6750 | 1.5 | 6750 | 1575 | 2362.5
|  | 4: AE; 6: 4500; 13: 50.4015; 14: 226806.75; 15: 1575; 16: 79382.3625 | AE
146 |  | 118 | SOTC147 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Brick Masonary) | Cum | 900 | 118 | 106200 |  | 0 | 118 | 106200 | 118 | 106200 | 315 | 37170
|  | 4: AE; 6: 900; 13: 34.691; 14: 31221.9; 15: 315; 16: 10927.665 | AE
147 |  | 119 | SOTC148 | Dismantling, clearing away and carefully stacking useful materials for re-use and disposal of unserviceable materials with 100m lead as directed by Engineer-in-Charge duly taking actual premeasurements before dismantling including all charges complete (Kadapa slabs or shahabad stone slabs on sand bed) | Sqm | 630 | 25 | 15750 |  | 0 | 25 | 15750 | 25 | 15750 | 220.5 | 5512.5
|  | 4: AE; 6: 630; 13: 667.9265; 14: 420793.695; 15: 220.5; 16: 147277.7933 | AE
148 |  | 120 | SOTC149 | Dismantling doors, windows and clear storey windows, Ventilators etc., (wood or steel) shutters including Chowkhats, architraves,hold fasts and other attachments etc., and stacking them within 100m lead including charge etc., complete for finished item of work. (Not exceeding 3 sqm in area) | Nos | 1800 | 57 | 102600 |  | 0 | 57 | 102600 | 57 | 102600 | 630 | 35910
|  | 4: AE; 6: 1800; 13: 146; 14: 262800; 15: 630; 16: 91980 | AE
149 |  | 121 | SOTC150 | Conveyance of un-useful excavated earth to a distance of 16 KM for disposal including hire charges of T and P, labour charges etc., complete for finished item of work. | Cum | 900 | 250 | 225000 |  | 0 | 250 | 225000 | 250 | 225000 | 315 | 78750
|  | 4: AE; 6: 900; 13: 64.769; 14: 58292.1; 15: 315; 16: 20402.235 | AE
150 | 40 | 122 | SOTC151 | RCC M 25 grade design mix (For lintels) | Cum | 18900 | 3 | 56700 |  | 0 | 3 | 56700 | 3 | 56700 | 6615 | 19845
|  | 4: AE; 6: 18900; 13: 0.17; 14: 3213; 15: 6615; 16: 1124.55 | AE
151 | 41 | 123 | SOTC152 | RCC M 20 grade design mix (50mm thick platforms) | Sqm | 1170 | 12 | 14040 |  | 0 | 12 | 14040 | 0 | 0 | 409.5 | 0
152 | 41 | 124 | SOTC153 | RCC M 20 grade design mix (25 mm thick Shelves) | Sqm | 900 | 12 | 10800 |  | 0 | 12 | 10800 | 0 | 0 | 315 | 0
153 | 42 | 125 | SOTC154 | Brick Masonry work in CM (1:6) prop in superstructure | Cum | 15300 | 3 | 45900 |  | 0 | 3 | 45900 | 3 | 45900 | 5355 | 16065
|  |  |  | AE |  | 15300 | [6 empty] | 108.951 | 1666950.3 | 5355 | 583432.605
154 | 43 | 126 | SOTC155 | Reinforced Masonry for partition walls (100 mm thick) in CM (1:4) | Sqm | 2700 | 500 | 1350000 |  | 0 | 500 | 1350000 | 404.9325 | 1093317.75 | 945 | 382661.2125
155 | 44 | 127 | SOTC156 | PCC (1:3:6) nominal mix using 20mm size graded m/c (For bed blocks and hold fasts) (OTs screed) | Cum | 9000 | 1.5 | 13500 |  | 0 | 1.5 | 13500 | 0 | 0 | 3150 | 0
156 | 45 | 128 | SOTC157 | Filling with light weight concrete in Cement Concrete (1:5:10) proportion using brick jelly for low roofs | Cum | 7200 | 23 | 165600 |  | 0 | 23 | 165600 | 16.8651 | 121428.72 | 2520 | 42500.052
157 | 46 | 129 | SOTC158 | Thermo Mechanically Treated (Fe -500/500D/550D) for RCC works | MT | 126000 | 1.25 | 157500 |  | 0 | 1.25 | 157500 | 0.7686 | 96843.6 | 44100 | 33895.26
158 | 49 | 130 | SOTC159 | Plastering 12mm thick in two coats with base coat of 8mm thick in CM (1:6) and top coat of 4mm thick in CM (1:4). for Internal walls. | Sqm | 1224 | 1600 | 1958400 |  | 0 | 1600 | 1958400 | 1600 | 1958400 | 428.4 | 685440
|  |  |  | AE |  | 1224 | [6 empty] | 548.804 | 671736.096 | 428.4 | 235107.6336
159 | 51 | 131 | SOTC160 | Impervious coat to exposed RCC roof slab surfaces (APSS No. 901 and 903) For Toilets | Sqm | 360 | 77.78 | 28000.8 |  | 0 | 77.78 | 28000.8 | 43.05 | 15498 | 126 | 5424.3
160 | 92 | 222 | SOTC161 | Providing and applying Wall putty of White Cement or Polymer or Cement based of average 1 to 2 mm thickness over plastered surface to prepare the surface even and smooth after thoroughly brushing the surface to remove all dirt and remains of loose powdered materials, applying emery paper, Sand the surface, clean & wipe off loose dust, applying knifing paste filler by putty knife / muslin pad, air dry for 2 - 3 | Sqm | 270 | 4447 | 1200690 |  | 0 | 4447 | 1200690 | 1811.5335 | 489114.045 | 94.5 | 171189.9158
161 | 53 | 132 | SOTC162 | Flooring with non-skid full body ceramic floor tiles | Sqm | 1710 | 85 | 145350 |  | 0 | 85 | 145350 | 85 | 145350 | 598.5 | 50872.5
|  | 4: AE; 6: 1710; 13: 13.0805; 14: 22367.655; 15: 598.5; 16: 7828.6793 | AE
162 | 55 | 133 | SOTC163 | Dadooing to walls with glazed full body Porcelain wall tiles | Sqm | 1440 | 225 | 324000 |  | 0 | 225 | 324000 | 225 | 324000 | 504 | 113400
|  | 4: AE; 6: 1440; 13: 115; 14: 165600; 15: 504; 16: 57960 | AE
163 | 56 | 134 | SOTC164 | Dadooing to walls with glazed full body Ceramic tiles | Sqm | 1440 | 350 | 504000 |  | 0 | 350 | 504000 | 270.2175 | 389113.2 | 504 | 136189.62
164 | 57 | 135 | SOTC165 | Painting one coat water based cement primer of interior grade I and two coats of acrylic emulsion paint for ceiling and Walls | Sqm | 360 | 4447 | 1600920 |  | 0 | 4447 | 1600920 | 1372.014 | 493925.04 | 126 | 172873.764
165 | 59 | 136 | SOTC166 | Painting to new wood work | Sqm | 360 | 313 | 112680 |  | 0 | 313 | 112680 | 75 | 27000 | 126 | 9450
166 | 60 | 137 | SOTC167 | Painting to new iron work | Sqm | 270 | 88 | 23760 |  | 0 | 88 | 23760 | 88 | 23760 | 94.5 | 8316
|  | 4: AE; 6: 270; 13: 38.42; 14: 10373.4; 15: 94.5; 16: 3630.69 | AE
167 | 61 | 138 | SOTC168 | Two shutter cupboards | Sqm | 9000 | 100 | 900000 |  | 0 | 100 | 900000 | 0 | 0 | 3150 | 0
168 | 64 | 139 | SOTC169 | UPVC Fixed Louvered Ventilator | Sqm | 12000 | 7 | 84000 |  | 0 | 7 | 84000 | 7 | 84000 | 4200 | 29400
|  | 4: AE; 6: 12000; 13: 9.5165; 14: 114198; 15: 4200; 16: 39969.3 | AE
169 |  | 140 | SOTC170 | UPVC 3 track Sliding Windows | Sqm | 9000 | 15 | 135000 |  | 0 | 15 | 135000 | 15 | 135000 | 3150 | 47250
|  | 4: AE; 6: 9000; 13: 30.276; 14: 272484; 15: 3150; 16: 95369.4 | AE
170 |  | 141 | SOTC171 | MS Grills to Windows | Sqm | 1800 | 150 | 270000 |  | 0 | 150 | 270000 | 126.42 | 227556 | 630 | 79644.6
171 | 66 | 142 | SOTC172 | Flooring with 16 to 18 mm thick high polished granite stone slabs black colour for platforms (S.S.701 and special) | Sqm | 6300 | 50 | 315000 |  | 0 | 50 | 315000 | 50 | 315000 | 2205 | 110250
172 | 67 | 143 | SOTC173 | Doors as per approved drawings with medium teak wood frame (1500mm x 2600mm) | Sqm | 6300 | 50 | 315000 |  | 0 | 50 | 315000 | 15.4 | 97020 | 2205 | 33957
173 | 68 | 144 | SOTC174 | Doors as per approved drawings with medium teak wood frame (1000mm x 2100mm) | Sqm | 7400 | 45 | 333000 |  | 0 | 45 | 333000 | 17.2 | 127280 | 2590 | 44548
174 | 69 | 145 | SOTC175 | Doors Shutters WPC(800mm x 2100mm) | Sqm | 5400 | 40 | 216000 |  | 0 | 40 | 216000 | 33.3795 | 180249.3 | 1890 | 63087.255
175 | 70 | 146 | SOTC176 | Scientific Doors with metal door frames and door shutters made of galvanize steel | Sqm | 18000 | 45 | 810000 |  | 0 | 45 | 810000 | 45 | 810000 | 6300 | 283500
|  | 4: AE; 6: 18000; 13: 24.3; 14: 437400; 15: 6300; 16: 153090 | AE
176 | 71 | 147 | SOTC177 | False ceiling as per Technical specification | Sqm | 1800 | 1400 | 2520000 |  | 0 | 1400 | 2520000 | 750 | 1350000 | 630 | 472500
177 | 72 | 148 | SOTC178 | Vinyl flooring | Sqm | 3000 | 500 | 1500000 |  | 0 | 500 | 1500000 | 500 | 1500000 | 1050 | 525000
|  | 4: AE; 6: 3000; 13: 164; 14: 492000; 15: 1050; 16: 172200 | AE
178 | 74 | 149 | SOTC179 | Impervious coat to exposed RCC roof slab surfacesof 20mm thick (APSS No. 901 and 903) | Sqm | 1260 | 350 | 441000 |  | 0 | 350 | 441000 | 0 | 0 | 441 | 0
179 | 63 | 233 | SOTC180 | Fixed Glass Window – 1200 x 1200 | Sqm | 5400 | 53.55 | 289170 |  | 0 | 53.55 | 289170 | 53.55 | 289170 | 1890 | 101209.5
|  | 4: AE; 6: 5400; 13: 7.46; 14: 40284; 15: 1890; 16: 14099.4 | AE
180 | 95 | 223 | SOTC181 | Grouting the holes with neat cement slurry of 20mm dia with all required accessories of all materials etc., including cost & Conveyance of all labour Charges etc., complete finished item of work (*As per SSR2021-22 of S.NO:-8) | Nos | 180 | 500 | 90000 |  | 0 | 500 | 90000 | 0 | 0 | 63 | 0
181 | 96 | 224 | SOTC182 | Pressure grouting the drilled holes with neat cement slurry or with approved grout admixture using pump - excluding cost of drilling holes after fixing nozzles as technical specification approved by the department etc., including cost & Conveyance of all labour charges etc., complete finished item of work | Nos | 630 | 500 | 315000 |  | 0 | 500 | 315000 | 500 | 315000 | 220.5 | 110250
|  | 4: AE; 6: 630; 13: 632; 14: 398160; 15: 220.5; 16: 139356 | AE
182 | 87 A | 234 | SOTC183 | Supply and fabricating,erecting and fixing inposition trusses of approved design with structural steel other than MS. | Kgs | 180 | 6500 | 1170000 |  | 0 | 6500 | 1170000 | 6500 | 1170000 | 63 | 409500
183 | 87 B | 150 | SOTC184 | Supply and fixing of pre painted Galvalume Trapezoidal Profile Roofing with 0.50mm Thickness. | Sqm | 1080 | 65 | 70200 |  | 0 | 65 | 70200 | 65 | 70200 | 378 | 24570
14 | 91 | 13 | SOTC014 | Ceiling/Wall mounted CCTV Room Camera | Nos | 22500 | 4 | 90000 | 2 | 45000 | 6 | 135000 | 6 | 135000 | 7875 | 47250
15 | 6 | 14 | SOTC015 | LED Peripheral Lights cum clean room (OT) luminaries | Nos | 18750 | 62 | 1162500 | 40 | 750000 | 102 | 1912500 | 102 | 1912500 | 6562.5 | 669375
|  | 4: AE; 6: 18750; 13: 5; 14: 93750; 15: 6562.5; 16: 32812.5 | AE
27 | 16.3 & 16.4 | 24 | SOTC027 | Cable connections for integration within MOTs and with Workshop Projector Hall, Networks with OFC Cable | Job | 997500 | 4 | 3990000 | 2 | 1995000 | 6 | 5985000 | 6 | 5985000 | 349125 | 2094750
38 | 19 | 201 | SOTC038 | Electrical Installations in MOTs & TIRs | Job | 195000 | 7 | 1365000 | 2 | 390000 | 9 | 1755000 | 9 | 1755000 | 68250 | 614250
51 | 91 | 45 | SOTC052 | Ceiling/Wall mounted CCTV Room Camera | Nos | 12000 | 3 | 36000 |  | 0 | 3 | 36000 | 3 | 36000 | 4200 | 12600
55 | 91 | 49 | SOTC056 | CCTV CEILING CAMERA | Nos | 9500 | 10 | 95000 |  | 0 | 10 | 95000 | 10 | 95000 | 3325 | 33250
56 | 22 a | 50 | SOTC057 | Supply and Fixing of 25mm dia Conduit Pipes surface on wall. | Rmt | 110 | 10000 | 1100000 |  | 0 | 10000 | 1100000 | 10000 | 1100000 | 38.5 | 385000
57 | 22 b | 51 | SOTC058 | Supply and Fixing of 25mm dia Conduit Pipes Concealed on wall. | Rmt | 115 | 4000 | 460000 |  | 0 | 4000 | 460000 | 4000 | 460000 | 40.25 | 161000
58 | 23 a | 52 | SOTC059 | Wiring with run of 2 of 1.5 Sqmm Copper cable for points wiring. | Pts | 1525 | 570 | 869250 |  | 0 | 570 | 869250 | 570 | 869250 | 533.75 | 304237.5
59 | 23 b | 53 | SOTC060 | Wiring with run of 2 of 1.5 Sqmm Copper cable for stairecase points wiring. | Pts | 1100 | 10 | 11000 |  | 0 | 10 | 11000 | 10 | 11000 | 385 | 3850
60 | 23 c | 54 | SOTC061 | Supply and fixing of 6A/10A ISI Mark 3/2 pin Modular socket Common switch board | Pts | 900 | 25 | 22500 |  | 0 | 25 | 22500 | 25 | 22500 | 315 | 7875
61 | 23 d | 55 | SOTC062 | Wiring with 3 of 1.5 sq.mm with 6A switch and 6A, 3/2 pin socket Modular type with 6A switch control fixing on separate board. | Pts | 2800 | 50 | 140000 |  | 0 | 50 | 140000 | 50 | 140000 | 190.75 | 9537.5
62 | 23 e | 56 | SOTC063 | Supply and fixing of 6A switchs - 2 Nos and 6A 3/2 pin socket - 3 Nos Modular type with cover plate | Pts | 1400 | 200 | 280000 |  | 0 | 200 | 280000 | 200 | 280000 | 490 | 98000
63 | 23 f | 203 | SOTC064 | Supply & fixing of 16A/6A, 2 in one socket with 16A switch control modular type | Nos | 900 | 200 | 180000 |  | 0 | 200 | 180000 | 200 | 180000 | 315 | 63000
64 | 23 g | 204 | SOTC065 | Supply & fixing of 32A, socket with switch control modular | Nos | 1600 | 18 | 28800 |  | 0 | 18 | 28800 | 18 | 28800 | 560 | 10080
65 | 23 h | 205 | SOTC066 | Supply & fixing of 64A, socket with 64A switch control modular type | Nos | 18000 | 4 | 72000 |  | 0 | 4 | 72000 | 4 | 72000 | 6300 | 25200
66 | 24 a | 57 | SOTC067 | Supply and Run of 1 of 1.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 36 | 2000 | 72000 |  | 0 | 2000 | 72000 | 2000 | 72000 | 12.6 | 25200
67 | 24 b | 58 | SOTC068 | Supply and Run of 3 of 1.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable . | Rmt | 100 | 2000 | 200000 |  | 0 | 2000 | 200000 | 2000 | 200000 | 35 | 70000
68 | 24 c | 59 | SOTC069 | Supply and Run of 3 of 2.5 sq.mm (phase, neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 145 | 8000 | 1160000 |  | 0 | 8000 | 1160000 | 8000 | 1160000 | 50.75 | 406000
69 | 24 d | 60 | SOTC070 | Supply and Run of 3 runs of 4.0 sq mm (phase neutral and earth) FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 230 | 5000 | 1150000 |  | 0 | 5000 | 1150000 | 5000 | 1150000 | 80.5 | 402500
70 | 24 e | 61 | SOTC071 | Supply and Run of 3 of 6.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 325 | 300 | 97500 |  | 0 | 300 | 97500 | 300 | 97500 | 113.75 | 34125
71 | 24 f | 62 | SOTC072 | Supply and Run of 5 of 6.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 545 | 300 | 163500 |  | 0 | 300 | 163500 | 300 | 163500 | 190.75 | 57225
72 | 24 g | 63 | SOTC073 | Supply and Run of 5 of 10.0 Sq.mm FRLSH / HFFR PVC insulated 1100V grade as per IS:694/1990, IS 17048 specifications for Copper cable. | Rmt | 850 | 500 | 425000 |  | 0 | 500 | 425000 | 500 | 425000 | 297.5 | 148750
73 | 25 a | 64 | SOTC074 | Supply and fixing of DP Metal Enclosure with IP 20 Protection DB Make with 1 No 20A, 10 KA DP MCB | Nos | 1800 | 8 | 14400 |  | 0 | 8 | 14400 | 8 | 14400 | 630 | 5040
74 | 25 b | 65 | SOTC075 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 (For Lighting DBs) | Nos | 13000 | 10 | 130000 |  | 0 | 10 | 130000 | 10 | 130000 | 4550 | 45500
75 | 25 c | 230 | SOTC076 | Supply and fixing of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 (For Power DB's) | Nos | 13000 | 14 | 182000 |  | 0 | 14 | 182000 | 14 | 182000 | 4550 | 63700
76 | 25 d | 66 | SOTC077 | Supply and fixing of 8 Way VTPN DB with IP 43 Protection as per IS:13032 | Nos | 50000 | 5 | 250000 |  | 0 | 5 | 250000 | 5 | 250000 | 17500 | 87500
77 | 25 e | 67 | SOTC078 | Supply and fixing of cable adopteres box with cover for DBs including, massanory work etc., complete., | Nos | 6000 | 10 | 60000 |  | 0 | 10 | 60000 | 10 | 60000 | 2100 | 21000
78 | 26 a | 206 | SOTC079 | Providing independent earthing for Important equipment with 40mm dia 'B' class 2.5m long G.I pipe (GI Earthing) | Nos | 22500 | 18 | 405000 |  | 0 | 18 | 405000 | 18 | 405000 | 7875 | 141750
79 | 26 b | 68 | SOTC080 | Providing independent earthing by exacavating a pit to a depth of 2.25Mtr in all soils as per size specified in the data for Sophisticated Electronic equipment (Copper Earthing) | Nos | 54000 | 18 | 972000 |  | 0 | 18 | 972000 | 18 | 972000 | 18900 | 340200
80 | 26 b 1 | 69 | SOTC081 | Providing independent earthing for Important equipment with 100mm dia Heavy gauge C.I Earthing | Nos | 25000 | 6 | 150000 |  | 0 | 6 | 150000 | 6 | 150000 | 8750 | 52500
81 | 26 c | 70 | SOTC082 | Supply and Run of 50mm x 6mm G.I Strip | Rmt | 450 | 400 | 180000 |  | 0 | 400 | 180000 | 400 | 180000 | 157.5 | 63000
82 | 26 d | 71 | SOTC083 | Supply and Run of 25mm x 3mm copper strip | Rmt | 300 | 400 | 120000 |  | 0 | 400 | 120000 | 400 | 120000 | 105 | 42000
83 | 27 a | 207 | SOTC084 | Supply, transportation and fixing of 22W +/ 10% , >/ 2300 lumens, 1200mm length LED light | Nos | 4800 | 20 | 96000 |  | 0 | 20 | 96000 | 20 | 96000 | 1680 | 33600
84 | 27 b | 208 | SOTC085 | Supply, transportation and fixing 32-36W (>=3600 Lumens), 2' x2' (600mm x 600mm) slim panel LED luminaire | Nos | 4000 | 60 | 240000 |  | 0 | 60 | 240000 | 60 | 240000 | 1400 | 84000
85 | 27 c | 209 | SOTC086 | Supply, transportation and fixing 12 W +/-10% (>= 1200 Lumens) Down lighter back lit LED Down Light Recessed / Surface | Nos | 1400 | 215 | 301000 |  | 0 | 215 | 301000 | 215 | 301000 | 490 | 105350
86 | 27 d | 210 | SOTC087 | Supply, transportation and fixing 18 W +/-10% (>= 1800 Lumens) Down lighter back lit LED Down Light | Nos | 1800 | 95 | 171000 |  | 0 | 95 | 171000 | 95 | 171000 | 630 | 59850
87 | 27 e | 72 | SOTC088 | Supply, transportation and fixing ISI mark batten holder / slanting holder | Nos | 160 | 8 | 1280 |  | 0 | 8 | 1280 | 8 | 1280 | 56 | 448
88 | 27 f | 231 | SOTC089 | Supply, Transportation of energy efficient fan, 1200 mm sweep, aluminium body, consuming 28 W, BEE 5 star rated, ceiling fan | Nos | 3700 | 40 | 148000 |  | 0 | 40 | 148000 | 40 | 148000 | 1295 | 51800
89 | 27 f 1 | 73 | SOTC090 | Supply and fixing of Modular type Stepped electronic regulator. | Nos | 1000 | 40 | 40000 |  | 0 | 40 | 40000 | 40 | 40000 | 350 | 14000
90 | 27 f 2 | 74 | SOTC091 | Labour charges for fixing of ceiling fan and regulator | Nos | 210 | 40 | 8400 |  | 0 | 40 | 8400 | 40 | 8400 | 73.5 | 2940
91 | 27 f 3 | 75 | SOTC092 | Supply and erecting 19/20mm steel tube down rod of one meter length | Nos | 600 | 40 | 24000 |  | 0 | 40 | 24000 | 40 | 24000 | 210 | 8400
92 | 27 g | 211 | SOTC093 | Supply of 12" (300mm) Light duty exhaust fan | Nos | 3000 | 5 | 15000 |  | 0 | 5 | 15000 | 5 | 15000 | 1050 | 5250
93 | 27 h | 212 | SOTC094 | Supply,Transportation of 12" (300mm) ISI, 900 RPM Heavy duty exhaust fan | Nos | 4900 | 10 | 49000 |  | 0 | 10 | 49000 | 10 | 49000 | 1715 | 17150
94 | 27 i | 76 | SOTC095 | Labour charges for fixing the exhaust fan in wall with necessary connections | Nos | 900 | 15 | 13500 |  | 0 | 15 | 13500 | 15 | 13500 |  | 0
95 | 27 j | 77 | SOTC096 | Supply and fixing of GI louver shutter including GI mesh | Nos | 3200 | 15 | 48000 |  | 0 | 15 | 48000 | 15 | 48000 |  | 0
96 | 28 a | 213 | SOTC097 | Main Power Panel with 1000A 4 Pole ACB as incomer - 1 No and out goings 800 A 4P MCCB - 1 No., 630 A 4P MCCB - 1 No., 400A 4P MCCB - 4 Nos & 250A 4P MCCB - 3 No's with required Digital Ammeter and Voltmer, LED Indicators | Nos | 1315000 | 1 | 1315000 |  | 0 | 1 | 1315000 | 1 | 1315000 |  | 0
97 | 28 b | 214 | SOTC098 | Floor Power Panel : Incomer: 630A 4 Pole MCCB,- 1 No Outgoings 250 A 4P MCCB - 4 No's 125 A 4P MCCB - 10 No's, 63 A 4P MCCB - 4 No's with required Digital Ammeter and Voltmer, LED Indicators | Nos | 875000 | 1 | 875000 |  | 0 | 1 | 875000 | 1 | 875000 |  | 0
98 | 28 c | 215 | SOTC099 | Electrical Lighting Panels : Incomer: 250 A 4 Pole MCCB - 1 No, Out Goings 125 A 4P MCCB - 4 No's 63 A 4P MCCB - 3 No's with required Digital Ammeter and Voltmer, LED Indicators | Nos | 370000 | 2 | 740000 |  | 0 | 2 | 740000 | 2 | 740000 |  | 0
99 | 29 d | 78 | SOTC100 | 130KVAR Out Door Capacitor panel : Incomer: 250A FP MCCB - 1 No, 63A 10KA TP MCB - 9 Nos. 20 KVAR Capacitor Duty contactors - 5 Nos., 10 KVAR Capacitor Duty contactors - 2 Nos, .5 KVAR Capacitor Duty contactors - 2 Nos. 12 stage APFC Relay - 1 No | Nos | 450000 | 1 | 450000 |  | 0 | 1 | 450000 | 1 | 450000 |  | 0
100 |  | 232 | SOTC101 | 630 KVA Transformer OLTC for transformers with RTCC: Supply, Transportation, Installation, Testing and Commissioning of 630 KVA TRANSFORMER with all test reports. The Transformer shall be designed and manufactured as per IS:1180 OLTC with level-II with initial filling of oil as per IS 335-1993. 1000 A LT Breaker Kiosk - 01 No.The basic details of the Transformer are as under. Makes: Kirloskar / PETE / Esennar / Voltamp / Crompton / ABB / Schneider. | Nos | 4000000 | 1 | 4000000 |  | 0 | 1 | 4000000 | 0 | 0 |  | 0
101 | 30 a | 79 | SOTC102 | Supply of 25 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 300 | 200 | 60000 |  | 0 | 200 | 60000 | 200 | 60000 |  | 0
102 | 30 b | 80 | SOTC103 | Supply of 50 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 560 | 200 | 112000 |  | 0 | 200 | 112000 | 200 | 112000 |  | 0
103 | 30 c | 81 | SOTC104 | Supply of 70 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 750 | 75 | 56250 |  | 0 | 75 | 56250 | 75 | 56250 |  | 0
104 | 30 d | 82 | SOTC105 | Supply of 120 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 1050 | 50 | 52500 |  | 0 | 50 | 52500 | 50 | 52500 |  | 0
105 | 30 e | 83 | SOTC106 | Supply of 185 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 1500 | 50 | 75000 |  | 0 | 50 | 75000 | 50 | 75000 |  | 0
106 | 30 f | 84 | SOTC107 | Supply of 240 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 1900 | 100 | 190000 |  | 0 | 100 | 190000 | 100 | 190000 |  | 0
107 | 30 g | 85 | SOTC108 | Supply of 300 Sqmm 3.5 Core XLPE insulated UG Cable. | Rmt | 2400 | 500 | 1200000 |  | 0 | 500 | 1200000 | 500 | 1200000 |  | 0
108 | 31 a | 86 | SOTC109 | Termination of UG cables of 3.5 core 25 Sq.mm | Nos | 850 | 8 | 6800 |  | 0 | 8 | 6800 | 8 | 6800 |  | 0
109 | 31 b | 87 | SOTC110 | Termination of UG cables of 3.5 core 50 Sq.mm | Nos | 1200 | 8 | 9600 |  | 0 | 8 | 9600 | 8 | 9600 |  | 0
110 | 31 c | 88 | SOTC111 | Termination of UG cables of 3.5 core 70 Sq.mm | Nos | 1500 | 8 | 12000 |  | 0 | 8 | 12000 | 8 | 12000 |  | 0
111 | 31 d | 89 | SOTC112 | Termination of UG cables of 3.5 core 120 Sq.mm | Nos | 1900 | 4 | 7600 |  | 0 | 4 | 7600 | 4 | 7600 |  | 0
112 | 31 e | 90 | SOTC113 | Termination of UG cables of 3.5 core 185 Sq.mm | Nos | 2500 | 4 | 10000 |  | 0 | 4 | 10000 | 4 | 10000 |  | 0
113 | 31 f | 91 | SOTC114 | Termination of UG cables of 3.5 core 240 Sq.mm | Nos | 3500 | 4 | 14000 |  | 0 | 4 | 14000 | 4 | 14000 |  | 0
114 | 31 g | 92 | SOTC115 | Termination of UG cables of 3.5 core 300 Sq.mm | Nos | 4000 | 12 | 48000 |  | 0 | 12 | 48000 | 12 | 48000 |  | 0
115 | 31 h | 93 | SOTC116 | Earth work excavation of Trench laying of U.G cables up to 70 sqmm | Rmt | 1100 | 100 | 110000 |  | 0 | 100 | 110000 | 100 | 110000 |  | 0
116 | 31 i | 94 | SOTC117 | Earth work excavation of Trench laying of U.G cables from 95 Sqmm | Rmt | 1150 | 100 | 115000 |  | 0 | 100 | 115000 | 100 | 115000 |  | 0
117 | 31 j | 95 | SOTC118 | Laying of PVC armoured under ground cable up to 95 Sqmm on wall | Rmt | 125 | 200 | 25000 |  | 0 | 200 | 25000 | 200 | 25000 |  | 0
118 | 31 k | 96 | SOTC119 | Laying of PVC armoured under ground cable from 120 Sq.mm to 400 Sqmm saddles on wall | Rmt | 270 | 700 | 189000 |  | 0 | 700 | 189000 | 700 | 189000 |  | 0
119 | 32 a | 97 | SOTC120 | Supply, Transportation and Installation of 150mm x 50mm x 2mm thick hot dip GI perforated cable tray | Rmt | 1295 | 200 | 259000 |  | 0 | 200 | 259000 | 200 | 259000 |  | 0
120 | 32 b | 98 | SOTC121 | Supply, Transportation and Installation of 300mm x 50mm x 2mm thick thick hot dip GI perforated cable tray | Rmt | 4500 | 100 | 450000 |  | 0 | 100 | 450000 | 100 | 450000 |  | 0
121 | 33 a | 99 | SOTC122 | Supply, Transportation and installation of 10KVA / 312V DC on line UPS system | Nos | 400000 | 7 | 2800000 | 2 | 800000 | 9 | 3600000 | 9 | 3600000 |  | 0
122 | 33 b | 100 | SOTC123 | Supply and fixing of 12V, 150 AH MF battery | Nos | 25000 | 182 | 4550000 | 52 | 1300000 | 234 | 5850000 | 234 | 5850000 |  | 0
|  | 4: AE; 6: 25000; 13: 118; 14: 2950000; 16: 0 | AE
123 | 33 c | 101 | SOTC124 | Supply and providing of UPS cum battery rack 20 batteries | Nos | 30000 | 7 | 210000 | 2 | 60000 | 9 | 270000 | 9 | 270000 |  | 0
|  | 4: AE; 6: 30000; 13: 2; 14: 60000; 16: 0 | AE
124 | 33 d | 102 | SOTC125 | Supply, Transportation, Installation, Testing and commissioning of storage / Pressure type 5 Star rated water heater with ABS plastic body of 15 Ltrs | Nos | 16000 | 7 | 112000 |  | 0 | 7 | 112000 | 7 | 112000 |  | 0
|  | 4: AE; 6: 16000; 13: 4; 14: 64000; 16: 0 | AE
125 | 34 | 103 | SOTC126 | 26 persons ICU bed cum passenger lift (1768 Kgs) G+8 Floors, 9 stops,9 Openings (Cost Includes amount for Construction of Shaft / Cladding from Ground to 8th Floor) | Nos | 10495000 | 1 | 10495000 |  | 0 | 1 | 10495000 | 1 | 10495000 |  | 0
0
241 |  |  |  | Electrical connections for 2 UPS | Job | 100000 |  |  | 1 | 100000 | 1 | 100000 | 0 |  |  | 0
[12 empty] | TOTAL |  | 49845130
141 | 37 | 221 | SOTC142 | Telephone & EPABX System | Job | 1000000 | 1 | 1000000 |  | 0 | 1 | 1000000 | 1 | 1000000 |  | 0
142 | 38 | 114 | SOTC143 | Local Area Network (LAN) System | Job | 1250000 | 1 | 1250000 |  | 0 | 1 | 1250000 | 1 | 1250000 |  | 0
143 | 39 | 115 | SOTC144 | Biometric Access Control System | Nos | 300000 | 2 | 600000 |  | 0 | 2 | 600000 | 2 | 600000 |  | 0
|  | 4: AE; 6: 300000; 13: 1; 14: 300000; 16: 0 | AE
[12 empty] | TOTAL |  | 3150000
133 | 36.2 | 108 | SOTC134 | Automatic Smoke Detection System | Job | 1425000 | 1 | 1425000 |  | 0 | 1 | 1425000 | 1 | 1425000 |  | 0
134 | 36.3 | 109 | SOTC135 | Automatic Fire Alarm System | Job | 1400000 | 1 | 1400000 |  | 0 | 1 | 1400000 | 1 | 1400000 |  | 0
135 | 36.4 | 219 | SOTC136 | Supply & Fixing of 4.5Kg, CO2 Type Fire Extinguisher. | Nos | 27000 | 6 | 162000 |  | 0 | 6 | 162000 | 6 | 162000 |  | 0
136 | 36.5 | 110 | SOTC137 | Supply and fixing of ABC stored pressure squeeze grip type fire extinguishers, 9 kg capacity. | Nos | 16000 | 6 | 96000 |  | 0 | 6 | 96000 | 6 | 96000 |  | 0
137 | 36.6 | 111 | SOTC138 | Supply and fixing of ABC Powder MAP 4 Kg Fire extinguisher | Nos | 11000 | 10 | 110000 |  | 0 | 10 | 110000 | 10 | 110000 |  | 0
138 | 36.7 | 112 | SOTC139 | Supply and fixing of 2 Kg Fire extinguisher Clean Agent | Nos | 22500 | 10 | 225000 |  | 0 | 10 | 225000 | 10 | 225000 |  | 0
139 | 36.8 | 113 | SOTC140 | Supply and fixing of Escape signage boards in Rigid Photo luminescent based glow | Nos | 2000 | 150 | 300000 |  | 0 | 150 | 300000 | 150 | 300000 |  | 0
140 | 36.9 | 220 | SOTC141 | Supply & Fixing of Powder Coated Fire Rated doors. | Sqm | 29000 | 6 | 174000 |  | 0 | 6 | 174000 | 6 | 174000 |  | 0
|  | 4: AE; 6: 29000; 13: 7.8; 14: 226200; 16: 0 | AE
[12 empty] | TOTAL |  | 4118200
| TECHNICAL ASSISTANT | 4: DY.EXECUTIVE ENGINEER; 7: EXECUTIVE ENGINEER; 12: CHIEF ENGINEER
| Spl. Projects, TSMSIDC | 4: Spl. Projects, TSMSIDC; 7: Spl. Projects, TSMSIDC; 12: Spl. Projects, TSMSIDC
EQUIPMENT
3 | 1.5 | 2 | SOTC003 | Dynamic Hatch Box | Nos | 295000 | 2 | 590000 | 1 | 295000 | 3 | 885000 | 0 | 0 |  | 0
9 | 4 | 8 | SOTC009 | Pressure Relief Dampers | Nos | 22500 | 4 | 90000 | 2 | 45000 | 6 | 135000 | 6 | 135000 |  | 0
10 | 5.1 | 9 | SOTC010 | Single arm Anesthesia Pendants (Imported) | Nos | 1195000 | 4 | 4780000 | 2 | 2390000 | 6 | 7170000 | 6 | 7170000 |  | 0
11 | 5.2 | 10 | SOTC011 | Triple Dome Ceiling OT LED Lights (Imported) | Nos | 4750000 | 2 | 9500000 |  | 0 | 2 | 9500000 | 2 | 9500000 |  | 0
|  | 4: AE; 6: 4750000; 13: 2; 14: 9500000; 16: 0 | AE
12 | 5.3 | 11 | SOTC012 | Double Dome Ceiling OT LED Lights (Imported) | Nos | 3550000 | 2 | 7100000 | 2 | 7100000 | 4 | 14200000 | 2 | 7100000 |  | 0
13 | 5.4 | 12 | SOTC013 | Detachable Hi Definition Cameras in Triple Dome Ceiling OT Lights | Nos | 995000 | 2 | 1990000 | 1 | 995000 | 3 | 2985000 | 3 | 2985000 |  | 0
[14 empty] | 0 |  | 0
16 | 7 | 239 | SOTC016 | View Window with Motorised Blinds of 1 Mt Length & 1 Mt Height | Nos | 115000 | 7 | 805000 | 2 | 230000 | 9 | 1035000 | 9 | 1035000 |  | 0
|  | 4: AE; 6: 115000; 13: 5; 14: 575000; 16: 0 | AE
21 | 12 | 18 | SOTC021 | X-Ray CT Scan LED viewing Screen | Nos | 37500 | 4 | 150000 | 2 | 75000 | 6 | 225000 | 6 | 225000 |  | 0
22 | 13 | 19 | SOTC022 | Touch Screen Surgeon Control Panels | Nos | 385000 | 4 | 1540000 | 2 | 770000 | 6 | 2310000 | 6 | 2310000 |  | 0
|  | 4: AE; 6: 385000; 13: 3; 14: 1155000; 16: 0 | AE
23 | 14 | 20 | SOTC023 | 3-Bay Scrub Stations/Sinks | Nos | 368750 | 2 | 737500 |  | 0 | 2 | 737500 | 2 | 737500 |  | 0
|  | 4: AE; 6: 368750; 13: 2; 14: 737500; 16: 0 | AE
24 | 16 | 21 | SOTC024 | Video and Image Management system | Nos | 8000000 | 1 | 8000000 |  | 0 | 1 | 8000000 | 1 | 8000000 |  | 0
25 | 16.1 | 22 | SOTC025 | Medical Grade Monitors 32 inch 4 K Resolution | Nos | 1295000 | 4 | 5180000 | 2 | 2590000 | 6 | 7770000 | 6 | 7770000 |  | 0
26 | 16.2 | 23 | SOTC026 | Wall mounted large screen display 55 inch (Commercial Grade) | Nos | 495000 | 2 | 990000 |  | 0 | 2 | 990000 | 2 | 990000 |  | 0
28 | 16.5 | 25 | SOTC028 | Wireless Microphone | Nos | 255000 | 1 | 255000 |  | 0 | 1 | 255000 | 1 | 255000 |  | 0
29 | 16.6 | 26 | SOTC029 | Digital mixer Amplifier | Nos | 245000 | 1 | 245000 |  | 0 | 1 | 245000 | 1 | 245000 |  | 0
30 | 16.7 | 27 | SOTC030 | Ceiling Mounted Speakers | Nos | 15000 | 4 | 60000 | 2 | 30000 | 6 | 90000 | 6 | 90000 |  | 0
31 | 16.8 | 28 | SOTC031 | Video Conferencing System | Nos | 1195000 | 1 | 1195000 |  | 0 | 1 | 1195000 | 1 | 1195000 |  | 0
32 | 17.1 | 29 | SOTC032 | Home Theatre Power Conditioner, 230 V | Nos | 145000 | 1 | 145000 |  | 0 | 1 | 145000 | 1 | 145000 |  | 0
33 | 17.2 | 30 | SOTC033 | Amplifier (8 Channel) | Nos | 245000 | 1 | 245000 |  | 0 | 1 | 245000 | 1 | 245000 |  | 0
34 | 17.3 | 31 | SOTC034 | HiFi Active Sub Woofer | Nos | 50000 | 1 | 50000 |  | 0 | 1 | 50000 | 1 | 50000 |  | 0
35 | 17.5 | 32 | SOTC035 | 4K Laser Projection TV | Nos | 1495000 | 1 | 1495000 |  | 0 | 1 | 1495000 | 1 | 1495000 |  | 0
36 | 17.6 & 17.7 | 200 | SOTC036 | Equalization & Loud Speaker Control System | Nos | 40000 | 1 | 40000 |  | 0 | 1 | 40000 | 1 | 40000 |  | 0
37 | 17.8 | 33 | SOTC037 | Sound Analog Mixer | Nos | 245000 | 1 | 245000 |  | 0 | 1 | 245000 | 1 | 245000 |  | 0
47 | 4 | 41 | SOTC047 | Pressure Relief Dampers | Nos | 22500 | 3 | 67500 |  | 0 | 3 | 67500 | 3 | 67500 |  | 0
50 | 15 | 44 | SOTC051 | Wall mounted LED TV43 inchesFull HD | Nos | 165000 | 3 | 495000 |  | 0 | 3 | 495000 | 3 | 495000 |  | 0
53 | 12 | 47 | SOTC054 | X-RAY VIEWERS FOR ALL ICUS AND PRE OPP AREAS AND DOCTORS ROOMS | Nos | 37500 | 5 | 187500 |  | 0 | 5 | 187500 | 5 | 187500 |  | 0
|  | 4: AE; 13: 1; 14: 37500; 16: 0 | AE
242 |  |  |  | Double Arm Surgical Pendant | Nos | 1195000 | 0 | 0 | 6 | 7170000 | 6 | 7170000 | 6 | 7170000 |  | 0
[12 empty] | TOTAL |  | 71887500
| TECHNICAL ASSISTANT | 4: DY.EXECUTIVE ENGINEER; 7: EXECUTIVE ENGINEER; 12: CHIEF ENGINEER
| Spl. Projects, TSMSIDC | 4: Spl. Projects, TSMSIDC; 7: Spl. Projects, TSMSIDC; 12: Spl. Projects, TSMSIDC
AIR CONDITIONING WORKS
6 | 3 | 5 | SOTC006 | Uni Directional Ceiling Laminar Airflow Systems | Nos | 465000 | 4 | 1860000 | 2 | 930000 | 6 | 2790000 | 6 | 2790000 |  | 0
7 | 3.1 | 6 | SOTC007 | Air Handling Units (AHUs) 11 TR | Nos | 1495000 | 4 | 5980000 | 2 | 2990000 | 6 | 8970000 | 6 | 8970000 |  | 0
8 | 3.2 | 7 | SOTC008 | Condensing Units | Nos | 345000 | 4 | 1380000 | 2 | 690000 | 6 | 2070000 | 6 | 2070000 |  | 0
|  | 4: AE; 6: 345000; 13: 4; 14: 1380000; 16: 0 | AE
43 | 3 | 37 | SOTC043 | Uni Directional Ceiling Laminar Airflow Systems | Nos | 395000 | 3 | 1185000 |  | 0 | 3 | 1185000 | 3 | 1185000 |  | 0
44 | 3.1 | 38 | SOTC044 | Air Handling Units (AHUs) 11 TR | Nos | 1495000 | 2 | 2990000 |  | 0 | 2 | 2990000 | 2 | 2990000 |  | 0
45 | 3.1 | 39 | SOTC045 | Air Handling Units (AHUs) 8.5 TR | Nos | 1195000 | 1 | 1195000 |  | 0 | 1 | 1195000 | 1 | 1195000 |  | 0
46 | 3.2 | 40 | SOTC046 | Condensing Units | Nos | 345000 | 3 | 1035000 |  | 0 | 3 | 1035000 | 3 | 1035000 |  | 0
|  | 4: AE; 6: 345000; 13: 3; 14: 1035000; 16: 0 | AE
126 | 35.1 | 104 | SOTC127 | 1.50 TR with , 18000 BTU/Hr High Wall mount Split Air Conditioners | Nos | 150000 | 6 | 900000 |  | 0 | 6 | 900000 | 6 | 900000 |  | 0
|  | 4: AE; 6: 150000; 13: 1; 14: 150000; 16: 0 | AE
127 | 35.2 | 105 | SOTC128 | 2.0 TR with , 24000 BTU/Hr High Wall mount Split Air Conditioners | Nos | 210000 | 2 | 420000 |  | 0 | 2 | 420000 | 2 | 420000 |  | 0
|  | 4: AE; 6: 210000; 13: 4; 14: 840000; 16: 0 | AE
128 | 35.3 | 106 | SOTC129 | Voltage stabilizer for 4 KVA maximum load | Nos | 7000 | 6 | 42000 |  | 0 | 6 | 42000 | 6 | 42000 |  | 0
|  | 4: AE; 6: 7000; 13: 1; 14: 7000; 16: 0 | AE
129 | 35.4 | 107 | SOTC130 | Voltage stabilizer for 5 KVA maximum load | Nos | 8500 | 2 | 17000 |  | 0 | 2 | 17000 | 2 | 17000 |  | 0
|  | 4: AE; 6: 8500; 13: 4; 14: 34000; 16: 0 | AE
130 | 35.5 | 216 | SOTC131 | Ductable Air Conditioners 11.0 TR with ISEER ≥ 4 | Nos | 1200000 | 1 | 1200000 |  | 0 | 1 | 1200000 | 1 | 1200000 |  | 0
131 | 35.6 | 217 | SOTC132 | Ductable Air Conditioners 8.5 TR with ISEER ≥ 4 | Nos | 1000000 | 2 | 2000000 |  | 0 | 2 | 2000000 | 2 | 2000000 |  | 0
|  | 4: AE; 6: 1000000; 13: 2; 14: 2000000; 16: 0 | AE
132 | 35.7 | 218 | SOTC133 | Ductable Air Conditioners 5.5 TR with ISEER ≥ 4 | Nos | 900000 | 1 | 900000 |  | 0 | 1 | 900000 | 1 | 900000 |  | 0
|  | 4: AE; 6: 900000; 13: 2; 14: 1800000; 16: 0 | AE
[12 empty] | TOTAL |  | 32960000
| TECHNICAL ASSISTANT | 4: DY.EXECUTIVE ENGINEER; 7: EXECUTIVE ENGINEER; 12: CHIEF ENGINEER
| Spl. Projects, TSMSIDC | 4: Spl. Projects, TSMSIDC; 7: Spl. Projects, TSMSIDC; 12: Spl. Projects, TSMSIDC
PLUMBING WORKS
184 | 75 | 225 | SOTC185 | 4" (101.6mm) multi floor trap with jali - UPVC/SWR | Nos | 270 | 25 | 6750 |  | 0 | 25 | 6750 | 25 | 6750 |  | 0
|  | 4: AE; 6: 270; 13: 19; 14: 5130; 16: 0 | AE
185 | 76 | 151 | SOTC186 | 580mm x 440mm long Orissa pan white glazed Water Closet | Nos | 5400 | 4 | 21600 |  | 0 | 4 | 21600 | 4 | 21600 |  | 0
0
186 | 77 | 152 | SOTC187 | European Water Closet of 1st quality | Nos | 6300 | 9 | 56700 |  | 0 | 9 | 56700 | 9 | 56700 |  | 0
0
187 | 78 | 153 | SOTC188 | Indian make Flat Back Wash Hand Basin 1st quality | Nos | 3600 | 16 | 57600 |  | 0 | 16 | 57600 | 15 | 54000 |  | 0
0
188 | 79 | 154 | SOTC189 | CP finish brass soap dish | Nos | 1100 | 21 | 23100 |  | 0 | 21 | 23100 | 21 | 23100 |  | 0
0
189 | 80 | 155 | SOTC190 | TV shape mirror with plastic frame of size 609.6mm x 457.2mm | Nos | 630 | 25 | 15750 |  | 0 | 25 | 15750 | 15 | 9450 |  | 0
0
190 | 81 | 156 | SOTC191 | 25.4mm dia , 609.6mm long aluminium anodized towel rods | Nos | 540 | 36 | 19440 |  | 0 | 36 | 19440 | 21 | 11340 |  | 0
0
191 | 82 | 156 | SOTC192 | 15 mm brass body CP finish bib tap of not less than 300 grams weight | Nos | 540 | 25 | 13500 |  | 0 | 25 | 13500 | 14 | 7560 |  | 0
0
192 | 87 C | 158 | SOTC193 | Self Closing Tap - Push Type | Nos | 720 | 25 | 18000 |  | 0 | 25 | 18000 | 15 | 10800 |  | 0
0
193 | 84 | 159 | SOTC194 | Chromium plated finish brass body quarter turn Bibcock cum Health Faucet | Nos | 3600 | 12 | 43200 |  | 0 | 12 | 43200 | 9 | 32400 |  | 0
|  | 4: AE; 6: 3600; 16: 0 | AE
194 | 85 | 160 | SOTC195 | Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings - 15.90mm OD pipe | Rmt | 270 | 55 | 14850 |  | 0 | 55 | 14850 | 55 | 14850 |  | 0
|  | 4: AE; 6: 270; 13: 53.234; 14: 14373.18; 16: 0 | AE
195 | 85 | 161 | SOTC196 | Ashirvad/Ajay/Astral Flowguard or equivalent CPVC Pipes and Fittings - 22.20mm OD pipe | Rmt | 360 | 115 | 41400 |  | 0 | 115 | 41400 | 115 | 41400 |  | 0
|  | 4: AE; 6: 360; 13: 14.7065; 14: 5294.34; 16: 0 | AE
196 | 85 | 162 | SOTC197 | Ashirvad/ Ajay/ Astral Flowguard or equivalent CPVC Pipes and Fittings -28.60mm OD pipe | Rmt | 450 | 143 | 64350 |  | 0 | 143 | 64350 | 115.5 | 51975 |  | 0
0
197 | 86 | 163 | SOTC198 | Bronze Gate/ Globe valve - 25mm Nominal bore | Nos | 1440 | 15 | 21600 |  | 0 | 15 | 21600 | 15 | 21600 |  | 0
|  | 4: AE; 6: 1440; 13: 5; 14: 7200; 16: 0 | AE
198 | 87 | 164 | SOTC199 | SWR PVC pipes (Prince/ Sudhakar/ Kisan/ Supreme or any ISI brand) 4 Kg/Sq.cm. - 75mmdia | Rmt | 450 | 145 | 65250 |  | 0 | 145 | 65250 | 84 | 37800 |  | 0
0
199 | 87 | 165 | SOTC200 | SWR PVC pipes (Prince/ Sudhakar/ Kisan/ Supreme or any ISI brand) 4 Kg/Sq.cm. -110mmdia | Rmt | 540 | 145 | 78300 |  | 0 | 145 | 78300 | 68.25 | 36855 |  | 0
0
200 | 90 | 226 | SOTC201 | Supplying and fixing15 mm nominal size 152.0 mm CP finish iron body shower rose 1st quality including cost and conveyance of all materials, labour charges , overheads & contractors profit for finished item of work in all floors. | Nos | 630 | 5 | 3150 |  | 0 | 5 | 3150 | 5 | 3150 |  | 0
|  | 4: AE; 6: 630; 13: 1; 14: 630; 16: 0 | AE
201 | 87 D | 166 | SOTC202 | Supply and Fixing of white glazed flat back bowl urinals | Nos | 2700 | 4 | 10800 |  | 0 | 4 | 10800 | 0 | 0 |  | 0
0
202 | 87 E | 227 | SOTC203 | Supply and fixing of 16mm to 20 mm thick ploished marbles slab partitions of size 4'0"*2'0" | Nos | 3600 | 10 | 36000 |  | 0 | 10 | 36000 | 0 | 0 |  | 0
[12 empty] | TOTAL |  | 473957.52
| TECHNICAL ASSISTANT | 4: DY.EXECUTIVE ENGINEER; 7: EXECUTIVE ENGINEER; 12: CHIEF ENGINEER
| Spl. Projects, TSMSIDC | 4: Spl. Projects, TSMSIDC; 7: Spl. Projects, TSMSIDC; 12: Spl. Projects, TSMSIDC
MGPS WORKS
52 | 88.6 | 46 | SOTC053 | BED HEAD PANEL FOR TIR WITH DOUBLE OUTLETS AND ELECTRICAL OUTLETS | Nos | 49500 | 3 | 148500 |  | 0 | 3 | 148500 | 3 | 148500 |  | 0
203 | 88.1 | 167 | SOTC204 | 28 mm dia. and 0.90 mm thick Copper Pipe Lines for Main lines | Rmt | 1750 | 700 | 1225000 |  | 0 | 700 | 1225000 | 700 | 1225000 |  | 0
|  | 4: AE; 6: 1750; 13: 133; 14: 232750; 16: 0 | AE
204 | 88.1 | 168 | SOTC205 | 42 mm dia. and 1.20 mm thick Copper Pipe Lines for Main lines | Rmt | 2250 | 200 | 450000 |  | 0 | 200 | 450000 | 200 | 450000 |  | 0
|  | 4: AE; 6: 2250; 13: 27; 14: 60750; 16: 0 | AE
205 | 88.1 | 169 | SOTC206 | 54 mm dia. and 1.20 mm thick Copper Pipe Lines for Main lines | Rmt | 2950 | 550 | 1622500 |  | 0 | 550 | 1622500 | 550 | 1622500 |  | 0
|  | 4: AE; 6: 2950; 13: 14; 14: 41300; 16: 0 | AE
206 | 88.1 | 170 | SOTC207 | 12 mm dia. and 0.70 mm thick Copper Pipe Lines for distribution lines | Rmt | 650 | 320 | 208000 |  | 0 | 320 | 208000 | 320 | 208000 |  | 0
|  | 4: AE; 6: 650; 13: 224; 14: 145600; 16: 0 | AE
207 | 88.1 | 171 | SOTC208 | 15 mm dia. and 0.90 mm thick Copper Pipe Lines for distribution lines | Rmt | 950 | 525 | 498750 |  | 0 | 525 | 498750 | 525 | 498750 |  | 0
|  | 4: AE; 6: 950; 13: 232; 14: 220400; 16: 0 | AE
208 | 88.1 | 172 | SOTC209 | 22 mm dia. and 0.90 mm thick Copper Pipe Lines for distribution lines | Rmt | 1450 | 530 | 768500 |  | 0 | 530 | 768500 | 530 | 768500 |  | 0
|  | 4: AE; 6: 1450; 13: 65; 14: 94250; 16: 0 | AE
209 | 88.2 | 228 | SOTC210 | 15 mm (1/2") Isolation Valves | Nos | 1500 | 40 | 60000 |  | 0 | 40 | 60000 | 31 | 46500 |  | 0
0
210 | 88.2 | 229 | SOTC211 | 22 mm (3/4") Isolation Valves | Nos | 2500 | 15 | 37500 |  | 0 | 15 | 37500 | 14 | 35000 |  | 0
0
211 | 88.2 | 173 | SOTC212 | 28 mm Isolation Valves | Nos | 3500 | 3 | 10500 | 2 | 7000 | 5 | 17500 | 5 | 17500 |  | 0
|  | 4: AE; 6: 3500; 13: 4; 14: 14000; 16: 0 | AE
212 | 88.2 | 174 | SOTC213 | 42 mm Isolation Valves | Nos | 4500 | 2 | 9000 | 3 | 13500 | 5 | 22500 | 4 | 18000 |  | 0
0
213 | 88.2 | 175 | SOTC214 | 54 mm Isolation Valves | Nos | 5500 | 2 | 11000 | 1 | 5500 | 3 | 16500 | 3 | 16500 |  | 0
|  | 4: AE; 6: 5500; 13: 7; 14: 38500; 16: 0 | AE
214 | 88.3 | 176 | SOTC215 | Gas Outlet Points with probes for Oxygen with S Brackets | Nos | 2850 | 189 | 538650 |  | 0 | 189 | 538650 | 189 | 538650 |  | 0
|  | 4: AE; 6: 2850; 13: 17; 14: 48450; 16: 0 | AE
215 | 88.4 | 177 | SOTC216 | 2 Gas Digital Area Alarm Panels | Nos | 25000 | 2 | 50000 |  | 0 | 2 | 50000 | 0 | 0 |  | 0
0
216 | 88.4 | 178 | SOTC217 | 3 Gas Digital Area Alarm Panels | Nos | 30000 | 4 | 120000 |  | 0 | 4 | 120000 | 4 | 120000 |  | 0
|  | 4: AE; 6: 30000; 13: 1; 14: 30000; 16: 0 | AE
217 | 88.4 | 179 | SOTC218 | 5 Gas Digital Area Alarm Panels | Nos | 40000 | 5 | 200000 | 1 | 40000 | 6 | 240000 | 0 | 0 |  | 0
0
218 | 88.4 | 180 | SOTC219 | Master Digital Alarm Panels | Nos | 50000 | 1 | 50000 |  | 0 | 1 | 50000 | 1 | 50000 |  | 0
0
219 | 88.5 | 181 | SOTC220 | BPC Flow meter with Humidifier bottle and L adapter | Nos | 2250 | 27 | 60750 |  | 0 | 27 | 60750 | 27 | 60750 |  | 0
|  | 4: AE; 6: 2250; 13: 16; 14: 36000; 16: 0 | AE
220 | 88.5 | 182 | SOTC221 | L Type Adapter for Oxygen Flow meters | Nos | 1250 | 27 | 33750 |  | 0 | 27 | 33750 | 27 | 33750 |  | 0
0
221 | 88.5 | 183 | SOTC222 | Kit for conversion of Oxygen | Nos | 1650 | 27 | 44550 |  | 0 | 27 | 44550 | 18 | 29700 |  | 0
0
222 | 88.5 | 184 | SOTC223 | Suction Jars of 600 ml capacity | Nos | 3450 | 27 | 93150 |  | 0 | 27 | 93150 | 27 | 93150 |  | 0
|  | 4: AE; 6: 3450; 13: 19; 14: 65550; 16: 0 | AE
223 | 88.5 | 185 | SOTC224 | Adapters for Vacuum | Nos | 750 | 27 | 20250 |  | 0 | 27 | 20250 | 27 | 20250 |  | 0
0
224 | 88.5 | 186 | SOTC225 | Adapters for Air | Nos | 750 | 27 | 20250 |  | 0 | 27 | 20250 | 27 | 20250 |  | 0
0
225 | 88.5 | 187 | SOTC226 | Adapters for Nitrous Oxide | Nos | 750 | 15 | 11250 |  | 0 | 15 | 11250 | 15 | 11250 |  | 0
0
226 | 88.5 | 188 | SOTC227 | Vacuum Tube | Nos | 550 | 27 | 14850 | 58 | 31900 | 85 | 46750 | 85 | 46750 |  | 0
|  | 4: AE; 6: 550; 13: 30; 14: 16500; 16: 0 | AE
227 | 88.6 | 189 | SOTC228 | Bed Head wall panel horizontal 1500 mm long single railing | Nos | 35000 | 27 | 945000 |  | 0 | 27 | 945000 | 27 | 945000 |  | 0
|  | 4: AE; 6: 35000; 13: 4; 14: 140000; 16: 0 | AE
228 | 88.7 b | 190 | SOTC229 | Valve box -2 services | Nos | 9500 | 1 | 9500 |  | 0 | 1 | 9500 | 0 | 0 |  | 0
0
229 | 88.7 b | 191 | SOTC230 | Valve box -3 services | Nos | 14500 | 3 | 43500 |  | 0 | 3 | 43500 | 3 | 43500 |  | 0
|  | 4: AE; 6: 14500; 13: 2; 14: 29000; 16: 0 | AE
230 | 88.7 b | 192 | SOTC231 | Valve box -6 services | Nos | 22500 | 1 | 22500 | 5 | 112500 | 6 | 135000 | 6 | 135000 |  | 0
0
231 | 88.8 a | 193 | SOTC232 | 4 + 4 size of CO2 manifold System | Job | 40000 | 1 | 40000 | 1 | 40000 | 2 | 80000 | 2 | 80000 |  | 0
|  | 4: AE; 6: 40000; 13: 1; 14: 40000; 16: 0 | AE
232 | 88.8 b | 194 | SOTC233 | 2 cylinder emergency manifold CO2 | Job | 14500 | 1 | 14500 | 1 | 14500 | 2 | 29000 | 2 | 29000 |  | 0
0
233 | 88.8 c | 195 | SOTC234 | Fully Automatic CO2 Control System | Job | 185000 | 1 | 185000 | 1 | 185000 | 2 | 370000 | 2 | 370000 |  | 0
0
234 | 88.9 | 237 | SOTC235 | Aneste Iwata Make TFS 150 C9 Model, Compresso Two stage, Motor 15 HP & 57.18 CFM, 60 CFM Air Dryer with 2000 Ltrs Receiver Twin System (For Air4, Air7) | Job | 1895000 | 1 | 1895000 |  | 0 | 1 | 1895000 | 1 | 1895000 |  | 0
0
235 | 88.1 | 196 | SOTC236 | Supporting structure for MGPS lines with Ismb Columns, beams, MS angles, Flats and square rods | Job | 795000 | 1 | 795000 |  | 0 | 1 | 795000 | 1 | 795000 |  | 0
0
236 | 88.11 | 197 | SOTC237 | 2x20 Oxygen Main manifold System | Job | 95000 | 1 | 95000 |  | 0 | 1 | 95000 | 1 | 95000 |  | 0
0
237 | 88.12 | 198 | SOTC238 | Electrical Control Panel for MGPS | Job | 145000 | 1 | 145000 |  | 0 | 1 | 145000 | 1 | 145000 |  | 0
0
238 | 88.13 | 238 | SOTC239 | Vaccum system Ingersoll Rand Make Model 15V x 10 Model with 5 HP Motor with 1000 Liters Reciever, Filters, Electricals, Etc Secretion Trap and Bacteria Filter | Job | 1495000 | 2 | 2990000 |  | 0 | 2 | 2990000 | 2 | 2990000 |  | 0
0
239 |  | 235 | SOTC240 | Validation By Third Party Agency Charges per Each MOT | Each | 100000 | 4 | 400000 |  | 0 | 4 | 400000 | 4 | 400000 |  | 0
|  | 4: AE; 6: 100000; 13: 5; 14: 500000; 16: 0 | AE
240 |  | 236 | SOTC241 | Anesthetic Gas Scavenging System (AGSS) | Job | 1213000 | 1 | 1213000 |  | 0 | 1 | 1213000 | 1 | 1213000 |  | 0
[12 empty] | TOTAL |  | 16967800
| TECHNICAL ASSISTANT | 4: DY.EXECUTIVE ENGINEER; 7: EXECUTIVE ENGINEER; 12: CHIEF ENGINEER
| Spl. Projects, TSMSIDC | 4: Spl. Projects, TSMSIDC; 7: Spl. Projects, TSMSIDC; 12: Spl. Projects, TSMSIDC
CIVIL SUPPLIMENTAL WORKS
1 |  | 4: Supply and installation of Under-deck Thermocol insulation sheets of 40 mm thick having more than 30 Kg/m3 density to ceiling by brush application of bituminous adhesive to the sheets and secured with screw along with washer at the centre of the sheet supported with GI wire running diagonally to the sheet of 2mm dia. (in ICUs & MOTs Integration Room); 5: Sqm; 6: 1014; 13: 262.74; 14: 266418.36; 16: 0 | SI
2 |  | 4: Supply and placing of the Design Mix Plain Cement Concrete of M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Concrete Batching Plant with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials. (in 6 OTs); 5: Cum; 6: 11740; 13: 28.01; 14: 328837.4; 16: 0 | SI
3 |  | 4: Supply and Laying of Floor leveller compund (self smoothing mortar) to level the surface, having bulk density not less than 2 Kg/l for a fresh mortor, compressive strength not less than 20 N/mm2, initial setting time not more than 40 minutes and offer a 25 minutes working time, The surface should be walkabe after 30 min of laying. (all rooms & corridors except OTs, TIRs and Sterile corridor); 5: Sqm; 6: 1460; 13: 882.44; 14: 1288362.4; 16: 0 | SI
4 |  | 4: Providing dadooing to walls with glazed full body ceramic wall tiles of size 800 x 1600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. (at Entrance); 5: Sqm; 6: 4665; 13: 119.385; 14: 556931.025; 16: 0 | SI
5 |  | 4: Providing (1500 X 2100) single sliding door operated by elbow switches / foot switch as well as touchless sensor of 10mm thick toughened glass (Saint Gobin / Modi Guard) fixed in SS 304 grade 2 Track top channel of 45 mm (one track to hold fixed glass partition in position and second track with top rollers suitably angled to reduce resistance to movement to facilitate smooth sliding movement of the door). Single track bottom channel to be provided for fixed glass partition. Floor guide to be provided for smooth sliding of the door. Concealed door handle of (150 mm) to be provided in cutout on the sliding door for manual operation when required. All fittings provided should be of Titon /Ozone / Enox make in SS 304 - In TIRs; 5: Nos; 6: 270276; 13: 2; 14: 540552; 16: 0 | SI
6 |  | 4: V-Board Partitions on top of false ceiling for partitioning of sterile corridor and non-sterile corridor (for dividing corridors into zones above ceiling); 5: Sqm; 6: 3640; 13: 16; 14: 58240; 16: 0 | SI
7 |  | 4: GI Powder Coated Sliding Doors (0.8mm shutter sheet thk & 1.2mm frame sheet thk with Single Rebate and Honeycomb Infill) Double Leaf Door 1200 x 2100mm with Accessories (Sliding Track for Double Door, Sliding Dead Lock Enox, Concealed Handles 100mm Ahlada, Flush Bolt 300mm Ahlada, SS304 Kick Plate upto 350mm ht, DG Clear Float Glass 350x750x6mm with Adhesive Tape & Silicon Sealant) (for change rooms to corridor entrance); 5: Nos; 6: 84133; 13: 1; 14: 84133; 16: 0 | SI
8 |  | 4: Supply and installation of 50mm thick double skin modular wall Panels made of 0.8 mm thick powder coated GI on both the sides, with 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, flush on both sides with maximum allowable gap of 3- 4mm filled with food grade silicon sealant and placed on cold rolled galvanised bottom tracks with a recess to provide floor to wall coving flush with the wall panel. This includes all required harware for completion Panels to be covered with a protective film to avoid any damages during transportation and installation; 5: Sqm; 6: 7450; 13: 297.52; 14: 2216524; 16: 0 | SI
9 |  | 4: Supply and installation of 50mm thick double skin ceiling system made of 0.8 mm thick Powder Coated GI sheets on both sides, 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, panels flush towards room side with maximum allowable gap of 3-4mm at panel to panel joints filled with silicon sealant. Ceiling panels are suspended from the RCC slab by using concealed AL ceiling grid with tie rod and adjustable turn buckle arrangement etc. This includes all required hardware for completion. Panels to be covered with a protective film to avoid any damages during transportation and installation; 5: Sqm; 6: 7450; 13: 163.08; 14: 1214946; 16: 0 | SI
10 |  | 4: Acoustic Wall Panelling with framework consisting of 25mm high GI wall channels with fully knurled surface of 0.55mm thick bottom wedge of 80mm width, having two equal flanges of 26mm is anchored to GI studs of 50mm high. GI studs of 50mm High to be fixed to wall at 600mm centres, 25mm thick channels are then fixed perpendicular to the GI studs and suitable fixing channel is fixed to the cross channel to fix the panel to achieve overall air gap of 75mm from the wall and GI Clips for inside panel and Clips for border panel of 18mm to be fixed to the GI wall channel to achieve required shape. Secured arranging of polyester wool of – thickness/density, Prelam Board to be installed. 15mm thick Prelam perforated Wooden slat of required dia perforation & pitch is to be customised and then fixed to GI frame rigidly by using fixing channel fastened perpendicular to the cross channel with GI brackets. The boards shall be fixed to the GI frame with special cleats. (MOTs Integration Room); 5: Sqm; 6: 6350; 13: 110; 14: 698500; 16: 0 | SI
11 |  | 4: Accooustic Ceiling Paneling with Perforated board Fine line Grid false ceiling using 11mm thick Perforated Board sheet tiles of size 595mm x 595mm fixing to steel precoated GI wall angle of size 25mm x 25mm x 0.70mm thick along the perimeter of ceiling screw fixed to brick work / partition at 610mm center to center and suspending the frame work using precoated GI Tee section (24mm x 38mm x 0.7mm) from soffit at 1220mm center to center fixed with GI Soffit Cleat, rawl plugs and steel expansion fasteners & connecting clip to the GI Tee section with 4mm dia GI rod with galvanised spring steel level clip of PVC unversal holding clips system at 1200mm center to center and Secured arranging of polyester wool of 50mm thick 1000 GSM, Prelam Board to be installed. 15mm thick Prelam perforated Wooden slat of required dia perforation & pitch is to be customised and then fixed to GI frame rigidly by using fixing channel fastened perpendicular to the cross channel with GI brackets. The boards shall be fixed to the GI frame with special cleats. (MOTs Integration Room); 5: Sqm; 6: 5700; 13: 62; 14: 353400; 16: 0 | SI
12 |  | 4: Wooden Flooring with Engineered wood planks of 14mm thick (MOTs Integration Room); 5: Sqm; 6: 7300; 13: 65; 14: 474500; 16: 0 | SI
13 |  | 4: Skirting for Wooden Flooring with Engineered wood planks of 14mm thick (MOTs Integration Room); 5: Rmt; 6: 900; 13: 40; 14: 36000; 16: 0 | SI
14 |  | 4: 80% blockout Ruler Blinds for MOTs Integration Room Windows; 5: Nos; 6: 12000; 13: 3; 14: 36000; 16: 0 | SI
15 |  | 4: Supply and installation of double pass RO system having 2 nos feed pumps of 1.5 HP with max flow of 4000 ltr/hr including construction of sand filter of dimensions (H=1650 mm, D=325 mm) with filter media as Quartz sand of SS vessel construction and Activated Carbon filter of dimensions (H= 1650mm) with filter media as Activated carbon (IV-600) of SS vessel construction, with 4 nos of spiral wound RO membrane of size 4 inch dia x 1 m length of make ION EXCHANGE (HYDROMEN) (or) equal, 2 nos UV system with service flow of 1000 ltr/hr (Before 2nd filter and after SS tank out-let) with PEX pipeline recirculation loop to avoid contamination in pipe to supply for 10 beds in Post ICU, 4 beds in Transplant ICU and 1 for each TIR.) Drinage outlet to be provided near each RO outlet.; 5: Job; 6: 6240000; 13: 1; 14: 6240000; 16: 0 | SI
16 |  | 4: Water Proofing of roof and peripheral walls of south west block, 8th floor, Gandhi Hospital which includes Dismantling of existing screed and lifting of debris to ground floor, Surface preparation and cracks treatment, Providing Angle fillet/taper of 75mm X 75mm with polymer modified mortor in the ratio of cement:sand:admixture (1:1.5:1.5) (Forsoc Nitobond SBR/M-Crete PC Bond @ 10% by weight of cement), Applying 1 coat of Forsoc Nitoproof WB Primer, Application of 2 coats of pitch free based liquid applied single component elastomeric waterproofing membrane (Forsoc Nito proof 600PF/BASF HLM5000), Laying 200 GSM Geotextile Fabric, Laying of 125mm Fiber Reinforced M20 grade protective concrete screed on terrace, Control joints treatment and External walls repair with window Frame-walls joints/Gaps treatment.; 5: Job; 6: 12611958; 13: 1; 14: 12611958; 16: 0 | SI
17 |  | 4: Supply of Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs with borders and design as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM (1:8) prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab , including neat cement slurry of honey like consistancy spread @ 3.3 kgs per Sqm. and jointed neately with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site (excluding cost of C.C. bed) including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in-charge etc.,and overheads & contractors profit complete for finished item of work. (APSS No.701 & 707).; 5: Sqm; 6: 2550; 13: 342; 14: 872100; 16: 0 | SI
18 |  | 4: Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707); 5: Rmt; 6: 250; 13: 120; 14: 30000; 16: 0 | SI
[12 empty] | TOTAL |  | 27907402.185
| TECHNICAL ASSISTANT | 4: DY.EXECUTIVE ENGINEER; 7: EXECUTIVE ENGINEER; 12: CHIEF ENGINEER
| Spl. Projects, TSMSIDC | 4: Spl. Projects, TSMSIDC; 7: Spl. Projects, TSMSIDC; 12: Spl. Projects, TSMSIDC
ELECTRICAL SUPPLIMENTAL WORKS
29 |  | 4: Supply, Transportation and installation of 20KVA / 312V DC on line UPS system (for emergency lighting in all rooms & Corridor except OTs & TIRs); 5: Nos; 6: 629358; 13: 2; 14: 1258716 | SI
30 |  | 4: 800 KVA Transformer OLTC for transformers with RTCC: Supply, Transportation, Installation, Testing and Commissioning of 800 KVA TRANSFORMER with all test reports. The Transformer shall be designed and manufactured as per IS:1180 OLTC with level-II with initial filling of oil as per IS 335-1993. 1000 A LT Breaker Kiosk - 01 No.The basic details of the Transformer are as under. Makes: Kirloskar / PETE / Esennar / Voltamp / Crompton / ABB / Schneider.; 5: Nos; 6: 4814994; 13: 1; 14: 4814994 | SI
31 |  | 4: 750 KVA Generator Set with AMF Control Panel Supply, Transportation, erection and commissioning (Excluding Foundation) of 3 Phase, 415, 50Hz, water cooled multi cylinder diesel generator set with alternator of 750 KVA output continuous rating directly coupled Engine and Alternator 750 KVA, 415 Volts with guard and mounted on a common base plate of Robust construction and complete with AMF panel having IP-52 protection, Acoustic Enclosure as per CPCB norms , sound absorbing material, t to restrict sound level up to 75 dB up to 1 Mtr distance and as per CPCB norms etc.; 5: Nos; 6: 9540000; 13: 1; 14: 9540000 | SI
[12 empty] | TOTAL |  | 15613710
| TECHNICAL ASSISTANT | 4: DY.EXECUTIVE ENGINEER; 7: EXECUTIVE ENGINEER; 12: CHIEF ENGINEER
| Spl. Projects, TSMSIDC | 4: Spl. Projects, TSMSIDC; 7: Spl. Projects, TSMSIDC; 12: Spl. Projects, TSMSIDC
ELV SUPPLIMENTAL WORKS
S.No | Tech. Spec Cl. No in TED | 2: Item S.No; 3: Item Code; 4: Item Name; 7: As Per Agreement (with 4 Ots); 9: Additional Sanction fot 2 Ots; 11: Total (6 Ots); 13: As Per Work Done/To Be Done
[5 empty] | UOM | Unit Rate (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.) | QTY | Amount (Rs.)
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
27 |  | 4: Recording in counselling room; 5: Job; 6: 155378; 13: 1; 14: 155378 |  |  | SI
28 |  | 4: Local Area Network (LAN) System; 5: Job; 6: 460242; 13: 1; 14: 460242 |  |  | SI
[12 empty] | TOTAL |  | 615620
| TECHNICAL ASSISTANT | 4: DY.EXECUTIVE ENGINEER; 7: EXECUTIVE ENGINEER; 12: CHIEF ENGINEER
| Spl. Projects, TSMSIDC | 4: Spl. Projects, TSMSIDC; 7: Spl. Projects, TSMSIDC; 12: Spl. Projects, TSMSIDC
EQUIPMENT SUPPLIMENTAL
32 |  | 4: Monitor Stand beside Bed in ICUs & TIRs; 5: Nos; 6: 6176; 13: 31; 14: 191456 |  |  | SI
[12 empty] | TOTAL |  | 191456
| TECHNICAL ASSISTANT | 4: DY.EXECUTIVE ENGINEER; 7: EXECUTIVE ENGINEER; 12: CHIEF ENGINEER
| Spl. Projects, TSMSIDC | 4: Spl. Projects, TSMSIDC; 7: Spl. Projects, TSMSIDC; 12: Spl. Projects, TSMSIDC
MGPS SUPPLIMENTAL WORKS
19 |  | 4: 4 Gas Digital Alarm Panels : 4 Gas Digital Alarm Panel consisting of atl necessary accessories ie Pressure sensors,reguIators,hand valves ,pressure gauges ecL(Oxygen, Nitrous oxide, Medical Air, Vacuum) (for TIRs); 5: Nos; 6: 42150; 13: 2; 14: 84300 |  |  | SI
20 |  | 4: 6 Gas Digital Alarm Panele : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. (for OTs); 5: Nos; 6: 60008; 13: 6; 14: 360048 |  |  | SI
21 |  | 4: Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. (for TIRs); 5: Nos; 6: 22201; 13: 2; 14: 44402 |  |  | SI
22 |  | 4: 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen.; 5: Job; 6: 48103; 13: 1; 14: 48103 |  |  | SI
24 |  | 4: 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide.; 5: Job; 6: 48103; 13: 1; 14: 48103 |  |  | SI
25 |  | 4: 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide.; 5: Job; 6: 17401; 13: 1; 14: 17401 |  |  | SI
23 |  | 4: Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED.; 5: Job; 6: 222013; 13: 1; 14: 222013 |  |  | SI
26 |  | 4: Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041 C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED; 5: Job; 6: 222013; 13: 1; 14: 222013 |  |  | SI
[12 empty] | TOTAL |  | 1046383
| TECHNICAL ASSISTANT | 4: DY.EXECUTIVE ENGINEER; 7: EXECUTIVE ENGINEER; 12: CHIEF ENGINEER
| Spl. Projects, TSMSIDC | 4: Spl. Projects, TSMSIDC; 7: Spl. Projects, TSMSIDC; 12: Spl. Projects, TSMSIDC

## Sheet1 (hidden)
S.No | Description | UOM | QTY | Rate | Amount
1 | Providing dadooing to walls with glazed full body ceramic wall tiles of size 800 x 1600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. (at Entrance) | Sqm | 119.35 | 4665 | 556767.75
| Dadoing Rate | Sqm | 2899
| Maintanance @ 5% per year for 4 years | Sqm | 580
| Sub Total |  | 3479
| Contractor Profit @ 13.615 | Sqm | 474
| Rate excluding GST | Sqm | 3953
| Rate includng GST @ 18% | Sqm | 4665

## GA (3) (hidden)
Name of Work: Design, Fabrication, Installation and Commissioning on Turnkey basis for the work of Establishment of State Organ Transplant Centre in the 8th Floor, South West Block of Gandhi Hospital, Secunderabad.
COMPARATIVE STATEMENT FOR GENERAL ABSTRACT OF ORIGINAL AGREEMENT AND REVISED ESTIMATE
S.No | Description |  |  | As per Agreement-1 | As per Agreement-2 for additional 2 OT's | Total As per Agreement (4+5) | As per Workdone/To be done Estimate | Excess | Less | Remarks
|  |  |  | (in Rs.) | (in Rs.) | (in Rs.) | (in Rs.) | (in Rs.) | (in Rs.)
1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | Civil Works |  |  | 40701300.8 | 7352080 | 48053380.8 | 43223650.441 | 0 | 4829730.359
2 | Electrical Works |  |  | 45337380 | 5440000 | 50777380 | 49845130 | 0 | 932250
3 | ELV Work |  |  | 2850000 | 0 | 2850000 | 3150000 | 300000 | 0
4 | Fire Fighting Work |  |  | 3892000 | 0 | 3892000 | 4118200 | 226200 | 0
5 | Equipment |  |  | 46177500 | 21690000 | 67867500 | 71887500 | 4020000 | 0
6 | Air Conditioning Work |  |  | 21104000 | 4610000 | 25714000 | 32960000 | 7246000 | 0
7 | Plumbing Work |  |  | 611340 | 0 | 611340 | 473957.52 | 0 | 137382.48
8 | MGPS Work |  |  | 15099700 | 449900 | 15549600 | 16967800 | 1418200 | 0
| Sub Total-Agreement (A) |  |  | 175773220.8 | 39541980 | 215315200.8 | 222626237.961 | 13210400 | 5899362.839 | Excess is 56,87,787
9 | Civil Supplimental Works |  |  |  |  | 0 | 27907402.185 | 27907402.185 | 0
10 | Electrical Supplimental Works |  |  |  |  | 0 | 15613710 | 15613710 | 0
11 | ELV Supplimental Work |  |  |  |  | 0 | 615620 | 615620 | 0
12 | Equipment Supplimental |  |  |  |  | 0 | 191456 | 191456 | 0
13 | MGPS Supplimental Work |  |  |  |  | 0 | 1046383 | 1046383 | 0
| Sub Total-Supplimental (B) |  |  | 0 | 0 | 0 | 45374571.185 | 45374571.185 | 0
| Total (A+B) |  |  | 175773220.8 | 39541980 | 215315200.8 | 268000809.146 | 52685608.346 | 0 |  | 228458829.146 | 52685608.346
| Basic Price (Excluding GST) |  |  | 148960356.6102 | 33510152.5424 | 182470509.1525 | 227119329.7847 | 44648820.6322 | 0
| GST @ 18% | 18% |  | 26812864.1898 | 6031827.4576 | 32844691.6475 | 40881479.3613 | 8036787.7138 | 0
| Total |  |  | 175773220.8 | 39541980 | 215315200.8 | 268000809.146 | 52685608.346 | 0
14 | Labour Cess @ 1% on Basic Price of Revised Estimate | 1% | 182470509.1525 |  |  |  | 1824705.0915 | 1824705.0915 | 0
15 | NAC @ 0.1% on Basic Price of Revised estimate | 0.1% | 182470509.1525 |  |  |  | 182470.5092 | 182470.5092 | 0
16 | Provision towards Seniorage Charges on Civil Component |  | 2549 |  |  |  | 2549 | 2549 | 0
17 | Provision towards DMF Charges 30% on Seniorage Charges | 30% | 2549 |  |  |  | 764.7 | 764.7 | 0
18 | Provision towards SMFT Charges 2% on seniorage Charges | 2% | 2549 |  |  |  | 50.98 | 50.98 | 0
| Provision towards Haritha Nidhi | 0.01% |  |  |  |  | 22711.933 | 22711.933 | 0
| Sub total of S.No 14 to 18 | [5 empty] | 2033252.2137
19 | Provision towards GST 18% on Seniorage Charges | 18% | 2033252.2137 |  |  |  | 365985.3985 | 365985.3985 | 0
21 | Provision towards Engineering Supervision Charges @ 4% on RE Value | 4% | 215315200.8 |  |  |  | 8612608.032 | 8612608.032 | 0 |  |  | 195947053
22 | Provision towards Unforseen items and rounding off (LS) | 0.5% | 215315200.8 |  | 0 |  | 1076576.004 | 1076576.004 | 0
| Sub Total (Other than RE ECV ) |  |  |  | 0 | 0 | 12088421.6481 | 12088421.6481 | 0
| Grand Total |  |  | 175773220.8 | 39541980 | 227403622.4481 | 280089230.7941 | 64774029.9941 | 0
[5 empty] | As Per Agreement |  | 215315200.8 | Excess | 64774029.9941
[5 empty] | As Per RE |  | 280089230.7941 | Less | 0
[5 empty] | Difference |  | 64774029.9941 | Difference | 64774029.9941
| DY.EXECUTIVE ENGINEER |  |  |  | EXECUTIVE ENGINEER |  |  |  | SUPERINTENDING ENGINEER
| TSMSIDC, MEDCHAL MALKAJGIRI |  |  |  | TSMSISDC, HYDERAVAD DIVISION |  |  |  | TSMSISDC, HYDERAVAD CIRCLE
0.711

## GA (4) (hidden)
Name of Work: Design, Fabrication, Installation and Commissioning on Turnkey basis for the work of Establishment of State Organ Transplant Centre in the 8th Floor, South West Block of Gandhi Hospital, Secunderabad.
COMPARATIVE STATEMENT FOR GENERAL ABSTRACT OF ORIGINAL AGREEMENT AND REVISED ESTIMATE
S.No | Description |  |  | As per Agreement-1 | As per Agreement-2 for additional 2 OT's | Total As per Agreement (4+5) | As per Workdone/To be done Estimate | Excess | Less | Remarks
|  |  |  | (in Rs.) | (in Rs.) | (in Rs.) | (in Rs.) | (in Rs.) | (in Rs.)
1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | Civil Works |  |  | 40701300.8 | 7352080 | 48053380.8 | 43223650.441 | 0 | 4829730.359
2 | Electrical Works |  |  | 45337380 | 5440000 | 50777380 | 49845130 | 0 | 932250
3 | ELV Work |  |  | 2850000 | 0 | 2850000 | 3150000 | 300000 | 0
4 | Fire Fighting Work |  |  | 3892000 | 0 | 3892000 | 4118200 | 226200 | 0
5 | Equipment |  |  | 46177500 | 21690000 | 67867500 | 71887500 | 4020000 | 0
6 | Air Conditioning Work |  |  | 21104000 | 4610000 | 25714000 | 32960000 | 7246000 | 0
7 | Plumbing Work |  |  | 611340 | 0 | 611340 | 473957.52 | 0 | 137382.48
8 | MGPS Work |  |  | 15099700 | 449900 | 15549600 | 16967800 | 1418200 | 0
| Sub Total-Agreement (A) |  |  | 175773220.8 | 39541980 | 215315200.8 | 222626237.961 | 13210400 | 5899362.839 | Excess is 56,87,787
9 | Civil Supplimental Works |  |  |  |  | 0 | 27907402.185 | 27907402.185 | 0
10 | Electrical Supplimental Works |  |  |  |  | 0 | 15613710 | 15613710 | 0
11 | ELV Supplimental Work |  |  |  |  | 0 | 615620 | 615620 | 0
12 | Equipment Supplimental |  |  |  |  | 0 | 191456 | 191456 | 0
13 | MGPS Supplimental Work |  |  |  |  | 0 | 1046383 | 1046383 | 0
| Sub Total-Supplimental (B) |  |  | 0 | 0 | 0 | 45374571.185 | 45374571.185 | 0
| Total (A+B) |  |  | 175773220.8 | 39541980 | 215315200.8 | 268000809.146 | 52685608.346 | 0 |  | 228458829.146 | 52685608.346
| Basic Price (Excluding GST) |  |  | 148960356.6102 | 33510152.5424 | 182470509.1525 | 227119329.7847 | 44648820.6322 | 0
| GST @ 18% | 18% |  | 26812864.1898 | 6031827.4576 | 32844691.6475 | 40881479.3613 | 8036787.7138 | 0
| Total |  |  | 175773220.8 | 39541980 | 215315200.8 | 268000809.146 | 52685608.346 | 0
14 | Labour Cess @ 1% on Basic Price of Revised Estimate | 1% | 227119329.7847 |  |  |  | 2271193.2978 | 2271193.2978 | 0
15 | NAC @ 0.1% on Basic Price of Revised estimate | 0.1% | 227119329.7847 |  |  |  | 227119.3298 | 227119.3298 | 0
16 | Provision towards Seniorage Charges on Civil Component |  | 2549 |  |  |  | 2549 | 2549 | 0
17 | Provision towards DMF Charges 30% on Seniorage Charges | 30% | 2549 |  |  |  | 764.7 | 764.7 | 0
18 | Provision towards SMFT Charges 2% on seniorage Charges | 2% | 2549 |  |  |  | 50.98 | 50.98 | 0
| Provision towards Haritha Nidhi | 0.01% |  |  |  |  | 22711.933 | 22711.933 | 0
| Sub total of S.No 14 to 18 | [5 empty] | 2524389.2406
19 | Provision towards GST 18% on Seniorage Charges | 18% | 2524389.2406 |  |  |  | 454390.0633 | 454390.0633 | 0
21 | Provision towards Engineering Supervision Charges @ 4% on RE Value | 4% | 268000809.146 |  |  |  | 10720032.3658 | 10720032.3658 | 0 |  |  | 195947053
22 | Provision towards Unforseen items and rounding off (LS) | 0.5% | 268000809.146 |  | 0 |  | 1340004.0457 | 1340004.0457 | 0
| Sub Total (Other than RE ECV ) |  |  |  | 0 | 0 | 15038815.7155 | 15038815.7155 | 0
| Grand Total |  |  | 175773220.8 | 39541980 | 215315200.8 | 283039624.8615 | 67724424.0615 | 0
[5 empty] | As Per Agreement |  | 215315200.8 | Excess | 67724424.0615
[5 empty] | As Per RE |  | 283039624.8615 | Less | 0
[5 empty] | Difference |  | 67724424.0615 | Difference | 67724424.0615
| TECHNICAL ASSISTANT |  |  | DY.EXECUTIVE ENGINEER |  | EXECUTIVE ENGINEER |  |  | CHIEF ENGINEER
| Spl. Projects, TSMSIDC |  |  | Spl. Projects, TSMSIDC |  | Spl. Projects, TSMSIDC |  |  | TSMSIDC

## Abstract (3) (hidden)
Name of Work: Design, Fabrication, Installation and Commissioning on Turnkey basis for the work of Establishment of State Organ Transplant Centre in the 8th Floor, South West Block of Gandhi Hospital, Secunderabad.
GENERAL ABSTRACT FOR REVISED ESTIMATE
S.No | Description |  |  | Amount (Rs.)
1 | Civil Works |  |  | #REF!
2 | Electrical Works |  |  | #REF!
3 | ELV Work |  |  | #REF!
4 | Fire Fighting Work |  |  | #REF!
5 | Equipment |  |  | #REF!
6 | Air Conditioning Work |  |  | #REF!
7 | Plumbing Work |  |  | #REF!
8 | MGPS Work |  |  | #REF!
| Sub Total-Agreement (A) |  |  | 222626238
9 | Civil Supplimental Works |  |  | #REF!
10 | Electrical Supplimental Works |  |  | #REF!
11 | ELV Supplimental Work |  |  | #REF!
12 | Equipment Supplimental |  |  | #REF!
13 | MGPS Supplimental Work |  |  | #REF!
| Sub Total-Supplimental (B) |  |  | 45374570.825
| Total (A+B) |  |  | 268000808.825
| Basic Price (Excluding GST) |  |  | 227119329.5127
| GST @ 18% |  |  | 40881479.3123
| Total |  |  | #REF!
14 | Labour Cess @ 1% on Basic Value of Revised Estimate |  |  | 2271193.2951
15 | NAC @ 0.1% on Basic Value of Revised estimate |  |  | 227119.3295
16 | Provision towards Seniorage Charges on Civil Component |  |  | 2549
17 | Provision towards DMF Charges 30% on Seniorage Charges |  |  | 764.7
18 | Provision towards SMFT Charges 2% on seniorage Charges |  |  | 50.98
19 | Provision towards Haritha Nidhi |  |  | 22711.933
| Total of S.No 14 to 19 |  |  | 2524389.2376
20 | Provision towards GST 18% on Seniorage Charges |  |  | 454390.0628
21 | Provision towards Engineering Supervision Charges @ 4% on RE Value (except equipment & AC) |  |  | 10720032.353
22 | Provision towards Unforseen items and rounding off (LS) |  |  | 1340004.0441
| Sub Total (Other than RE ECV ) |  |  | #REF!
| Grand Total |  |  | 283039624.5225
TECHNICAL ASSISTANT |  | DY.EXECUTIVE ENGINEER | EXECUTIVE ENGINEER | CHIEF ENGINEER
Spl. Projects, TSMSIDC |  | Spl. Projects, TSMSIDC | Spl. Projects, TSMSIDC | TSMSIDC

## Sheet5 (2) (hidden)
S.No | Description |  | Amount
1 | Terrace & Exterior walls water proofing |  | 12611958
a | Terrace Area: 1700 Sqm @ Rs.3855/Sqm |  |  |  | 6553500
b | External Wall Area: 1700 Sqm @ Rs.700/Sqm |  |  |  | 1190000
c | Sunshade Area: 645 Sqm @ Rs.4400/Sqm |  |  |  | 2838000
d | Window Frame Treatment: 300 Rmt @Rs.357/Rmt |  |  |  | 107100
GST on above @ 18% - Rs.19,23,858
2 | Double Pass Reverse Osmosis (RO) plant with recirculation loop |  | 6240000 |  | 10688600
3 | 800 KVA Transformer |  | 4814994 |  | 12612548
4 | 750 KVA DG set with AMF panel |  | 9540000 |  | 1923948
5 | O2 & N2O Manifold, Auto Control Systems & 4 & 6 Gas Digital Alarm Systems |  | 1046383 | 1923858
6 | 20 KVA/312V DC Online UPS System |  | 1258716
7 | Recording Counselling Room & Local Area Network |  | 615620
8 | Enhance the aesthetics at the entrance lobby |  | 556931
9 | Miscellaneous works: |  | 8689968
a | Under-deck thermocol insulation | 266418
b | PCC M 25 grade | 328837
c | Floor leveler compound | 1288362
d | Monitor Stand beside Bed | 191456
e | V-Board Partitions on top of false ceiling | 58240
f | Sliding doors | 624685
g | PCGI wall & ceiling panels | 3431470
h | Acoustic wall & ceiling paneling | 1051900
i | Wooden flooring in MOTsIntegration room | 546500
j | Double charged vitrified tiles | 902100
| Sub-Total (a to j) | 8689968
| Total |  | 45374570
a

## Sheet2 (hidden)
1 |  | SOTC243 | Supply and installation of Under-deck Thermocol insulation sheets of 40 mm thick having more than 30 Kg/m3 density to ceiling by brush application of bituminous adhesive to the sheets and secured with screw along with washer at the centre of the sheet supported with GI wire running diagonally to the sheet of 2mm dia. (in ICUs & MOTs Integration Room) | Sqm | 1014 | 262.74 | 266418 | 0 | 0
2 |  | SOTC244 | Supply and placing of the Design Mix Plain Cement Concrete of M 25 grade corresponding to IS 456 with minimum cement content of 380 kgs per 1 cum of concrete using Concrete Batching Plant with 20mm size graded machine crushed hard granite metal (coarse aggregate - as per IS 383 - 1970 and IS 2386 Part 1 to Part 8) including cost and conveyance of all materials like cement, fine aggregate (sand) coarse aggregate, water etc., to site and sales & other taxes on all materials. (in 6 OTs) | Cum | 11740 | 28.01 | 328837 | 0 | 0
3 |  | SOTC245 | Supply and Laying of Floor leveller compund (self smoothing mortar) to level the surface, having bulk density not less than 2 Kg/l for a fresh mortor, compressive strength not less than 20 N/mm2, initial setting time not more than 40 minutes and offer a 25 minutes working time, The surface should be walkabe after 30 min of laying. (all rooms & corridors except OTs, TIRs and Sterile corridor) | Sqm | 1460 | 882.44 | 1288362 | 0 | 0
4 |  | SOTC246 | Providing dadooing to walls with glazed full body ceramic wall tiles of size 800 x 1600 mm with any type of design texture such as marble finish, wooden, bamboo, stone finishes etc., scratch less, stain free and thickness between 6-8 mm 1st quality conforming to IS:13711, IS:13712, IS:13630 Parts 1 to 15 of any colour and finish in all shades and designs with borders as approved by Engineer-in-Charge set over base coat of CM1:5 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc., complete for finished item of work. (at Entrance) | Sqm | 4665 | 119.385 | 556931 | 0 | 0
5 |  | SOTC247 | Providing (1500 X 2100) single sliding door operated by elbow switches / foot switch as well as touchless sensor of 10mm thick toughened glass (Saint Gobin / Modi Guard) fixed in SS 304 grade 2 Track top channel of 45 mm (one track to hold fixed glass partition in position and second track with top rollers suitably angled to reduce resistance to movement to facilitate smooth sliding movement of the door). Single track bottom channel to be provided for fixed glass partition. Floor guide to be provided for smooth sliding of the door. Concealed door handle of (150 mm) to be provided in cutout on the sliding door for manual operation when required. All fittings provided should be of Titon /Ozone / Enox make in SS 304 - In TIRs | Nos | 270276 | 2 | 540552 | 94600 | 189200
6 |  | SOTC248 | V-Board Partitions on top of false ceiling for partitioning of sterile corridor and non-sterile corridor (for dividing corridors into zones above ceiling) | Sqm | 3640 | 16 | 58240 | 1274.0625 | 20385
7 |  | SOTC249 | GI Powder Coated Sliding Doors (0.8mm shutter sheet thk & 1.2mm frame sheet thk with Single Rebate and Honeycomb Infill) Double Leaf Door 1200 x 2100mm with Accessories (Sliding Track for Double Door, Sliding Dead Lock Enox, Concealed Handles 100mm Ahlada, Flush Bolt 300mm Ahlada, SS304 Kick Plate upto 350mm ht, DG Clear Float Glass 350x750x6mm with Adhesive Tape & Silicon Sealant) (for change rooms to corridor entrance) | Nos | 84133 | 1 | 84133 | 29450 | 29450
8 |  | SOTC250 | Supply and installation of 50mm thick double skin modular wall Panels made of 0.8 mm thick powder coated GI on both the sides, with 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, flush on both sides with maximum allowable gap of 3- 4mm filled with food grade silicon sealant and placed on cold rolled galvanised bottom tracks with a recess to provide floor to wall coving flush with the wall panel. This includes all required harware for completion Panels to be covered with a protective film to avoid any damages during transportation and installation | Sqm | 7450 | 297.52 | 2216524 | 756.252 | 225000
9 |  | SOTC251 | Supply and installation of 50mm thick double skin ceiling system made of 0.8 mm thick Powder Coated GI sheets on both sides, 40 plus or minus 2 kg/m3 density PUF as infill, GI profiles all along the periphery, panels flush towards room side with maximum allowable gap of 3-4mm at panel to panel joints filled with silicon sealant. Ceiling panels are suspended from the RCC slab by using concealed AL ceiling grid with tie rod and adjustable turn buckle arrangement etc. This includes all required hardware for completion. Panels to be covered with a protective film to avoid any damages during transportation and installation | Sqm | 7450 | 163.08 | 1214946 | 1073.0929 | 175000
10 |  | SOTC252 | Acoustic Wall Panelling with framework consisting of 25mm high GI wall channels with fully knurled surface of 0.55mm thick bottom wedge of 80mm width, having two equal flanges of 26mm is anchored to GI studs of 50mm high. GI studs of 50mm High to be fixed to wall at 600mm centres, 25mm thick channels are then fixed perpendicular to the GI studs and suitable fixing channel is fixed to the cross channel to fix the panel to achieve overall air gap of 75mm from the wall and GI Clips for inside panel and Clips for border panel of 18mm to be fixed to the GI wall channel to achieve required shape. Secured arranging of polyester wool of – thickness/density, Prelam Board to be installed. 15mm thick Prelam perforated Wooden slat of required dia perforation & pitch is to be customised and then fixed to GI frame rigidly by using fixing channel fastened perpendicular to the cross channel with GI brackets. The boards shall be fixed to the GI frame with special cleats. (MOTs Integration Room) | Sqm | 6350 | 110 | 698500 | 1363.636 | 150000
11 |  | SOTC253 | Accooustic Ceiling Paneling with Perforated board Fine line Grid false ceiling using 11mm thick Perforated Board sheet tiles of size 595mm x 595mm fixing to steel precoated GI wall angle of size 25mm x 25mm x 0.70mm thick along the perimeter of ceiling screw fixed to brick work / partition at 610mm center to center and suspending the frame work using precoated GI Tee section (24mm x 38mm x 0.7mm) from soffit at 1220mm center to center fixed with GI Soffit Cleat, rawl plugs and steel expansion fasteners & connecting clip to the GI Tee section with 4mm dia GI rod with galvanised spring steel level clip of PVC unversal holding clips system at 1200mm center to center and Secured arranging of polyester wool of 50mm thick 1000 GSM, Prelam Board to be installed. 15mm thick Prelam perforated Wooden slat of required dia perforation & pitch is to be customised and then fixed to GI frame rigidly by using fixing channel fastened perpendicular to the cross channel with GI brackets. The boards shall be fixed to the GI frame with special cleats. (MOTs Integration Room) | Sqm | 5700 | 62 | 353400 | 1223.79 | 75875
12 |  | SOTC254 | Wooden Flooring with Engineered wood planks of 14mm thick (MOTs Integration Room) | Sqm | 7300 | 65 | 474500 | 1230.7692 | 80000
13 |  | SOTC255 | Skirting for Wooden Flooring with Engineered wood planks of 14mm thick (MOTs Integration Room) | Rmt | 900 | 40 | 36000 | 315 | 12600
14 |  | SOTC256 | 80% blockout Ruler Blinds for MOTs Integration Room Windows | Nos | 12000 | 3 | 36000 | 4200 | 12600
15 |  | SOTC257 | Supply and installation of double pass RO system having 2 nos feed pumps of 1.5 HP with max flow of 4000 ltr/hr including construction of sand filter of dimensions (H=1650 mm, D=325 mm) with filter media as Quartz sand of SS vessel construction and Activated Carbon filter of dimensions (H= 1650mm) with filter media as Activated carbon (IV-600) of SS vessel construction, with 4 nos of spiral wound RO membrane of size 4 inch dia x 1 m length of make ION EXCHANGE (HYDROMEN) (or) equal, 2 nos UV system with service flow of 1000 ltr/hr (Before 2nd filter and after SS tank out-let) with PEX pipeline recirculation loop to avoid contamination in pipe to supply for 10 beds in Post ICU, 4 beds in Transplant ICU and 1 for each TIR.) Drinage outlet to be provided near each RO outlet. | Job | 6240000 | 1 | 6240000 | 4459625 | 4459625
16 |  | SOTC258 | Terrace Water Proofing: Dismantling and shifting of debris to Ground Floor: Dismantling the existed Concrete Screed flooring completely by using mechanical chipping machine, and shifting debris from terrace to ground floor. | sqm | 306.8 | 1700 | 521560 | 4414185 | 7504114500
17 |  | SOTC259 | Terrace Water Proofing: Surface Preparation & Cracks Treatment: Prepare the surface thoroughly by cleaning and wash , removing dust, dirt, oil, grease and loose particle with high 160 bar pressure water Jet pumps. Find the cracks on rcc slab, Shrinkage and non-moving cracks should be pre-treated by cutting the crack @10mmx10mm, prepare the cracks dust free by using of wire brush& air blower, mix the two components of low viscosity epoxy epoxy resin Fosroc Conbextra EP10 two components epoxy injection grout and treat the cracks. Seal the ceacks with Fosroc Nitoseal PU 50 single-component moisture-cure, polyurethane hybrid joint sealant. | Sqm | 206.5 | 1700 | 351050 |  | 0
18 |  | SOTC260 | Terrace Water Proofing: Angle fillet / taper: Providing angle fillet of 75mmx75mm with polymer modified mortar in the ratio of cement: sand: aggregate in the ratio of (1:1.5:1.5) admixed with Fosroc Nitobond SBR/M-Crete PC Bond SBR @10% by the weight of cement to avoid cracking at 90º angle of RCC slab & Masonry wall joints. iv) | Sqm | 507.4 | 650 | 329810 |  | 0
29 |  | SOTC261 | Terrace Water Proofing: Primer Coat: Applying 1 coat of Fosroc Nitoproof WB Primer is a two component product and must be mixed & applied in order to perform as specified. Transfer base and the hardener to a suitable fresh container and mix thoroughly with a slow speed mixer for 2 -3 minutes which makes the mix as a milky white paste . Add double the quantity of clean water by volume to the mix gradually under mixing which makes the mix as low viscous milky white liquid. The diluted primer should be applied at a coverage of 8-10 m2/litre, preferably using roller. The applied primer should be allowed to reach tack free condition before applying liquid applied coatings and membranes. The tack free condition of Nitoproof WB primer happens after 4-5 hours of application @ 27 deg. | Sqm | 159.3 | 1700 | 270810 |  | 0
30 |  | SOTC262 | Terrace Water Proofing: Application of 2 Coats of Pitch Free PU based Liquid applied single component elastomeric waterproofing membrane (Fosroc Nitoproof 600PF/BASF HLM5000). Apploication of Fosroc Nitoproof 600PF/BASF HLM 5000 can be applied by brush, squeegee, roller/ suitable spray applied machine. It is applied at a minimum wet fi lm thickness of 1.5mm in 2 coats. The second coat should be applied in perpendicular direction to the first coat. | Sqm | 1569.4 | 1700 | 2667980 |  | 0
31 |  | SOTC263 | Terrace Water Proofing: Laying 200 GSM Geotextile Fabric: Laying of 200GSM geotextile cloth over the waterproof coating with overlap of 30mm at cloth joints. | Sqm | 177 | 1700 | 300900 |  | 0
27 |  | SOTC264 | Terrace Water Proofing: Laying of 125mm Fiber Reinforced M20 Grade Protective Concrete Screed on Terrace. Marking the levels over the waterproofing system as per the slab level towards rain outlet. Laying of M20 grade fiber reinforced concrete screed, leveling the surface as per the marked levels, providing the proper slope to rain water outlets providing the neat kalai finish polymer modified slurry. Cut the 5mmx5mm groove for every 4mtrx4mtr between 24hrs-48 hrs of concrete laying. Provide water stoppers for curing with water. | Sqm | 1770 | 1700 | 3009000 |  | 0
28 |  | SOTC265 | Terrace Water Proofing: Control Joints Treatment: Provide the masking tape of bothe edges of joint, prepare the joints dust free by wire brush and air blower, seal the joints of 5mmx5mm with Fosroc Nitoseal PU50 single component polyurethane sealant by using PU Gun. Remove the masking tapes. | Sqm | 265.5 | 1060 | 281430 |  | 0
32 |  | SOTC266 | External Walls Repair & Waterproofing Treatment: RCC Sunshades Repairs : a. Check the damaged Rcc sunshades/projections/any plastered area damages by visual inspection & fiber hammer test. b. Mark those damaged area, cut the marked area with electronic cutting machine and remove the loose concrete/plaster and expose the reinforcement. c. Apply Fosroc Reebaklens RR Rustremover with brush for complete wetting of rusted reinforcement and allowed to react it for 16-24 hours. After 24 hours, clean the rust with wire brush & air blower. | Sqm | 5192 | 645 | 3348840 |  | 0
19 |  | SOTC267 | External wall waterproofing. a. Surface Preparation: Surface must be thoroughly cleaned by using 160 bar Jet pump to clean dust, fungus, algae, grease etc. Treat any areas affected by Algae, moss or fungal growth. b. Crack Filling: The surface to be checked for cracks, cut the cracks 5mmx5mm by electronic cutting machine, clean the cracks with wire brush and air blower, seal the cracks with Fosroc Nitoseal PU50 Polyurethane Sealant . c. External Wall Waterproof Coating: Priming:After the proper surface preparation and curing of repaired areas wash the surface well and maintaining it in saturated surface dry condition proceed for priming using Dr. Fixit Primeseal diluted in 2:1 ratio with water (2 parts Primeseal diluted with 1 part water). Maintain the spreading rate of 8-10 sq mtr per litre for a single coat application to achieve about 20 – 25 microns DFT. Allow it to dry for 6-8 hrs. | Sqm | 826 | 1700 | 1404200 |  | 0
20 |  |  | External wall waterproofing. d. Wash the reinforcement thoroughly with clean water. Wire brush again to remove remaining loose material and finish by thoroughly washing down with clean water and allow to complete dry. e. Appying of FOSROC Nitozinc primer to exposed existed reinforcement after cleaning the Rust, an unbroken 40 microns coating capable of provided 'active' galvanic protection for exposed reinforcement. f. Enhancing the bonding between Old RCC Ceiling to New Polymer Mortar with applying of SBR Based Polymer Modified Cementitious Bond coat admixed FOSROC Nitobond SBR/ M- Crete PC bond SBR. g. Providing 20mm of structural grade polymet modified mortar by Fosroc Renderoc S2/M- Crete PC Mortar Ultra with then 2nd layer of finishing will be done by polymer modified mortar with cement mortar 1:3 (cement:sand) admixed Fosroc Nitobond SBR/M-Crete PC bond SBR @10% by the weight of cement weight and water, make the proper finish to existed wall level. |  |  |  | 0 |  | 0
21 |  | SOTC268 | Window Frame-Wall Joints/Gaps Treatment: a. Cut the joint and make a groove of 5mmx5mm by electronic cutting machine, clean the cracks with wire brush and air blower, seal the cracks with Fosroc Nitoseal PU50 Polyurethane Sealant | Sqm | 421.26 | 300 | 126378 |  | 0
22 |  | SOTC269 | Supply of Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs with borders and design as per the approved flooring pattern as directed by the Engineer-In -Charge, laying tiles using spacers of 2mm thick, set over a base coat of CM (1:8) prop. 12mm thick using screened sand over CC bed already laid or RCC roof slab , including neat cement slurry of honey like consistancy spread @ 3.3 kgs per Sqm. and jointed neately with white cement paste to full depth mixed with pigment of matching shade including cost and conveyance of all materials like cement, sand, water, tiles, white cement etc., to site (excluding cost of C.C. bed) including cost of base coat and all labour charges for mixing of cement mortar, laying tiles to required slope as directed by the Engineer- in-charge etc.,and overheads & contractors profit complete for finished item of work. (APSS No.701 & 707). | Sqm | 2550 | 342 | 872100 | 0 | 0
24 |  | SOTC270 | Providing skirting to internal walls to 10 cm height with Double charged / multi charged stain free full body porcelain vitrified tiles with double layer pigment of size 600 x 600 mm and thickness between 8-10 mm 1st quality conforming to IS:15622 - 2017, IS:13630 (Parts 1 to 15) of any colour and finish in all shades and designs, length equal to flooring tiles, set over base coat of CM(1:5) 12 mm thick using screened sand with cement slurry of honey like consistency spread at the rate of 3.30 kgs per sqm and jointing with white cement paste mixed with pigment of matching shade to full depth, including cost of all materials like tiles, cement, sand and water etc.,and overheads & contractors profit complete for finished item of work.(APSS No.701 &707) | Rmt | 250 | 120 | 30000 | 0 | 0
25 |  | SOTC271 | Supply, Transportation and installation of 20KVA / 312V DC on line UPS system (for emergency lighting in all rooms & Corridor except OTs & TIRs) | Nos | 629358 | 2 | 1258716 | 100000 | 200000
23 |  | SOTC272 | 800 KVA Transformer OLTC for transformers with RTCC: Supply, Transportation, Installation, Testing and Commissioning of 800 KVA TRANSFORMER with all test reports. The Transformer shall be designed and manufactured as per IS:1180 OLTC with level-II with initial filling of oil as per IS 335-1993. 1000 A LT Breaker Kiosk - 01 No.The basic details of the Transformer are as under. Makes: Kirloskar / PETE / Esennar / Voltamp / Crompton / ABB / Schneider. | Nos | 4814994 | 1 | 4814994 | 1685250 | 1685250
26 |  | SOTC273 | 750 KVA Generator Set with AMF Control Panel Supply, Transportation, erection and commissioning (Excluding Foundation) of 3 Phase, 415, 50Hz, water cooled multi cylinder diesel generator set with alternator of 750 KVA output continuous rating directly coupled Engine and Alternator 750 KVA, 415 Volts with guard and mounted on a common base plate of Robust construction and complete with AMF panel having IP-52 protection, Acoustic Enclosure as per CPCB norms , sound absorbing material, t to restrict sound level up to 75 dB up to 1 Mtr distance and as per CPCB norms etc. | Nos | 9540000 | 1 | 9540000 | 3339000 | 3339000
|  | SOTC274 | Recording in counselling room | Job | 155378 | 1 | 155378 | 32000 | 32000
|  | SOTC275 | Local Area Network (LAN) System | Job | 460242 | 1 | 460242 | 120000 | 120000
|  | SOTC276 | Monitor Stand beside Bed in ICUs & TIRs | Nos | 6176 | 31 | 191456 | 645.1612 | 20000
|  | SOTC277 | 4 Gas Digital Alarm Panels : 4 Gas Digital Alarm Panel consisting of atl necessary accessories ie Pressure sensors,reguIators,hand valves ,pressure gauges ecL(Oxygen, Nitrous oxide, Medical Air, Vacuum) (for TIRs) | Nos | 42150 | 2 | 84300 | 14755 | 29510
|  | SOTC278 | 6 Gas Digital Alarm Panels : 6 Gas Digital Alarm Panel(Oxygen, Nitrous oxide, Medical Air, Surgical Air, Vacuum, Carbon dieoxide) consisting of all necessary accessories ie pressure sensors, regulators, hand vatves, pressure gauges etc. (for OTs) | Nos | 60008 | 6 | 360048 | 21002.5 | 126015
| TECHNICAL ASSISTANT | SOTC279 | Valve box -4 services : Valve box - 4 Service consisting of Isolation valve 15 mm OD - 04 Nos. and isolation valve 22 mm OD - 01 Nos. accessories ie Pressure gauge connection in a powder coated box The box consisting of lock & key and a brakable glass for emergency. (for TIRs) | Nos | 22201 | 2 | 44402 | 7770 | 15540
| Spl. Projects, TSMSIDC | SOTC280 | 4 + 4 size of O2 manifold system : 4+4 Oxygen Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at250Kg/Cum 2 pressure & Fully automatic control panel for Oxygen. | Job | 48103 | 1 | 48103 | 16835 | 16835
|  | SOTC281 | 4 + 4 size of N2O manifold system : 4+4 Nitrous oxide Main mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cylinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | Job | 48103 | 1 | 48103 | 16835 | 16835
|  | SOTC282 | 2 cylinder emergency maniféld - N2O : 2 Cylinder Nftmus oxide Emergency mannifold with 19mm ODx12mm I.D .Copper pipe mounted on top frame, Middle frmae and Bottom frame along with brass blocks, NRVs/ cytinder valves and pigtail pipes of 1m long of 8mm OD x 3mm I.D. duly tested at 250Kg/Cum 2 pressure & Fully automatic control panel for Nitrous Oxide. | Job | 17401 | 1 | 17401 | 6090 | 6090
|  | SOTC283 | Fully Automatic O2 Control System ”Manufactured under an ISO 9001: 2015 certified works. ”Control Panel cover made of M.S. duly powder coated. “Compact and fully automatic manifold control system far Oxygen services. *Easy to maintain and use. “Designed with both safety and continuity of flow supply at a constant pressure via to/o banks of bottled gas cylinders with following status monitoring. ”A-Bank in use (Green indication). ”B-Bank ready for use (Yelk›w indication). ”C-Empty Bank (Red indication). ”Control Panel has build in LED display to indicate Normal. High & Low line Pressure. ”It has facility to test all above indicators working perfectly. the Control Panel indudes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. ”Capable to provide a distribution distribution flow rate of 2IXI0 LPM or more for O2. the control panel incorporte safety puncture system in case pressure exceeds 100 Psi. ”In ease of failure of electronic pneumatics system, control can be used manually through by pass system. * CE CERTIFIED. | Job | 222013 | 1 | 222013 | 77705 | 77705
|  | SOTC284 | Fully Automatic N2O Control System Manufactured under an ISO 9001: 2015 certified works. *Control Panel cover made of M.S. duly powder coated. *Compact and fully automatic manifold control system for N2O services. Easy to maintain and use. *Designed with both safety and continuity of flow supply at a constant pressure via two banks of bottled gas cylinders with following status monitoring. *A-Bank in use (Green indication). *B-Bank ready for use (Yellow indication). Authorise&PITAL ENGINERS D-4 A, YADAV PARK, ROHTAK ROAD, NANGLOI, DELHI-110041 C-Empty Bank (Red indication). *Control Panel has build in LED display to indicate Normal. High & Low line Pressure. "It has facility to test all above indicators working perfectly. *The Control Panel includes Pressure gauge (63 mm) to indicate the gas pressure of each header and pipe line diistribution pressure. *Capable to provide a distribution flow rate of 500 LPM or more for N2O. *The control panel incorporte safety puncture system in case pressure exceeds 100 Psi. In ease of failure of electronic pneumatics system, control can be used manually through by pass system. CE CERTIFIED | Job | 222013 | 1 | 222013 | 77705 | 77705