## BOQ
QUOTE REF:NAIPL/VRV/2022-23/023
REVISION : R0
Date: 10-04-2023
To,
M/S. VARDHMAN MEDICARE PVT.LTD.
SUB: SUPPLY & INSTALLATION OF DAIKIN VRV SYSTEM
Dear Sir/Madam,
We thank you for giving us an opportunity to quote for the requirement of A/C for your esteemed organization. Here we wish to quote as per details given below.
PROJECT : M/S. VARDHMAN MEDICARE PVT.LTD.
HVAC VENDOR : NATIONAL AIRCON INDIA PVT LTD
S.no. | Description | Quantity | Unit | Supply Rate | Install Rate | Amount | Remarks
1 | Supply, transportation and installation of split AC unit 1.5 TR inverter type 3 Star capable of delivering 18000 BTU/hr and above with high wall mounted indoor unit and outdoor condensing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord , built-in stabilizer Voltage range 160- 264 volts and cordless remote control. Makes : Daikin / Thoshiba / O General. | 3 | No | 39000 | 2150 | 123450 | R-32 (3-Rmt copper Kit) Model:FTKL50UV16U
2 | Supply, transportation and installation of split AC unit 1.0 TR inverter type minimum 3 Star capable of delivering 12000 BTU/hr and above with high wall mounted indoor unit and outdoor condensing unit Hermetically sealed compressor suitable for operation on 230V, 50Hz, 1Phase AC supply capable of performing cooling dehumidifying air circulating and filtering with cooling and condensing units with 3.5 mts of copper piping, insulation kit and 4 mts of 3 core copper flexible chord , built-in stabilizer Voltage range 160- 264 volts and cordless remote control. Makes: Daikin / Thoshiba/ O General. | 3 | No | 32000 | 2150 | 102450 | R-32 (3-Rmt copper Kit) Model:FTKL35UV16W
3 | SITC of air cooled condensing units with two scroll compressors, air cooled condenser, power panel, vibration isolating pads, stand for ODU, thermostat, etc. of the following capacities. The nominal capacity of the condensing unit shall be as under. Air cooled condensing unit shall have horizontal discharge. All refrigerant piping accessories sight glass, drier, expansion 3valve, etc. shall be supplied with the condensing units and suitable to connect above AHUs. Refrigerant shall be R 407C / R 410A. Necessary thermostat, control wiring, etc. shall be included. Derating of the unit shall not be more than 15percentage under 45 deg. C ambient temperature. Condensing unit shall be capable of operating up 50 deg. C ambient temperature. 8.5 TR capacity. | 3 | No. | 105140 | 19000 | 372420 | Model:RR100FRY16
4 | SITC of Flange type, Flame proof FLP duct heaters of 5 kW capacity with Mineral Filled AISI SS304/SS321 Sheathed Tubular Heater with GI Helical fins, Tube dia 8.2mm min and Helical Finn dia 25mm min, enclosed in the frame, FLP Terminal box etc., Nickel Chromium Inner Element, Silicon Sealing to Restrict Moisture pickup, Silver brazed mounting plate etc., and heaters shall be controlled with PID thyrestor controller based on the analog output signal of 0-10 V DC of controller . And this should have saftey thermostat and cutouts and air stat etc. all safety controls. The capacities as follows and sizes of the heaters shall be as per the duct sizes and approved drawing. | 3 | No. | 67000 | 15000 | 246000 | Isotherm
5 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Liquid Line | 60 | RMT | 3100 | 750 | 231000 | Considered GC Copper pipe With Cable Tray(OEM Approved)
6 | SITC of 20/21 G hard drawn copper refrigerant piping with all fittings, supports, insulation with 19 mm thk class O nitrile rubber insulation with factory laminated glass cloth for physical protection and UV protection etc. Quality of copper piping fittings shall be suitable for 18 G piping. Copper piping shall be clamped at every 1.5 mt. distance. copper piping shall be laid on inverted GI perforated cable trays and clamps as per specification inside the building. Copper piping on the terrace shall be laid with bottom and top cable tray. Thickness of the tray shall be 1.6 mm. Copper pipe size shall be as per OEM standards. Suction Line | 60 | RMT | 3100 | 750 | 231000 | Considered GC Copper pipe With Cable Tray(OEM Approved)
7 | SITC of CPVC drain ping with supports, clamps and 9 mm thk. Nitrile rubber tube insulation of the following sizes. Insulation shall have factory laminated glass cloth. 32mm Dia | 150 | RMT | 330 | 50 | 57000 | Finolex/Supreme
8 | SITC of CPVC drain ping with supports, clamps and 9 mm thk. Nitrile rubber tube insulation of the following sizes. Insulation shall have factory laminated glass cloth. 25mm Dia | 150 | RMT | 252 | 50 | 45300 | Finolex/Supreme
9 | Condensing units - VRF/VRV System : Supply, Installation, Nitrogen testing, Vacuuming and Commissioning of air cooled variable refrigerant flow modular type condensing units, each comprising of multiple scroll compressors all inverter driven, full charge of refrigerant gas R-410a including additional gas filling , lubricating oil and all accessories as per the specifications. The condensing units shall be suitable to work on cooling mode. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B . The COP of the system shall be greater than 4 under ARI conditions for 100percentage load . The condensing units shall be suitable for operation on 415 plus or minus 10percentage volts, 50Hz, 3 phase AC power supply and , outdoor units to be mounted on MS platform with suitable Vibration Isolation pads to avoid vibrations. All the supports and angle base frame structure to be duly black painted with synthetic epoxy paint. the condensing units shall be of following capacities: The VRF ODU should be capable of working with total capacity of connected indoor units ranging between 100percentage to 140percentage of ODU capacity . COP minimum 3.5. Make : Daikin / LG / O General / Toshiba. 16 HP | 3 | SET | 297901.5 | 54700 | 1057804.5 | Model:RXQ16ARY6(Considered Lifting Shifting Charges & Ms Stand Floor Mounting Type
10 | VRF Indoor Units : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 0.8 TR | 6 | No. | 26065 | 2000 | 168390 | 0.83TR Model:FXAQ25ARVE6
11 | VRF Indoor Units : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.0 TR | 12 | No. | 26455 | 2000 | 341460 | 1.04TR Model:FXAQ32ARVE6
12 | VRF Indoor Units : Hi wall Splits : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 1.5 TR | 12 | No. | 28860 | 2000 | 370320 | 1.65TR Model:FXAQ50ARVE6
13 | Cassette Units : Supply, Installation, Testing and Commissioning of variable refrigerant flow modular type indoor units wired/wireless remote suitable for R410a refrigerant comprising of all accessories as per the specifications. The indoor units shall be suitable to work on cooling mode.The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The indoor units shall be suitable for operation on 220 plus or minus 6percentage volts, 50Hz, 1 phase AC power supply. 3.0 TR – 4 way | 3 | No. | 49367.5 | 3000 | 157102.5 | 3.31TR Model:FXFSQ100ARV16
14 | Supply, Installation, Testing and Commissioning of Hard copper REFRIGERANT PIPING of 16swg various sizes with necessary supports, fittings, interconnecting the liquid and suction lines between the aircooled outdoor units and the indoor units. The piping shall be carried out of Hard drawn copper pipes of type K with soldered / brazed socket fittings. Isolating valves shall be provided to isolate each compressor, strainers, sight glass and any other component requiring proper operation and maintenance. Both the suction and liquid lines shall be insulated with 19mm thick closed cell insulation for above 25mm dia , 13mm thick for pipes below 25mm dia . The insulation finished with treated woven glass fiber reinforced covering for inside Piping and including making required holes in the wall and re finishing and water tight of holes after laying holes as per the specifications and approved drawings | 396 | RMT | 3650 | 750 | 1742400 | Considered 12 RMT per each indoor unit(Drawings Required)Considered GC Copper pipe With Cable Tray(OEM Approved)
15 | Supply, Installation , Testing and Commissioning of Refnet joints to be provided in refrigerant pipe line. Material of construction for fittings shall be similar to refrigerant piping | 30 | Set |  |  |  | Included Refnet Joints
16 | Supply and Installation of control cum transmission wiring of size 3C x 1.5 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing and accessories | 450 | Rmt | 245 | 50 | 132750 | Polycab
17 | Supply and Installation of cabling of size 2C x 1 Sqmm copper wire to be laid in heavy grade PVC conduit including all fixing and accessories as per the approved routing | 300 | Rmt | 195 | 50 | 73500 | Polycab
| Total Basic Amount |  |  |  |  | 5452347
Equipment GST@28% Extra
Lowside GST@18% Extra
NOTE: Final bill as per site measurements.
Terms & Conditions:
1. Payment Terms : For Highside 70% Advance and 30% before dispatch of units against proforma invoice.
For Lowside 50% Advance along with order , 30% material at site & 10% against installation of VRV System and 10% against completion of project.
2. Delivery period : 3-5 Weeks from the date of confirmed order with advances.
3. Warranty Period(DLP) : 12 Months from the date of commissioning or 15 months from the date of ODU invoice whichever is earlier.
4. Final Billing will be done as per the actual high side units.
5. The above quoted price is valid for 01 month only.
6. Commissioning Terms :
a. | 100% permanent power required before commisioning.
b. | Stabalized power of 380-415V for 3-Phase & 220-230V for 1-Phase is required.
c. | 3 days prior notice is required for commisioning.
d. | Floor & Area should be Deep cleaned before commisioning.
Exclusions : (CUSTOMER SCOPE)
1. All civil works, Carpentry, Core cutting, chipping works, false ceiling works are at client scope only.
2. Main power supply of 3Phase near to ODU's and 1Phase/3Phase supply for indoor units as required with MCB to be provided with proper earthing is in client scope.
3. Outdoor unit lifting, Angular stands, Catwalk stands, Pedestrals or civil foundations are to be provided by client.
4. Underdeck Insulation if required for exposed slab is at client scope only.
5. Any cost implication for changes in models and capacities after award of contract has to be borned by client with extension of deliveries.
6. Any other items not mentioned in above BOQ is at client scope only.
7. Scaffolding to be provided wherever is required for doing external works of building.
Taxes: Included.
Thanking you sir.
Assuring you the best service at all times.
For National Aircon India Pvt Ltd
Authorized Signatory